## PCIR
Example: A 100kW rooftop solar project under the net-metering program
Distributed Energy Resource (DER) Connection |  |  |  | Distributor: Sample Utilities Corp.
Preliminary Consultation Information Request (PCIR) |  |  |  | Project Name: DER Working Group Example #1
OEB Template Version 2.2 (optional information Distributor can provide)
Distributor Template Version (optional information Distributor can provide)
1. Instruction
The Applicant should only proceed with this form if the proposed DER project meets the following conditions: a) Has a capacity larger than 12kW (AC). b) Not a sole emergency backup generator during a power interruption to the distribution system. For a micro DER project with a capacity size of 12kW or less, please review the Local Distribution Company (Distributor)'s website for application process. The Applicant should complete the latest version of the PCIR form, and submit the form per the instruction provided on the Distributor's website. All fields are required, unless otherwise noted, to enable the preliminary connection assessment. The Applicant does not need to commit to any information provided in the PCIR. Changes can be made when applying for a Connection Impact Assessment (CIA). Please note that the preliminary consultation process does not consider the full range of technical evaluations that would be performed through a CIA. The PCR provides additional information on the potential complexity of the connection of the proposed DER. Capacity is not reserved upon completion of a Preliminary Consultation Report (PCR). Please check the Independent Electricity System Operator (IESO)'s website for information on the System Impact Assessment if the Applicant plans to provide ancillary services. All kW capacity information in this form should be in AC.
2. Distributor Contact Information
2.01 | Contact Information
| A. Distributor Name | - | Sample Utilities Corp. | Pre-populated by Distributor
| B. Department Name | - | Distributed Energy Resources Team | Pre-populated by Distributor
| C. Department Address | - | 100 City Boulevard | Pre-populated by Distributor
| D. Department City & Postal Code | - | City #1, Ontario M0L 1A0 | Pre-populated by Distributor
| E. Department Fax | - |  | Pre-populated by Distributor (Optional)
| F. Department Phone | - | 111-111-1111 | Pre-populated by Distributor
| G. Department Email | - | DER@SampleUtilities.com | Pre-populated by Distributor
3. General
3.01 | Application Information
| A. Project Name | - | DER Working Group Example #1 | -
| B. Application Submission Date | Date | 2023-05-05 | Format: YYYY-MM-DD
3.02 | Applicant Information
| A. Applicant (Company Name) | - | ABC Inc. | -
| B. Applicant Type | Select | Property Owner / Landlord / Property Manager | -
| C. Applicant Representative (Individual Name) | - | Somebody | -
| D. Applicant Address | - | 123 Any Street | Corporate Address (if applicable)
| E. Applicant City | - | City #2 | -
| F. Applicant Postal Code | - | A0A-0A0 | Format: A0A 0A0
| G. Applicant Fax | - |  | Optional
| H. Applicant Phone | - | 222-222-2222 | Format: XXX-YYY-ZZZZ
| I. Applicant Email | - | abc.def@gmail.com | -
4. Project Information
4.01 | Project Nameplate & Type
| A. Proposed Capacity (Aggregate) | kW | 100 | AC capacity
| B. Exporting/Non-Exporting | Select | Exporting | Indicate if capable of exporting to grid
| C. Proposed Export Capacity (Aggregate) | kW | 10 | If capacity is different from Proposed Capacity
| D. Connection Type (Single/Three-Phase) | Select | Three-Phase | -
| E. Inverter-Based/Non-Inverter-Based | Select | Inverter-Based | -
4.02 | Proposed DER Fuel/Energy Type
Please use the selection below to identify the proposed DER fuel/energy type.
| A. Solar | kW | 100 | -
| B. Wind | kW |  | -
| C. Water (Hydroelectric) | kW |  | -
| D. Biofuel/Biogas | kW |  | -
| E. Thermal | kW |  | Other than biofuel
| F. Energy Storage (including bi-directional EV) | kW |  | -
| G. Other | Specify |  | Enter specific technology type and kW information
5. Site Information
5.01 | Existing Account Holder
| A. Existing Account Number (if Applicable) | - | 123456-1 | Required if applicable
| B. Existing Account Holder Name (if Applicable) | - | XYZ Ontario Inc. | Required if applicable
5.02 | Site Information
| A. Site Address | - | 123 Davis | Location of proposed facility
| B. Site City/Town/Township | - | Vaughan, Ontario | -
| C. Site Postal Code | - | L3M 0A5 | -
| D. Site GPS Co-ordinates | - |  | Required for rural locations
5.03 | Existing DERs at Site
If the Applicant has existing DER(s) at the same project site, please provide information required below to ensure proper preliminary connection assessment. If there is a variety of fuel/energy types, please explain in section "6.01 Other Information" below.
| A. Existing DER Capacity (Aggregate) | kW |  | Required if existing DER(s) installed
| B. Existing DER Connection (Single/Three-Phase) | Select |  | Required if existing DER(s) installed
| C. Existing DER Type (Inverter/Non-Inverter) | Select |  | Required if existing DER(s) installed
| D. Existing DER Intent (Exporting/Non-Exporting) | Select |  | Required if existing DER(s) installed
6. Other Information
6.01 | Other Information
A. In the comment box below, the Applicant can provide any additional information that is required as indicated in the above section(s) or considered beneficial for the purpose of obtaining a preliminary connection assessment.
Installing 100kW rooftop solar, net metering project
B. If the Applicant chooses to provide accompanying documents, please list them below.
7. Distributor Office Use Only (Optional)
7.01 | PCIR Status
| A. Date Received | Date |  | Completed by Distributor
| B. Date Returned Incomplete | Date |  | Completed by Distributor
| C. Date Preliminary Consultation Report Issued | Date |  | Completed by Distributor

## PCR
Distributed Energy Resource (DER) Connection
Preliminary Consultation Report (PCR)
OEB Template Version 2 (optional information Distributor can provide)
Distributor Template Version (optional information Distributor can provide)
1. Information
The PCR is an official response to an Applicant's Preliminary Consultation Information Request (PCIR). It assists the Applicant in completing a potential Connection Impact Assessment application (CIA), should the Applicant decide to proceed. Please note that the information provided below is based on information and records available at the time that this PCR was issued and is subject to change and verification. Further, the preliminary consultation process does not consider the full range of technical evaluations that would be performed through a CIA. Finally, capacity is only reserved upon completion of a successful CIA, in accordance with Distribution System Code and DER Connection Procedures requirements.
2. Distributor Contact Information
2.01 | Contact Information
| A. Distributor Name | - | Sample Utilities Corp. | Completed by Distributor
| B. Department Name | - | Distributed Energy Resources Team | Completed by Distributor
| C. Department Address | - | 100 City Boulevard | Completed by Distributor
| D. Department City & Postal Code | - | City #1, Ontario M0L 1A0 | Completed by Distributor
| E. Department Fax | - | -- | Completed by Distributor (Optional)
| F. Department Phone | - | 111-111-1111 | Completed by Distributor
| G. Department Email | - | DER@SampleUtilities.com | Completed by Distributor
3. General Application Information
3.01 | Administration
| A. Project ID | - |  | Assigned by Distributor
| B. Project Name | - | DER Working Group Example #1 | As provided by customer
| C. Report Date | Date |  | Assigned by Distributor
3.02 | Applicant Information
| A. Applicant (Company Name) | - | ABC Inc. | As provided by customer
| B. Applicant Representative Email | - | abc.def@gmail.com | As provided by customer
3.03 | Project Nameplate & Type
| A. Proposed Capacity (Aggregate) | kW | 100 | As provided by customer
| B. Exporting/Non-Exporting |  | Exporting | As provided by customer
| C. Proposed Export Capacity (Aggregate) | kW | 10 | As provided by customer
| D. Connection Type (Single/Three-Phase) |  | Three-Phase | As provided by customer
| E. Inverter-Based/Non-Inverter-Based |  | Inverter-Based | As provided by customer
3.04 | Proposed DER Fuel/Energy Type
| A. Solar | - | 100 | As provided by customer
| B. Wind | - | -- | As provided by customer
| C. Water (Hydroelectric) | - | -- | As provided by customer
| D. Biofuel/Biogas | - | -- | As provided by customer
| E. Thermal | - | -- | As provided by customer
| F. Energy Storage (including bi-directional EV) | - | -- | As provided by customer
| G. Other | Specify | -- | As provided by customer
3.05 | Site Information
| A. Site Address | - | 123 Davis | As provided by customer
| B. Site City/Town/Township | - | Vaughan, Ontario | As provided by customer
| C. Site Postal Code | - | L3M 0A5 | As provided by customer
| D. Site GPS Co-ordinates | - | -- | As provided by customer
3.06 | Existing DERs at Site
| A. Existing DER Capacity (Aggregate) | kW | -- | As provided by customer
| B. Existing DER Connection (Single/Three-Phase) | - | -- | As provided by customer
| C. Existing DER Type (Inverter/Non-Inverter) | - | -- | As provided by customer
| D. Existing DER Intent (Exporting/Non-Exporting) | - | -- | As provided by customer
4. Connection Overview
4.01 | Site Connection Information
| A. Existing Site Distribution Transformer Capacity | kVA | 500 | If customer owned, Applicant is to confirm with CIA application
| B. Existing Site Distribution Transformer Ownership | Select | Distributor-Owned | Distributor or Customer-Owned
| C. Existing Connection Voltage | kV | 13.8 | -
| D. Distributor Asset ID (if Applicable) | - | IDx-123 | Transformer ID, Vault ID, etc.
4.02 | Distribution System Assets
| A. Distributor Name | - | Sample Utilities Corp. | Same as 2.01-A above
| B. Distribution Station Name | - | MS#1 | -
| C. Distribution Feeder Designation | - | F1 | -
| D. Distribution Feeder Voltage | kV | 13.8 | -
4.03 | Upstream Distribution Assets (if Applicable)
| A. Upstream Distributor Name | - |  | -
| B. Upstream Distribution Station Name | - |  | -
| C. Upstream Distribution Feeder Designation | - |  | -
| D. Upstream Distribution Feeder Voltage | kV |  | -
4.04 | Transmitter
| A. Transmitter Name | - | Sample Transmission Corp. | -
| B. Transformer Station Name | - | ABCD TS | -
| C. Subtransmission Feeder Designation | - | M2 | -
| D. Subtransmission Feeder Voltage | kV | 44 | -
4.05 | Other Comments
A. Additional information not reported in the prescribed fields above (optional).
5. Preliminary Assessment of Connection Complexity
In order to provide an earlier indication of the anticipated complexity of a connection, this section provides an initial assessment of likely connection requirements and their complexity levels. These requirements are typically based on judgment or simplified criteria, and would be subject to change through the CIA process and further consultation with upstream utilities, including host Distributor and the transmitter. Further, this preliminary assessment does not evaluate the potential for the full range of requirements set through the CIA process. Please also review section 6.01 for additional insight on areas of uncertainty.
The following are four potential complexity tiers. • Extremely High: Projects that are characterized as having “extremely high” complexity are likely not viable, due to the nature of system constraints that preclude the connection of the contemplated DER facility. • High: Projects that are characterized as having “high” complexity can be made viable through a combination of transmission, distribution or customer-side infrastructure upgrades. • Medium: Projects that are characterized as having “medium” complexity can be made viable through a combination of distribution system upgrades. Transmission system upgrades are most likely not required. Customer-side infrastructure upgrades may be required. • Low: Projects that are characterized as having “low” complexity are viable with minor distribution system modifications. Transmission system upgrades are most likely not required. Customer-side infrastructure upgrades may be required.
No. | Item | Impact | Preliminary Assessment | Comments
5.01 | Station Constraints
If this section identifies a thermal constraint or a short circuit constraint, it is most likely the proposed project would not be able to connect.
| A. Thermal | Ex. High | No Known Constraint At This Time
| B. Short Circuit | Ex. High | No Known Constraint At This Time
5.02 | Anticipated Impact Assessments Required
This section provides details about the connection studi(es) required for the proposed DER project as guidance only and does not assume the outcome of the CIA. Please consult the Distributor website for instructions on how to apply for a CIA. Please check the Independent Electricity System Operator (IESO)'s website for information on the System Impact Assessment if the Applicant plans to provide ancillary services.
| A. Distributor CIA | Select | Is Required To Officially Apply For Connection | Move to section 5.06 if no Distributor CIA required
| B. Host Distributor CIA | Medium | Not Required | -
| C. Transmitter CIA | Medium | Not Required | -
| D. IESO System Impact Assessment | High | Not Required | Req'd for ancillary services & 10MW+
5.03 | Distribution System Infrastructure
| A. New Line Expansion | High | Not Required | -
| B. Reconductoring of Existing Feeder Trunk | High | Not Required | -
| C. Site Distribution Transformer Upgrades | Medium | Unlikely To Be Required | -
| D. Reconductoring of Branch/Tap | Medium | Not Required | -
5.04 | Protection, Monitoring, Metering and Telecom
| A. Station Protection Upgrades | High | Not Required | -
| B. Remote Monitoring | Medium | Required | -
| C. Metering Upgrades | Low | Required | -
| D. Transfer Trip | High | Not Required | -
5.05 | Distributor-Specific Criteria
| A. Optional (Distributor to complete if needed) | TBD |  | -
| B. Optional (Distributor to complete if needed) | TBD |  | -
| C. Optional (Distributor to complete if needed) | TBD |  | -
5.06 | Distributor Overall Assessment of Connection Feasibility
| A. Anticipated Connection Capacity | Select | Conditional Pass: There may be capacity at this location, subject to a connection impact assessment | Preliminary assessment by Distributor
| B. Anticipated Connection Complexity | Select | Low Complexity: Projects that are characterized as having “low” complexity are viable with minor distribution system modifications. Transmission system upgrades are most likely not required. Customer-side infrastructure upgrades may be required. | Preliminary assessment by Distributor
6. Additional Comments
6.01 | Other Comments by Distributor
A. This section provides additional information not discussed in the prescribed fields above (e.g., alternate system configurations due to feeder switching, potential interconnection design suggestions, teleprotection and/or communication media, etc.).

## Drop-Down Lists
Drop-Down List Selections (Do Not Edit)
Applicant Type | DER Phase |  | DER Inverter/Non-Inverter |  | DER Exporting/Non-Exporting
Please select applicant type | Please select number of phases |  | Please select whether inverter-based |  | Please select whether exporting
DER Owner | Single-Phase |  | Inverter-Based |  | Exporting
Property Owner / Landlord / Property Manager | Three-Phase |  | Non-Inverter-Based |  | Non-Exporting
Consultant |  |  | Multiple Units (provide details in PCIR section 6) |  | Multiple Units (provide details in PCIR section 6)
Other
| DER Solar |  | DER Wind | DER Hydroelectric |  |  | DER Biofuel/Biogas
| Please select whether solar |  | Please select whether wind | Please select whether hydroelectric |  |  | Please select whether biofuel/biogas
| Solar |  | Wind | Water (Hydroelectric) |  |  | Biofuel/Biogas
| N/A |  | N/A | N/A |  |  | N/A
DER Thermal |  | DER Energy Storage |  |  |  | Thermal and Short Circuit |  | Distributor CIA |  | Impact Assessment
Please select whether thermal (non-biofuel) |  | Please select whether energy storage |  |  |  | Please select response |  | Please select response |  | Distributor to select
Thermal (Non-Biofuel) |  | Energy Storage (including bi-directional EV) |  |  |  | Known Constraint |  | No CIA Required Due To Capacity Constraint |  | Required
N/A |  | N/A |  |  |  | No Known Constraint At This Time |  | Is Required To Officially Apply For Connection |  | Not Required
Dx Transformer Ownership |  | Preliminary Assessment |  | Weightings |  | Capacity
Distributor to select |  | Distributor to select |  | Distributor to select |  | Distributor to select |  |  | Preliminary Assessment
Distributor-Owned |  | Likely Required |  | N/A |  | No Capacity Due To Transmission Constraints At Present |  |  | Distributor to select
Customer-Owned |  | Required |  | Low |  | No Capacity Due To Distribution Constraints At Present |  |  | Required
|  | Unlikely To Be Required |  | Med |  | Conditional Pass: There may be capacity at this location, subject to a connection impact assessment |  |  | Not Required
|  | Not Required |  | High |  |  |  |  | Maybe Required
|  |  |  | Ex. High |  |  |  |  | Non-Transfer Trip Type of Protection & Control System Required
Complexity
Distributor to select
Low Complexity: Projects that are characterized as having “low” complexity are viable with minor distribution system modifications. Transmission system upgrades are most likely not required. Customer-side infrastructure upgrades may be required.
Medium Complexity: Projects that are characterized as having “medium” complexity can be made viable through a combination of distribution system upgrades. Transmission system upgrades are most likely not required. Customer-side infrastructure upgrades may be required.
High Complexity: Projects that are characterized as having “high” complexity can be made viable through a combination of transmission, distribution or customer-side infrastructure upgrades.
Extremely High Complexity: Projects that are characterized as having “extremely high” complexity are likely not viable, due to the nature of system constraints that preclude the connection of the contemplated DER facility.
N/A