## Read Me
Workbook Overview
This workbook contains the following sheets: eTRM+ This sheet shows the per-unit natural gas, electricity, and water savings; incremental cost; and measure life for energy efficiency measures contained in the Ontario Technical Resource Manual (TRM). Each row represents a unique measure installation context based on the sector, building type, and equipment type installed. The sheet also contains information not found in the TRM; namely, free-ridership, installation, and gross realization rates. The sources behind the non-TRM values are listed in the Sources sheet. In future versions of the eTRM+, these will be assigned by measure row. Should any inconsistencies arise between the TRM, source documents, and eTRM+, the TRM and source documents take precedence. Measures included in the eTRM+ or TRM are not guaranteed to be offered by current Ontario DSM programs. Measure Code This sheet shows the components of each measure code Sources This sheet shows the sources of values not contained within the written TRM such as free-ridership, spillover, gross realization rate, and installation rate values.
Data Dictionary
Variable | Description
Measure Code | ID associated with each measure. Each ID is unique within a TRM version
Status | Active status of each measure (e.g. current, new, retired)
Notes | Additional details for measure retirements or revisions
Sector | Affliated business sector associated with each measure (Residential, Commercial, Multi-residential)
Measure Group | (e.g. Adaptive Thermostat, Air Curtain, Combination Oven)
Building Type/ Size | Additional details on measure location
Measure Category | New Construction, Replacement, Retrofit
End Use | food service, water heating, or space heating
Efficient Technology | Technology used by each measure replacing the baseline
Efficient Technology Description | Further notes on each efficient technology, usually size or usage of each
Baseline Technology | Original technology replaced by each affliated efficient technology
Baseline Technology Description | Further notes on each baseline technology, usually size or usage of each
Quantity Unit | Per quantity calculation unit (e.g. unit, fan, foot)
Size Unit | Per size (quasi-prescriptive) measurement used for calcluation (e.g. kBtu/hr, CFM)
TRM | TRM Version containing each measure
TRM Published Date | Date TRM was published
LRAM Program Year | The year the measure comes into effect for Lost Revenue Adjustment Mechanism (LRAM) calculations. This corresponds to the best assumptions at the time of annual verification.
DSMSI Program Year | The year the measure comes into effect for Demand-Side Management Shareholder Incentive (DSMSI) calculations. This corresponds to the best assumptions at the time of program planning.
Annual Natural Gas Savings per Quantity Unit (m3)
Annual Natural Gas Savings per Size Unit (m3)
Annual Electric Savings per Quantity Unit (kWh)
Annual Electric Savings per Size Unit (kWh)
Annual Water Savings per Quantity Unit (L)
Annual Water Savings per Size Unit (L)
Incremental Cost per Quantity Unit ($ CAD)
Incremental Cost per Size Unit ($ CAD)
Rate Zone | Legacy Enbridge or Union
EUL | Effictive useful life of each measure in years
Delivery Channel | How each measure is delivered to the customer
Free Rider Rate (%) | The portion of a measure's verified energy savings that would naturally occur without the utility program
Installation Factor | The portion of a measure's claimed energy savings that were verified to have been installed
Gross Realization Rate | The portion of a measure's claimed energy savings that were verified. Includes corrections to the number of units installed, eligibility criterion, etc.

## eTRM+
Measure Code | Status | Notes | Sector | Measure Group | Building Type/ Size | Measure Category | End Use | Efficient Technology | Efficient Technology Description | Baseline Technology | Baseline Technology Description | Quantity Unit | Size Unit | Most recent eTRM Update | TRM Published Date | Annual Natural Gas Savings per Quantity Unit (m3) | Annual Natural Gas Savings per Size Unit (m3) | Annual Electric Savings per Quantity Unit (kWh) | Annual Electric Savings per Size Unit (kWh) | Annual Water Savings per Quantity Unit (L) | Annual Water Savings per Size Unit (L) | Incremental Cost per Quantity Unit ($ CAD) | Incremental Cost per Size Unit ($ CAD) | EUL | Delivery Channel | Free Rider Rate (%) | Installation Factor | Gross Realization Rate
COM-CS-WH-502-02 | Replaced | Replaced in TRM Version 8.0 | Commercial | Condensing Storage Water Heater | Low Utilization | New Construction/Natural Replacement | water heating | Condensing Storage Water Heater - Low Utilization | > 75 kBtu/hr and <=250 kBtu/hr. inputEstimated overall efficiency of units shipped = 94.5% | Non-condensing storage water heater | Non-condensing storage water heaterGreater than 75 kBtu/hr. inputEstimated overall efficiency of units shipped = 80.1% |  | kBtu/hr input capacity | TRM Version 5.0 | 2020-11-12 | 0 | 1.36 | 0 | 0 | 0 | 0 | 2591 | 0 | 15 | Direct Install | 0.05 | 1 | 1
COM-CS-WH-503-02 | Replaced | Replaced in TRM Version 8.0 | Commercial | Condensing Storage Water Heater | Medium Utilization | New Construction/Natural Replacement | water heating | Condensing Storage Water Heater - Medium Utilization | > 75 kBtu/hr and <=250 kBtu/hr. inputEstimated overall efficiency of units shipped = 94.5% | Non-condensing storage water heater | Greater than 75 kBtu/hr. inputEstimated overall efficiency of units shipped = 80.1% |  | kBtu/hr input capacity | TRM Version 5.0 | 2020-11-12 | 0 | 2.22 | 0 | 0 | 0 | 0 | 2591 | 0 | 15 | Direct Install | 0.05 | 1 | 1
COM-CS-WH-504-02 | Replaced | Replaced in TRM Version 8.0 | Commercial | Condensing Storage Water Heater | High Utilization | New Construction/Natural Replacement | water heating | Condensing Storage Water Heater - High Utilization | > 75 kBtu/hr and <=250 kBtu/hr. inputEstimated overall efficiency of units shipped = 94.5% | Non-condensing storage water heater | Greater than 75 kBtu/hr. inputEstimated overall efficiency of units shipped = 80.1% |  | kBtu/hr input capacity | TRM Version 5.0 | 2020-11-12 | 0 | 3.09 | 0 | 0 | 0 | 0 | 2591 | 0 | 15 | Direct Install | 0.05 | 1 | 1
COM-CT-WH-511-02 | Replaced | Replaced in TRM Version 8.0 | Commercial | Condensing Tankless Water Heater | Low Utilization | New Construction/Natural Replacement | water heating | Condensing Tankless Water Heater - Low Utilization | >=200 kBtu/hrThermal efficiency = 92.9%Stand-by Loss = negligible | Non-Condensing Storage Water Heater | 75 kBtu/hr. and greaterThermal efficiency of units shipped = 80.1%Stand-by Loss Q/0.8 +110√V0 | unit | kBtu/hr input capacity | TRM Version 5.0 | 2020-11-12 | 326 | 0.79 | 0 | 0 | 0 | 0 | 2227 | 0 | 20 | Direct Install | 0.02 | 1 | 1
COM-CT-WH-512-02 | Replaced | Replaced in TRM Version 8.0 | Commercial | Condensing Tankless Water Heater | Medium Utilization | New Construction/Natural Replacement | water heating | Condensing Tankless Water Heater - Medium Utilization | >=200 kBtu/hrThermal efficiency = 92.9%Stand-by Loss = negligible | Non-Condensing Storage Water Heater | 75 kBtu/hr. and greaterThermal efficiency of units shipped = 80.1%Stand-by Loss Q/0.8 +110√V0 | unit | kBtu/hr input capacity | TRM Version 5.0 | 2020-11-12 | 326 | 1.29 | 0 | 0 | 0 | 0 | 2227 | 0 | 20 | Direct Install | 0.02 | 1 | 1
COM-CT-WH-513-02 | Replaced | Replaced in TRM Version 8.0 | Commercial | Condensing Tankless Water Heater | High Utilization | New Construction/Natural Replacement | water heating | Condensing Tankless Water Heater - High Utilization | >=200 kBtu/hrThermal efficiency = 92.9%Stand-by Loss = negligible | Non-Condensing Storage Water Heater | 75 kBtu/hr. and greaterThermal efficiency of units shipped = 80.1%Stand-by Loss Q/0.8 +110√V0 | unit | kBtu/hr input capacity | TRM Version 5.0 | 2020-11-12 | 326 | 1.79 | 0 | 0 | 0 | 0 | 2227 | 0 | 20 | Direct Install | 0.02 | 1 | 1
COM-CS-WH-505-02 | Replaced | Replaced in TRM Version 8.0 | Commercial | Condensing Storage Water Heater | Low Utilization | New Construction/Natural Replacement | water heating | Condensing Storage Water Heater - Low Utilization | >250 kBtu/hr. inputEstimated overall efficiency of units shipped = 94.5% | Non-condensing storage water heater | Greater than 75 kBtu/hr. inputEstimated overall efficiency of units shipped = 80.1% |  | kBtu/hr input capacity | TRM Version 5.0 | 2020-11-12 | 0 | 1.36 | 0 | 0 | 0 | 0 | 4464 | 0 | 15 | Direct Install | 0.05 | 1 | 1
COM-CS-WH-506-02 | Replaced | Replaced in TRM Version 8.0 | Commercial | Condensing Storage Water Heater | Medium Utilization | New Construction/Natural Replacement | water heating | Condensing Storage Water Heater - Medium Utilization | >250 kBtu/hr. inputEstimated overall efficiency of units shipped = 94.5% | Non-condensing storage water heater | Greater than 75 kBtu/hr. inputEstimated overall efficiency of units shipped = 80.1% |  | kBtu/hr input capacity | TRM Version 5.0 | 2020-11-12 | 0 | 2.22 | 0 | 0 | 0 | 0 | 4464 | 0 | 15 | Direct Install | 0.05 | 1 | 1
COM-CS-WH-507-02 | Replaced | Replaced in TRM Version 8.0 | Commercial | Condensing Storage Water Heater | High Utilization | New Construction/Natural Replacement | water heating | Condensing Storage Water Heater - High Utilization | >250 kBtu/hr. inputEstimated overall efficiency of units shipped = 94.5% | Non-condensing storage water heater | Greater than 75 kBtu/hr. inputEstimated overall efficiency of units shipped = 80.1% |  | kBtu/hr input capacity | TRM Version 5.0 | 2020-11-12 | 0 | 3.09 | 0 | 0 | 0 | 0 | 4464 | 0 | 15 | Direct Install | 0.05 | 1 | 1
COM-CT-WH-508-02 | Replaced | Replaced in TRM Version 8.0 | Commercial | Condensing Tankless Water Heater | Low Utilization | New Construction/Natural Replacement | water heating | Condensing Tankless Water Heater - Low Utilization | >75 and <200 kBtu/hrThermal efficiency = 92.9%Stand-by Loss = negligible | Non-Condensing Storage Water Heater | 75 kBtu/hr. and greaterThermal efficiency of units shipped = 80.1%Stand-by Loss Q/0.8 +110√V0 | unit | kBtu/hr input capacity | TRM Version 5.0 | 2020-11-12 | 212 | 0.79 | 0 | 0 | 0 | 0 | 2227 | 0 | 20 | Direct Install | 0.02 | 1 | 1
COM-CT-WH-509-02 | Replaced | Replaced in TRM Version 8.0 | Commercial | Condensing Tankless Water Heater | Medium Utilization | New Construction/Natural Replacement | water heating | Condensing Tankless Water Heater - Medium Utilization | >75 and <200 kBtu/hrThermal efficiency = 92.9%Stand-by Loss = negligible | Non-Condensing Storage Water Heater | 75 kBtu/hr. and greaterThermal efficiency of units shipped = 80.1%Stand-by Loss Q/0.8 +110√V0 | unit | kBtu/hr input capacity | TRM Version 5.0 | 2020-11-12 | 212 | 1.29 | 0 | 0 | 0 | 0 | 2227 | 0 | 20 | Direct Install | 0.02 | 1 | 1
COM-CT-WH-510-02 | Replaced | Replaced in TRM Version 8.0 | Commercial | Condensing Tankless Water Heater | High Utilization | New Construction/Natural Replacement | water heating | Condensing Tankless Water Heater - High Utilization | >75 and <200 kBtu/hrThermal efficiency = 92.9%Stand-by Loss = negligible | Non-Condensing Storage Water Heater | 75 kBtu/hr. and greaterThermal efficiency of units shipped = 80.1%Stand-by Loss Q/0.8 +110√V0 | unit | kBtu/hr input capacity | TRM Version 5.0 | 2020-11-12 | 212 | 1.79 | 0 | 0 | 0 | 0 | 2227 | 0 | 20 | Direct Install | 0.02 | 1 | 1
COM-DK-SH-521-03 | Replaced | Updated in TRM V8.0 | Commercial | Demand Control Kitchen Ventilation |  | Retrofit | space heating | Demand Control Kitchen Ventilation | 0 - 5,000 CFM | Constant Volume Kitchen Ventilation |  | unit |  | TRM Version 5.0 | 2020-11-12 | 4207 | 0 | 4940 | 0 | 0 | 0 | 4766 | 0 | 15 | Direct Install | 0.05 | 1 | 1
COM-DK-SH-524-03 | Replaced | Updated in TRM V8.0 | Commercial | Demand Control Kitchen Ventilation |  | New Construction/Natural Replacement | space heating | Demand Control Kitchen Ventilation | 0 - 5,000 CFM | Constant Volume Kitchen Ventilation |  | unit |  | TRM Version 5.0 | 2020-11-12 | 4207 | 0 | 4940 | 0 | 0 | 0 | 2383 | 0 | 15 | Direct Install | 0.05 | 1 | 1
COM-DK-SH-523-03 | Replaced | Updated in TRM V8.0 | Commercial | Demand Control Kitchen Ventilation |  | Retrofit | space heating | Demand Control Kitchen Ventilation | 10,001 - 15,000 CFM | Constant Volume Kitchen Ventilation |  | unit |  | TRM Version 5.0 | 2020-11-12 | 17529 | 0 | 28929 | 0 | 0 | 0 | 19859 | 0 | 15 | Direct Install | 0.05 | 1 | 1
COM-DK-SH-526-03 | Replaced | Updated in TRM V8.0 | Commercial | Demand Control Kitchen Ventilation |  | New Construction/Natural Replacement | space heating | Demand Control Kitchen Ventilation | 10,001 - 15,000 CFM | Constant Volume Kitchen Ventilation |  | unit |  | TRM Version 5.0 | 2020-11-12 | 17529 | 0 | 28929 | 0 | 0 | 0 | 9929 | 0 | 15 | Direct Install | 0.05 | 1 | 1
COM-CU-SH-515-02 | Replaced | Updated in TRM Version 6.0 with new incremental cost and negative, not positive electric savings. | Commercial | Condensing Unit Heater |  | Natural Replacement | space heating | Condensing Unit Heater | 125-200 kBtu/hr 90% Thermal Efficiency, 89% Annual Efficiency | Non-Condensing Unit Heater | 80% Thermal Efficiency, 78% Annual Efficiency |  | kBtu/hr input capacity | TRM Version 5.0 | 2020-11-12 | 0 | 7.89 | -530 | 0 | 0 | 0 | 0 | 12.9 | 18 | Direct Install | 0 | 1 | 1
COM-CU-SH-518-02 | Replaced | Updated in TRM Version 6.0 with new incremental cost and negative, not positive electric savings. | Commercial | Condensing Unit Heater |  | New Construction | space heating | Condensing Unit Heater | 125-200 kBtu/hr 90% Thermal Efficiency, 89% Annual Efficiency | Non-Condensing Unit Heater | 80% Thermal Efficiency, 78% Annual Efficiency |  | kBtu/hr input capacity | TRM Version 5.0 | 2020-11-12 | 0 | 5.92 | -398 | 0 | 0 | 0 | 0 | 12.9 | 18 | Direct Install | 0 | 1 | 1
COM-CU-SH-516-02 | Replaced | Updated in TRM Version 6.0 with new incremental cost and negative, not positive electric savings. | Commercial | Condensing Unit Heater |  | Natural Replacement | space heating | Condensing Unit Heater | 225-300 kBtu/hr 90% Thermal Efficiency, 89% Annual Efficiency | Non-Condensing Unit Heater | 80% Thermal Efficiency, 78% Annual Efficiency |  | kBtu/hr input capacity | TRM Version 5.0 | 2020-11-12 | 0 | 7.89 | -546 | 0 | 0 | 0 | 0 | 12.9 | 18 | Direct Install | 0 | 1 | 1
COM-CU-SH-519-02 | Replaced | Updated in TRM Version 6.0 with new incremental cost and negative, not positive electric savings. | Commercial | Condensing Unit Heater |  | New Construction | space heating | Condensing Unit Heater | 225-300 kBtu/hr 90% Thermal Efficiency, 89% Annual Efficiency | Non-Condensing Unit Heater | 80% Thermal Efficiency, 78% Annual Efficiency |  | kBtu/hr input capacity | TRM Version 5.0 | 2020-11-12 | 0 | 5.92 | -410 | 0 | 0 | 0 | 0 | 12.9 | 18 | Direct Install | 0 | 1 | 1
COM-CU-SH-514-02 | Replaced | Updated in TRM Version 6.0 with new incremental cost and negative, not positive electric savings. | Commercial | Condensing Unit Heater |  | Natural Replacement | space heating | Condensing Unit Heater | 30-100 kBtu/hr - 90% Thermal Efficiency, 89% Annual Efficiency | Non-Condensing Unit Heater | 80% Thermal Efficiency, 78% Annual Efficiency |  | kBtu/hr input capacity | TRM Version 5.0 | 2020-11-12 | 0 | 7.89 | -296 | 0 | 0 | 0 | 0 | 12.9 | 18 | Direct Install | 0 | 1 | 1
COM-CU-SH-517-02 | Replaced | Updated in TRM Version 6.0 with new incremental cost and negative, not positive electric savings. | Commercial | Condensing Unit Heater |  | New Construction | space heating | Condensing Unit Heater | 30-100 kBtu/hr - 90% Thermal Efficiency, 89% Annual Efficiency | Non-Condensing Unit Heater | 80% Thermal Efficiency, 78% Annual Efficiency |  | kBtu/hr input capacity | TRM Version 5.0 | 2020-11-12 | 0 | 5.92 | -222 | 0 | 0 | 0 | 0 | 12.9 | 18 | Direct Install | 0 | 1 | 1
COM-DK-SH-522-03 | Replaced | Updated in TRM V8.0 | Commercial | Demand Control Kitchen Ventilation |  | Retrofit | space heating | Demand Control Kitchen Ventilation | 5,001 - 10,000 CFM | Constant Volume Kitchen Ventilation |  | unit |  | TRM Version 5.0 | 2020-11-12 | 10517 | 0 | 16294 | 0 | 0 | 0 | 11915 | 0 | 15 | Direct Install | 0.05 | 1 | 1
COM-DK-SH-525-03 | Replaced | Updated in TRM V8.0 | Commercial | Demand Control Kitchen Ventilation |  | New Construction/Natural Replacement | space heating | Demand Control Kitchen Ventilation | 5,001 - 10,000 CFM | Constant Volume Kitchen Ventilation |  | unit |  | TRM Version 5.0 | 2020-11-12 | 10517 | 0 | 16294 | 0 | 0 | 0 | 5958 | 0 | 15 | Direct Install | 0.05 | 1 | 1
COM-CF-SH-494-02 | Current |  | Commercial | Condensing Furnace |  | New Construction | space heating | High Efficiency Condensing Furnace | >=97% AFUE | Condensing Furnace | 95% AFUE |  | kBtu/hr | TRM Version 5.0 | 2020-11-12 | 0 | 0.884 | 0 | 0 | 0 | 0 | 188 | 0 | 18 | Direct Install | 0.175 | 1 | 1
COM-CF-SH-495-02 | Current |  | Commercial | Condensing Furnace |  | Natural Replacement | space heating | High Efficiency Condensing Furnace | >=97% AFUE | Condensing Furnace | 95% AFUE |  | kBtu/hr | TRM Version 5.0 | 2020-11-12 | 0 | 1.178 | 0 | 0 | 0 | 0 | 188 | 0 | 18 | Direct Install | 0.175 | 1 | 1
COM-DS-SH-560-03 | Current |  | Commercial | Dock Door Seals |  | Retrofit | space heating | Dock Door Seals | 10' x 10' | Dock door with deteriorated seals |  | unit |  | TRM Version 5.0 | 2020-11-12 | 1736 | 0 | 433 | 0 | 0 | 0 | 2968 | 0 | 10 | Direct Install | 0.05 | 1 | 1
COM-DS-SH-564-03 | Current |  | Commercial | Dock Door Seals |  | Retrofit | space heating | Dock Door Seals | 10' x 10' | Dock door without seals |  | unit |  | TRM Version 5.0 | 2020-11-12 | 4501 | 0 | 1123 | 0 | 0 | 0 | 2615 | 0 | 10 | Direct Install | 0.05 | 1 | 1
COM-CM-SH-497-02 | Current |  | Commercial | Condensing Make Up Air Unit | Commercial | New Construction/Natural Replacement | space heating | Condensing Make Up Air Unit (MUA) - Commercial | 2 Speed | Conventional MUA | 80% Thermal Efficiency |  | CFM | TRM Version 5.0 | 2020-11-12 | 0 | 1.22 | 0 | 1.24 | 0 | 0 | 870 | 1.01 | 20 | Direct Install | 0.05 | 1 | 1
COM-CM-SH-500-02 | Current |  | Commercial | Condensing Make Up Air Unit | Multi-Residential and Long Term Care | New Construction/Natural Replacement | space heating | Condensing Make Up Air Unit (MUA) - Commercial | 2 Speed | Conventional MUA | 80% Thermal Efficiency |  | CFM | TRM Version 5.0 | 2020-11-12 | 0 | 2.45 | 0 | 1.61 | 0 | 0 | 870 | 1.01 | 20 | Direct Install | 0.05 | 1 | 1
COM-DF-SH-545-03 | Current |  | Commercial | Destratification Fans |  | New Construction | space heating | HVLS (High Volume Low Speed) Destratification Fans | 20 ft fan diameter | No destratification fans |  | fan |  | TRM Version 5.0 | 2020-11-12 | 1472 | 0 | 0 | 0 | 0 | 0 | 7961 | 0 | 15 | Direct Install | 0.1 | 1 | 1
COM-DF-SH-546-03 | Current |  | Commercial | Destratification Fans |  | Retrofit | space heating | HVLS (High Volume Low Speed) Destratification Fans | 20 ft fan diameter | No destratification fans |  | fan |  | TRM Version 5.0 | 2020-11-12 | 2029 | 0 | 0 | 0 | 0 | 0 | 7961 | 0 | 15 | Direct Install | 0.1 | 1 | 1
COM-DF-SH-547-03 | Current |  | Commercial | Destratification Fans |  | New Construction | space heating | HVLS (High Volume Low Speed) Destratification Fans | 24 ft fan diameter | No destratification fans |  | fan |  | TRM Version 5.0 | 2020-11-12 | 2120 | 0 | 0 | 0 | 0 | 0 | 7961 | 0 | 15 | Direct Install | 0.1 | 1 | 1
COM-DF-SH-548-03 | Current |  | Commercial | Destratification Fans |  | Retrofit | space heating | HVLS (High Volume Low Speed) Destratification Fans | 24 ft fan diameter | No destratification fans |  | fan |  | TRM Version 5.0 | 2020-11-12 | 2922 | 0 | 0 | 0 | 0 | 0 | 7961 | 0 | 15 | Direct Install | 0.1 | 1 | 1
COM-DS-SH-559-03 | Current |  | Commercial | Dock Door Seals |  | Retrofit | space heating | Dock Door Seals | 8' x 10' | Dock door with deteriorated seals |  | unit |  | TRM Version 5.0 | 2020-11-12 | 2041 | 0 | 509 | 0 | 0 | 0 | 1617 | 0 | 10 | Direct Install | 0.05 | 1 | 1
COM-DS-SH-563-03 | Current |  | Commercial | Dock Door Seals |  | Retrofit | space heating | Dock Door Seals | 8' x 10' | Dock door without seals |  | unit |  | TRM Version 5.0 | 2020-11-12 | 5087 | 0 | 1269 | 0 | 0 | 0 | 1455 | 0 | 10 | Direct Install | 0.05 | 1 | 1
COM-CO-FS-520-02 | Replaced | Updated in TRM Version 6.0 | Commercial | Convection Ovens |  | New Construction/Natural Replacement | food service | Energy Star Convection Ovens | Energy Star Rated Convection Oven (Full Size) | Conventional Convection Oven (Full Size) |  | unit |  | TRM Version 5.0 | 2020-11-12 | 865 | 0 | 40.1 | 0 | 0 | 0 | 1200 | 0 | 12 | Direct Install | 0.2 | 1 | 1
COM-FR-FS-324-02 | Replaced | Updated in TRM Version 7.0 | Commercial | Fryer |  | New Construction/Natural Replacement | food service | Energy Star Fryer | Energy Star Rated Fryer | Non-Energy Star rated Fryer |  | unit |  | TRM Version 5.0 | 2020-11-12 | 1408 | 0 | 0 | 0 | 0 | 0 | 2476 | 0 | 12 | Direct Install | 0.2 | 1 | 1
COM-RO-FS-651-03 | Replaced | Updated in V6.0 | Commercial | Rack Oven |  | New Construction/Natural Replacement | food service | ENERGY STAR Rack Oven | Energy Star Rated Rack Oven, Double | Conventiona rack oven |  | unit |  | TRM Version 5.0 | 2020-11-12 | 1076 | 0 | 1685 | 0 | 0 | 0 | 2591 | 0 | 12 | Direct Install | 0.2 | 1 | 1
COM-RO-FS-650-03 | Replaced | Updated in V6.0 | Commercial | Rack Oven |  | New Construction/Natural Replacement | food service | ENERGY STAR Rack Oven | Energy Star Rated Rack Oven, Single | Conventiona rack oven |  | unit |  | TRM Version 5.0 | 2020-11-12 | 830 | 0 | 749 | 0 | 0 | 0 | 1544 | 0 | 12 | Direct Install | 0.2 | 1 | 1
COM-SC-FS-325-02 | Replaced | Updated in TRM Version 7.0 | Commercial | Steam Cookers |  | New Construction/Natural Replacement | food service | Energy Star Steam Cookers | Energy Star Rated Steam Cooker | Boiler-based steam cooker |  | unit |  | TRM Version 5.0 | 2020-11-12 | 8889 | 0 | 0 | 0 | 340142 | 0 | 3880 | 0 | 12 | Direct Install | 0.2 | 1 | 1
COM-DW-WH-555-03 | Replaced | Updated in TRM Version 6.0 | Commercial | Dishwasher |  | New Construction/Natural Replacement | water heating | Energy Star Dishwasher | Multi Tank Conveyor - High Temperature | Non-Energy Star Dishwasher |  | unit |  | TRM Version 5.0 | 2020-11-12 | 2260 | 0 | 9680 | 0 | 304677 | 0 | 1386 | 0 | 20 | Direct Install | 0.27 | 1 | 1
COM-DW-WH-556-03 | Replaced | Updated in TRM Version 6.0 | Commercial | Dishwasher |  | New Construction/Natural Replacement | water heating | Energy Star Dishwasher | Multi Tank Conveyor - Low Temperature | Non-Energy Star Dishwasher |  | unit |  | TRM Version 5.0 | 2020-11-12 | 2383 | 0 | 0 | 0 | 354276 | 0 | 1386 | 0 | 20 | Direct Install | 0.27 | 1 | 1
COM-OL-WH-329-02 | Replaced | Updated in TRM Version 6.0 | Commercial | Ozone Laundry |  | New Construction/Retrofit | water heating | Commercial Ozone Laundry Treatment | Ozone Treatment Tunnel Washer <= 120 lbs | Commercial laundry with no ozone treatment system |  |  | lbs/yr | TRM Version 5.0 | 2020-11-12 | 0 | 0.0305 | 0 | 0.0015 | 0 | 1.27 | 71429 | 0 | 15 | Direct Install | 0.08 | 1 | 1
COM-OL-WH-331-02 | Replaced | Updated in TRM Version 6.0 | Commercial | Ozone Laundry |  | New Construction/Retrofit | water heating | Commercial Ozone Laundry Treatment | Ozone Treatment Tunnel Washer=> 500 lbs | Commercial laundry with no ozone treatment system |  |  | lbs/yr | TRM Version 5.0 | 2020-11-12 | 0 | 0.0305 | 0 | 0.0015 | 0 | 1.27 | 228571 | 0 | 15 | Direct Install | 0.08 | 1 | 1
COM-OL-WH-330-02 | Replaced | Updated in TRM Version 6.0 | Commercial | Ozone Laundry |  | New Construction/Retrofit | water heating | Commercial Ozone Laundry Treatment | Ozone Treatment Tunnel Washer121 lbs to 499 lbs | Commercial laundry with no ozone treatment system |  |  | lbs/yr | TRM Version 5.0 | 2020-11-12 | 0 | 0.0305 | 0 | 0.0015 | 0 | 1.27 | 150000 | 0 | 15 | Direct Install | 0.08 | 1 | 1
COM-OL-WH-326-02 | Replaced | Updated in TRM Version 6.0 | Commercial | Ozone Laundry |  | New Construction/Retrofit | water heating | Commercial Ozone Laundry Treatment | Ozone Treatment Washer extractor =< 60 lbs | Commercial laundry with no ozone treatment system |  |  | lbs/yr | TRM Version 5.0 | 2020-11-12 | 0 | 0.0383 | 0 | 0.00213 | 0 | 2.08 | 15714 | 0 | 15 | Direct Install | 0.08 | 1 | 1
COM-OL-WH-327-02 | Replaced | Updated in TRM Version 6.0 | Commercial | Ozone Laundry |  | New Construction/Retrofit | water heating | Commercial Ozone Laundry Treatment | Ozone Treatment Washer extractor 61 lbs to 499 lbs | Commercial laundry with no ozone treatment system |  |  | lbs/yr | TRM Version 5.0 | 2020-11-12 | 0 | 0.0383 | 0 | 0.00213 | 0 | 2.08 | 35714 | 0 | 15 | Direct Install | 0.08 | 1 | 1
COM-OL-WH-328-02 | Replaced | Updated in TRM Version 6.0 | Commercial | Ozone Laundry |  | New Construction/Retrofit | water heating | Commercial Ozone Laundry Treatment | Ozone Treatment Washer extractor=> 500 lbs | Commercial laundry with no ozone treatment system |  |  | lbs/yr | TRM Version 5.0 | 2020-11-12 | 0 | 0.0383 | 0 | 0.00213 | 0 | 2.08 | 44286 | 0 | 15 | Direct Install | 0.08 | 1 | 1
COM-UB-FS-332-02 | Replaced | Updated in TRM Version 7.0 | Commercial | Under-Fired Broilers |  | New Construction/Natural Replacement | food service | High Efficiency Under-Fired Broilers - 3 foot | pre-heat =< 40,500 Btu and cooking energy rate =< 72,000 Btu/hr | Conventional Efficiency Under-Fired Broiler | pre-heat =< 48,000 Btu and cooking energy rate =< 96,000 Btu/hr | unit |  | TRM Version 5.0 | 2020-11-12 | 2511 | 0 | 0 | 0 | 0 | 0 | 1900 | 0 | 12 | Direct Install | 0.2 | 1 | 1
COM-UB-FS-333-02 | Replaced | Updated in TRM Version 7.0 | Commercial | Under-Fired Broilers |  | New Construction/Natural Replacement | food service | High Efficiency Under-Fired Broilers - 4 foot | pre-heat 40,501 to 54,000 Btu and a cooking energy rate 72,001 to 96,000 Btu/hr | Conventional Efficiency Under-Fired Broiler | pre-heat 48,001 to 64,000 Btu and a cooking energy rate 96,000 to 128,000 Btu/hr | unit |  | TRM Version 5.0 | 2020-11-12 | 3347 | 0 | 0 | 0 | 0 | 0 | 1900 | 0 | 12 | Direct Install | 0.2 | 1 | 1
COM-UB-FS-334-02 | Replaced | Updated in TRM Version 7.0 | Commercial | Under-Fired Broilers |  | New Construction/Natural Replacement | food service | High Efficiency Under-Fired Broilers - 5 foot | pre-heat 54,001 to 67,500 Btu and cooking energy rate 96,001 to 120,000 Btu/hr | Conventional Efficiency Under-Fired Broiler | pre-heat 64,001 to 80,000 Btu and cooking energy rate 128,001 to 160,000 Btu/hr | unit |  | TRM Version 5.0 | 2020-11-12 | 4184 | 0 | 0 | 0 | 0 | 0 | 1900 | 0 | 12 | Direct Install | 0.2 | 1 | 1
COM-UB-FS-335-02 | Replaced | Updated in TRM Version 7.0 | Commercial | Under-Fired Broilers |  | New Construction/Natural Replacement | food service | High Efficiency Under-Fired Broilers - 6 foot | pre-heat 67,501 to 81,000 Btu and cooking energy rate 120,001 to 144,000 Btu/hr | Conventional Efficiency Under-Fired Broiler | pre-heat 80,001 to 96,000 Btu and cooking energy rate 160,001 to 192,000 Btu/hr | unit |  | TRM Version 5.0 | 2020-11-12 | 5021 | 0 | 0 | 0 | 0 | 0 | 1900 | 0 | 12 | Direct Install | 0.2 | 1 | 1
COM-DW-WH-553-03 | Replaced | Updated in TRM Version 6.0 | Commercial | Dishwasher |  | New Construction/Natural Replacement | water heating | Energy Star Dishwasher | Single Tank Conveyor – High Temperature | Non-Energy Star Dishwasher |  | unit |  | TRM Version 5.0 | 2020-11-12 | 540 | 0 | 4251 | 0 | 80303 | 0 | 2929 | 0 | 20 | Direct Install | 0.27 | 1 | 1
COM-DW-WH-554-03 | Replaced | Updated in TRM Version 6.0 | Commercial | Dishwasher |  | New Construction/Natural Replacement | water heating | Energy Star Dishwasher | Single Tank Conveyor - Low Temperature | Non-Energy Star Dishwasher |  | unit |  | TRM Version 5.0 | 2020-11-12 | 1652 | 0 | 0 | 0 | 245631 | 0 | 0 | 0 | 20 | Direct Install | 0.27 | 1 | 1
COM-DW-WH-551-03 | Replaced | Updated in TRM Version 6.0 | Commercial | Dishwasher |  | New Construction/Natural Replacement | water heating | Energy Star Dishwasher | Stationary Single Tank Door – High Temperature | Non-Energy Star Dishwasher |  | unit |  | TRM Version 5.0 | 2020-11-12 | 890 | 0 | 4173 | 0 | 132263 | 0 | 1100 | 0 | 15 | Direct Install | 0.2 | 1 | 1
COM-DW-WH-552-03 | Replaced | Updated in TRM Version 6.0 | Commercial | Dishwasher |  | New Construction/Natural Replacement | water heating | Energy Star Dishwasher | Stationary Single Tank Door – Low Temperature | Non-Energy Star Dishwasher |  | unit |  | TRM Version 5.0 | 2020-11-12 | 2256 | 0 | 0 | 0 | 304205 | 0 | 0 | 0 | 15 | Direct Install | 0.2 | 1 | 1
COM-DW-WH-549-03 | Replaced | Updated in TRM Version 6.0 | Commercial | Dishwasher |  | New Construction/Natural Replacement | water heating | Energy Star Dishwasher | Undercounter – High Temperature | Non-Energy Star Dishwasher |  | unit |  | TRM Version 5.0 | 2020-11-12 | 137 | 0 | 1791 | 0 | 20371 | 0 | 171 | 0 | 10 | Direct Install | 0.4 | 1 | 1
COM-DW-WH-550-03 | Replaced | Updated in TRM Version 6.0 | Commercial | Dishwasher |  | New Construction/Natural Replacement | water heating | Energy Star Dishwasher | Undercounter – Low Temperature | Non-Energy Star Dishwasher |  | unit |  | TRM Version 5.0 | 2020-11-12 | 322 | 0 | 0 | 0 | 47827 | 0 | 71 | 0 | 10 | Direct Install | 0.4 | 1 | 1
COM-CU-SH-515-02 | Replaced | Updated in TRM Version 8.0 | Commercial | Condensing Unit Heater |  | Natural Replacement | space heating | Condensing Unit Heater | 125-200 kBtu/hr 90% Thermal Efficiency, 89% Annual Efficiency | Non-Condensing Unit Heater | 80% Thermal Efficiency, 78% Annual Efficiency |  | kBtu/hr input capacity | TRM Version 6.0 | 2021-12-16 | 0 | 7.89 | -530 | 0 | 0 | 0 | 0 | 16.08 | 18 | Direct Install | 0 | 1 | 1
COM-IH-SH-577-02 | Retired | retired in TRM 6.0 | Commercial | Infrared Heaters |  | Retrofit | space heating | 2-Stage Infrared Heaters | 0 - 49,999 BTU/hr | Regular Unit Heater |  |  | kBtu/hr input capacity | TRM Version 5.0 | 2020-11-12 | 0 | 13.1 | 0 | 0 | 0 | 0 | 0 | 30.28 | 17 | Direct Install | 0.33 | 1 | 1
COM-IH-SH-580-02 | Retired | retired in TRM 6.0 | Commercial | Infrared Heaters |  | New Construction | space heating | 2-Stage Infrared Heaters | 0 - 49,999 BTU/hr | Regular Unit Heater |  |  | kBtu/hr input capacity | TRM Version 5.0 | 2020-11-12 | 0 | 9.8 | 0 | 0 | 0 | 0 | 0 | 11.22 | 17 | Direct Install | 0.33 | 1 | 1
COM-IH-SH-583-02 | Retired | retired in TRM 6.0 | Commercial | Infrared Heaters |  | Retrofit | space heating | Single Stage & High Intensity Infrared Heaters | 0 - 49,999 BTU/hr | Regular Unit Heater |  |  | kBtu/hr input capacity | TRM Version 5.0 | 2020-11-12 | 0 | 11.5 | 0 | 0 | 0 | 0 | 0 | 30.28 | 17 | Direct Install | 0.33 | 1 | 1
COM-IH-SH-586-02 | Retired | retired in TRM 6.0 | Commercial | Infrared Heaters |  | New Construction | space heating | Single Stage & High Intensity Infrared Heaters | 0 - 49,999 BTU/hr | Regular Unit Heater |  |  | kBtu/hr input capacity | TRM Version 5.0 | 2020-11-12 | 0 | 8.6 | 0 | 0 | 0 | 0 | 0 | 11.22 | 17 | Direct Install | 0.33 | 1 | 1
COM-IH-SH-579-02 | Retired | retired in TRM 6.0 | Commercial | Infrared Heaters |  | Retrofit | space heating | 2-Stage Infrared Heaters | 165,000 - 300,000 BTU/hr | Regular Unit Heater |  |  | kBtu/hr input capacity | TRM Version 5.0 | 2020-11-12 | 0 | 13.1 | 1040 | 0 | 0 | 0 | 0 | 30.28 | 17 | Direct Install | 0.33 | 1 | 1
COM-IH-SH-582-02 | Retired | retired in TRM 6.0 | Commercial | Infrared Heaters |  | New Construction | space heating | 2-Stage Infrared Heaters | 165,000 - 300,000 BTU/hr | Regular Unit Heater |  |  | kBtu/hr input capacity | TRM Version 5.0 | 2020-11-12 | 0 | 9.8 | 510 | 0 | 0 | 0 | 0 | 11.22 | 17 | Direct Install | 0.33 | 1 | 1
COM-IH-SH-585-02 | Retired | retired in TRM 6.0 | Commercial | Infrared Heaters |  | Retrofit | space heating | Single Stage & High Intensity Infrared Heaters | 165,000 - 300,000 BTU/hr | Regular Unit Heater |  |  | kBtu/hr input capacity | TRM Version 5.0 | 2020-11-12 | 0 | 11.5 | 1040 | 0 | 0 | 0 | 0 | 30.28 | 17 | Direct Install | 0.33 | 1 | 1
COM-IH-SH-588-02 | Retired | retired in TRM 6.0 | Commercial | Infrared Heaters |  | New Construction | space heating | Single Stage & High Intensity Infrared Heaters | 165,000 - 300,000 BTU/hr | Regular Unit Heater |  |  | kBtu/hr input capacity | TRM Version 5.0 | 2020-11-12 | 0 | 8.6 | 510 | 0 | 0 | 0 | 0 | 11.22 | 17 | Direct Install | 0.33 | 1 | 1
COM-IH-SH-578-02 | Retired | retired in TRM 6.0 | Commercial | Infrared Heaters |  | Retrofit | space heating | 2-Stage Infrared Heaters | 50,000 - 164,999 BTU/hr | Regular Unit Heater |  |  | kBtu/hr input capacity | TRM Version 5.0 | 2020-11-12 | 0 | 13.1 | 300 | 0 | 0 | 0 | 0 | 30.28 | 17 | Direct Install | 0.33 | 1 | 1
COM-IH-SH-581-02 | Retired | retired in TRM 6.0 | Commercial | Infrared Heaters |  | New Construction | space heating | 2-Stage Infrared Heaters | 50,000 - 164,999 BTU/hr | Regular Unit Heater |  |  | kBtu/hr input capacity | TRM Version 5.0 | 2020-11-12 | 0 | 9.8 | 225 | 0 | 0 | 0 | 0 | 11.22 | 17 | Direct Install | 0.33 | 1 | 1
COM-IH-SH-584-02 | Retired | retired in TRM 6.0 | Commercial | Infrared Heaters |  | Retrofit | space heating | Single Stage & High Intensity Infrared Heaters | 50,000 - 164,999 BTU/hr | Regular Unit Heater |  |  | kBtu/hr input capacity | TRM Version 5.0 | 2020-11-12 | 0 | 11.5 | 300 | 0 | 0 | 0 | 0 | 30.28 | 17 | Direct Install | 0.33 | 1 | 1
COM-IH-SH-587-02 | Retired | retired in TRM 6.0 | Commercial | Infrared Heaters |  | New Construction | space heating | Single Stage & High Intensity Infrared Heaters | 50,000 - 164,999 BTU/hr | Regular Unit Heater |  |  | kBtu/hr input capacity | TRM Version 5.0 | 2020-11-12 | 0 | 8.6 | 225 | 0 | 0 | 0 | 0 | 11.22 | 17 | Direct Install | 0.33 | 1 | 1
COM-CU-SH-518-02 | Replaced | Updated in TRM Version 8.0 | Commercial | Condensing Unit Heater |  | New Construction | space heating | Condensing Unit Heater | 125-200 kBtu/hr 90% Thermal Efficiency, 89% Annual Efficiency | Non-Condensing Unit Heater | 80% Thermal Efficiency, 78% Annual Efficiency |  | kBtu/hr input capacity | TRM Version 6.0 | 2021-12-16 | 0 | 5.92 | -398 | 0 | 0 | 0 | 0 | 16.08 | 18 | Direct Install | 0 | 1 | 1
COM-CU-SH-516-02 | Replaced | Updated in TRM Version 8.0 | Commercial | Condensing Unit Heater |  | Natural Replacement | space heating | Condensing Unit Heater | 225-300 kBtu/hr 90% Thermal Efficiency, 89% Annual Efficiency | Non-Condensing Unit Heater | 80% Thermal Efficiency, 78% Annual Efficiency |  | kBtu/hr input capacity | TRM Version 6.0 | 2021-12-16 | 0 | 7.89 | -546 | 0 | 0 | 0 | 0 | 16.08 | 18 | Direct Install | 0 | 1 | 1
COM-CU-SH-519-02 | Replaced | Updated in TRM Version 8.0 | Commercial | Condensing Unit Heater |  | New Construction | space heating | Condensing Unit Heater | 225-300 kBtu/hr 90% Thermal Efficiency, 89% Annual Efficiency | Non-Condensing Unit Heater | 80% Thermal Efficiency, 78% Annual Efficiency |  | kBtu/hr input capacity | TRM Version 6.0 | 2021-12-16 | 0 | 5.92 | -410 | 0 | 0 | 0 | 0 | 16.08 | 18 | Direct Install | 0 | 1 | 1
COM-CU-SH-514-02 | Replaced | Updated in TRM Version 8.0 | Commercial | Condensing Unit Heater |  | Natural Replacement | space heating | Condensing Unit Heater | 30-100 kBtu/hr - 90% Thermal Efficiency, 89% Annual Efficiency | Non-Condensing Unit Heater | 80% Thermal Efficiency, 78% Annual Efficiency |  | kBtu/hr input capacity | TRM Version 6.0 | 2021-12-16 | 0 | 7.89 | -296 | 0 | 0 | 0 | 0 | 16.08 | 18 | Direct Install | 0 | 1 | 1
COM-CU-SH-517-02 | Replaced | Updated in TRM Version 8.0 | Commercial | Condensing Unit Heater |  | New Construction | space heating | Condensing Unit Heater | 30-100 kBtu/hr - 90% Thermal Efficiency, 89% Annual Efficiency | Non-Condensing Unit Heater | 80% Thermal Efficiency, 78% Annual Efficiency |  | kBtu/hr input capacity | TRM Version 6.0 | 2021-12-16 | 0 | 5.92 | -222 | 0 | 0 | 0 | 0 | 16.08 | 18 | Direct Install | 0 | 1 | 1
COM-DW-WH-555-03 | Replaced | Updated in TRM Version 7.0; revised from TRM Version 5.0: natural gas, electric savings, and water savings | Commercial | Dishwasher |  | New Construction/Natural Replacement | water heating | Energy Star Dishwasher | Multi Tank Conveyor - High Temperature | Non-Energy Star Dishwasher |  | unit |  | TRM Version 6.0 | 2021-12-16 | 2260 | 0 | 10673 | 0 | 335926 | 0 | 1386 | 0 | 20 | Direct Install | 0.27 | 1 | 1
COM-DW-WH-556-03 | Replaced | Updated in TRM Version 7.0; revised from TRM Version 5.0: natural gas, electric savings, and water savings | Commercial | Dishwasher |  | New Construction/Natural Replacement | water heating | Energy Star Dishwasher | Multi Tank Conveyor - Low Temperature | Non-Energy Star Dishwasher |  | unit |  | TRM Version 6.0 | 2021-12-16 | 2628 | 0 | 0 | 0 | 390612 | 0 | 1386 | 0 | 20 | Direct Install | 0.27 | 1 | 1
COM-DW-WH-553-03 | Replaced | Updated in TRM Version 7.0; revised from TRM Version 5.0: natural gas, electric savings, and water savings | Commercial | Dishwasher |  | New Construction/Natural Replacement | water heating | Energy Star Dishwasher | Single Tank Conveyor – High Temperature | Non-Energy Star Dishwasher |  | unit |  | TRM Version 6.0 | 2021-12-16 | 596 | 0 | 4686 | 0 | 88539 | 0 | 2929 | 0 | 20 | Direct Install | 0.27 | 1 | 1
COM-DW-WH-554-03 | Replaced | Updated in TRM Version 7.0; revised from TRM Version 5.0: natural gas, electric savings, and water savings | Commercial | Dishwasher |  | New Construction/Natural Replacement | water heating | Energy Star Dishwasher | Single Tank Conveyor - Low Temperature | Non-Energy Star Dishwasher |  | unit |  | TRM Version 6.0 | 2021-12-16 | 1822 | 0 | 0 | 0 | 270824 | 0 | 0 | 0 | 20 | Direct Install | 0.27 | 1 | 1
COM-DW-WH-551-03 | Replaced | Updated in TRM Version 7.0; revised from TRM Version 5.0: natural gas, electric savings, and water savings | Commercial | Dishwasher |  | New Construction/Natural Replacement | water heating | Energy Star Dishwasher | Stationary Single Tank Door – High Temperature | Non-Energy Star Dishwasher |  | unit |  | TRM Version 6.0 | 2021-12-16 | 981 | 0 | 4601 | 0 | 145828 | 0 | 1100 | 0 | 15 | Direct Install | 0.2 | 1 | 1
COM-DW-WH-552-03 | Replaced | Updated in TRM Version 7.0; revised from TRM Version 5.0: natural gas, electric savings, and water savings | Commercial | Dishwasher |  | New Construction/Natural Replacement | water heating | Energy Star Dishwasher | Stationary Single Tank Door – Low Temperature | Non-Energy Star Dishwasher |  | unit |  | TRM Version 6.0 | 2021-12-16 | 2256 | 0 | 0 | 0 | 335406 | 0 | 0 | 0 | 15 | Direct Install | 0.2 | 1 | 1
COM-DW-WH-549-03 | Replaced | Updated in TRM Version 7.0; revised from TRM Version 5.0: natural gas, electric savings, and water savings | Commercial | Dishwasher |  | New Construction/Natural Replacement | water heating | Energy Star Dishwasher | Undercounter – High Temperature | Non-Energy Star Dishwasher |  | unit |  | TRM Version 6.0 | 2021-12-16 | 151 | 0 | 1975 | 0 | 22460 | 0 | 171 | 0 | 10 | Direct Install | 0.4 | 1 | 1
COM-DS-SH-557-03 | Current |  | Commercial | Dock Door Seals |  | Retrofit | space heating | Dock Door Seals | 8' x 8' | Dock door with deteriorated seals |  | unit |  | TRM Version 5.0 | 2020-11-12 | 1897 | 0 | 451 | 0 | 0 | 0 | 1425 | 0 | 10 | Direct Install | 0.05 | 1 | 1
COM-DS-SH-561-03 | Current |  | Commercial | Dock Door Seals |  | Retrofit | space heating | Dock Door Seals | 8' x 8' | Dock door without seals |  | unit |  | TRM Version 5.0 | 2020-11-12 | 4853 | 0 | 1155 | 0 | 0 | 0 | 1263 | 0 | 10 | Direct Install | 0.05 | 1 | 1
COM-DS-SH-558-03 | Current |  | Commercial | Dock Door Seals |  | Retrofit | space heating | Dock Door Seals | 8' x 9' | Dock door with deteriorated seals |  | unit |  | TRM Version 5.0 | 2020-11-12 | 1977 | 0 | 481 | 0 | 0 | 0 | 1580 | 0 | 10 | Direct Install | 0.05 | 1 | 1
COM-DS-SH-562-03 | Current |  | Commercial | Dock Door Seals |  | Retrofit | space heating | Dock Door Seals | 8' x 9' | Dock door without seals |  | unit |  | TRM Version 5.0 | 2020-11-12 | 4988 | 0 | 1214 | 0 | 0 | 0 | 1417 | 0 | 10 | Direct Install | 0.05 | 1 | 1
RES-AT-SH-321-01 | Current |  | Residential | Adaptive Thermostat |  | Retrofit | space heating | Adaptive Thermostats - Direct Install | Adaptive Thermostat | Non-Programmable Thermostat |  | unit |  | TRM Version 5.0 | 2020-11-12 | 217 | 0 | 235 | 0 | 0 | 0 | 300 | 0 | 15 | Direct Install | 0.04 | 1 | 1
RES-AT-SH-322-01 | Current |  | Residential | Adaptive Thermostat |  | Retrofit | space heating | Adaptive Thermostats - Direct Install | Adaptive Thermostat | Programmable Thermostat |  | unit |  | TRM Version 5.0 | 2020-11-12 | 173 | 0 | 235 | 0 | 0 | 0 | 300 | 0 | 15 | Direct Install | 0.04 | 1 | 1
RES-AT-SH-324-01 | Current |  | Residential | Adaptive Thermostat |  | Retrofit | space heating | Adaptive Thermostats - Direct Install | Adaptive Thermostat | Non-Programmable Thermostat | No central air conditioning | unit |  | TRM Version 5.0 | 2020-11-12 | 217 | 0 | 0 | 0 | 0 | 0 | 300 | 0 | 15 | Direct Install | 0.04 | 1 | 1
RES-AT-SH-325-01 | Current |  | Residential | Adaptive Thermostat |  | Retrofit | space heating | Adaptive Thermostats - Direct Install | Adaptive Thermostat | Programmable Thermostat | No central air conditioning | unit |  | TRM Version 5.0 | 2020-11-12 | 173 | 0 | 0 | 0 | 0 | 0 | 300 | 0 | 15 | Direct Install | 0.04 | 1 | 1
COM-DW-WH-550-03 | Replaced | Updated in TRM Version 7.0; revised from TRM Version 5.0: natural gas, electric savings, and water savings | Commercial | Dishwasher |  | New Construction/Natural Replacement | water heating | Energy Star Dishwasher | Undercounter – Low Temperature | Non-Energy Star Dishwasher |  | unit |  | TRM Version 6.0 | 2021-12-16 | 355 | 0 | 0 | 0 | 52733 | 0 | 71 | 0 | 10 | Direct Install | 0.4 | 1 | 1
MRS-FA-WH-461-08 | Current |  | Commercial | Faucet Aerator | Multi-residential | Retrofit | water heating | Faucet Aerator | Bathroom, 1.0 GPM | Standard flow bathroom aerator (code compliant) | 2.2 GPM | unit |  | TRM Version 7.0 | 2022-11-30 | 6.65 | 0 | 0 | 0 | 2501 | 0 | 0.6 | 0 | 10 | Direct Install | 0.1 | 1 | 1
RES-FA-WH-461-05 | Current |  | Residential | Faucet Aerator |  | Retrofit | water heating | Faucet Aerator | Bathroom, 1.0 GPM | Standard flow bathroom aerator (code compliant) | 2.2 GPM | unit |  | TRM Version 7.0 | 2022-11-30 | 6.65 | 0 | 0 | 0 | 2501 | 0 | 0.6 | 0 | 10 | Direct Install | 0 | 1 | 1
MRS-FA-WH-460-08 | Current |  | Commercial | Faucet Aerator | Multi-residential | Retrofit | water heating | Faucet Aerator | Bathroom, 1.5 GPM | Standard flow bathroom aerator (code compliant) | 2.2 GPM | unit |  | TRM Version 7.0 | 2022-11-30 | 3.88 | 0 | 0 | 0 | 1459 | 0 | 0.6 | 0 | 10 | Direct Install | 0.1 | 1 | 1
RES-FA-WH-460-05 | Current |  | Residential | Faucet Aerator |  | Retrofit | water heating | Faucet Aerator | Bathroom, 1.5 GPM | Standard flow bathroom aerator (code compliant) | 2.2 GPM | unit |  | TRM Version 7.0 | 2022-11-30 | 3.88 | 0 | 0 | 0 | 1459 | 0 | 0.6 | 0 | 10 | Direct Install | 0 | 1 | 1
COM-CM-SH-496-02 | Current |  | Commercial | Condensing Make Up Air Unit | Commercial | New Construction/Natural Replacement | space heating | Condensing Make Up Air Unit (MUA) - Commercial | Constant Speed | Conventional MUA | 80% Thermal Efficiency |  | CFM | TRM Version 5.0 | 2020-11-12 | 0 | 0.407 | 0 | 0 | 0 | 0 | 870 | 0.66 | 20 | Direct Install | 0.05 | 1 | 1
COM-CM-SH-499-02 | Current |  | Commercial | Condensing Make Up Air Unit | Multi-Residential and Long Term Care | New Construction/Natural Replacement | space heating | Condensing Make Up Air Unit (MUA) - Commercial | Constant Speed | Conventional MUA | 80% Thermal Efficiency |  | CFM | TRM Version 5.0 | 2020-11-12 | 0 | 0.919 | 0 | 0 | 0 | 0 | 870 | 0.66 | 20 | Direct Install | 0.05 | 1 | 1
COM-HRV-SH-336-02 | Current |  | Commercial | Heat Recovery Ventialation | High Use | New Construction/Natural Replacement | space heating | High Efficient 65% Heat Recovery Ventilation High Use Group (Multi-Residential, Health Care, Nursing Homes) | HRV with Minimum 65% Sensible Heat Recovery Effectiveness at 32°F | HRV with Minimum 55% Sensible Heat Recovery Effectiveness as per Ontario Building Code 2017 |  |  | CFM | TRM Version 5.0 | 2020-11-12 | 0 | 0.7 | 0 | 0 | 0 | 0 | 0 | 1 | 14 | Direct Install | 0.05 | 1 | 1
COM-HRV-SH-337-02 | Current |  | Commercial | Heat Recovery Ventialation | Low Use | New Construction/Natural Replacement | space heating | High Efficient 65% Heat Recovery Ventilation Low Use Group (Office, Warehouse, School) | HRV with Minimum 65% Sensible Heat Recovery Effectiveness at 32°F | HRV with Minimum 55% Sensible Heat Recovery Effectiveness as per Ontario Building Code 2017 |  |  | CFM | TRM Version 5.0 | 2020-11-12 | 0 | 0.25 | 0 | 0 | 0 | 0 | 0 | 1 | 14 | Direct Install | 0.05 | 1 | 1
COM-IH-SH-577-01 | Retired | retired in TRM 6.0 | Commercial | Infrared Heaters |  | Retrofit | space heating | 2-Stage Infrared Heaters | 0 - 49,999 BTU/hr | Regular Unit Heater |  |  | kBtu/hr input capacity | TRM Version 5.0 | 2020-11-12 | 0 | 13.1 | 0 | 0 | 0 | 0 | 0 | 30.28 | 17 | Downstream | 0.89 | 1 | 1.0268
COM-IH-SH-580-01 | Retired | retired in TRM 6.0 | Commercial | Infrared Heaters |  | New Construction | space heating | 2-Stage Infrared Heaters | 0 - 49,999 BTU/hr | Regular Unit Heater |  |  | kBtu/hr input capacity | TRM Version 5.0 | 2020-11-12 | 0 | 9.8 | 0 | 0 | 0 | 0 | 0 | 11.22 | 17 | Downstream | 0.89 | 1 | 1.0268
COM-IH-SH-583-01 | Retired | retired in TRM 6.0 | Commercial | Infrared Heaters |  | Retrofit | space heating | Single Stage & High Intensity Infrared Heaters | 0 - 49,999 BTU/hr | Regular Unit Heater |  |  | kBtu/hr input capacity | TRM Version 5.0 | 2020-11-12 | 0 | 11.5 | 0 | 0 | 0 | 0 | 0 | 30.28 | 17 | Downstream | 0.89 | 1 | 1.0268
COM-IH-SH-586-01 | Retired | retired in TRM 6.0 | Commercial | Infrared Heaters |  | New Construction | space heating | Single Stage & High Intensity Infrared Heaters | 0 - 49,999 BTU/hr | Regular Unit Heater |  |  | kBtu/hr input capacity | TRM Version 5.0 | 2020-11-12 | 0 | 8.6 | 0 | 0 | 0 | 0 | 0 | 11.22 | 17 | Downstream | 0.89 | 1 | 1.0268
COM-IH-SH-579-01 | Retired | retired in TRM 6.0 | Commercial | Infrared Heaters |  | Retrofit | space heating | 2-Stage Infrared Heaters | 165,000 - 300,000 BTU/hr | Regular Unit Heater |  |  | kBtu/hr input capacity | TRM Version 5.0 | 2020-11-12 | 0 | 13.1 | 1040 | 0 | 0 | 0 | 0 | 30.28 | 17 | Downstream | 0.89 | 1 | 1.0268
COM-IH-SH-582-01 | Retired | retired in TRM 6.0 | Commercial | Infrared Heaters |  | New Construction | space heating | 2-Stage Infrared Heaters | 165,000 - 300,000 BTU/hr | Regular Unit Heater |  |  | kBtu/hr input capacity | TRM Version 5.0 | 2020-11-12 | 0 | 9.8 | 510 | 0 | 0 | 0 | 0 | 11.22 | 17 | Downstream | 0.89 | 1 | 1.0268
COM-IH-SH-585-01 | Retired | retired in TRM 6.0 | Commercial | Infrared Heaters |  | Retrofit | space heating | Single Stage & High Intensity Infrared Heaters | 165,000 - 300,000 BTU/hr | Regular Unit Heater |  |  | kBtu/hr input capacity | TRM Version 5.0 | 2020-11-12 | 0 | 11.5 | 1040 | 0 | 0 | 0 | 0 | 30.28 | 17 | Downstream | 0.89 | 1 | 1.0268
COM-IH-SH-588-01 | Retired | retired in TRM 6.0 | Commercial | Infrared Heaters |  | New Construction | space heating | Single Stage & High Intensity Infrared Heaters | 165,000 - 300,000 BTU/hr | Regular Unit Heater |  |  | kBtu/hr input capacity | TRM Version 5.0 | 2020-11-12 | 0 | 8.6 | 510 | 0 | 0 | 0 | 0 | 11.22 | 17 | Downstream | 0.89 | 1 | 1.0268
COM-HRV-SH-338-02 | Current |  | Commercial | Heat Recovery Ventialation | Medium Use | New Construction/Natural Replacement | space heating | High Efficient 65% Heat Recovery Ventilation Medium Use Group (Hotel, Restaurant, Retail) | HRV with Minimum 65% Sensible Heat Recovery Effectiveness at 32°F | HRV with Minimum 55% Sensible Heat Recovery Effectiveness as per Ontario Building Code 2017 |  |  | CFM | TRM Version 5.0 | 2020-11-12 | 0 | 0.39 | 0 | 0 | 0 | 0 | 0 | 1 | 14 | Direct Install | 0.05 | 1 | 1
COM-HRV-SH-345-02 | Current |  | Commercial | Heat Recovery Ventialation | Multi-Family, Health Care and Nursing Homes | New Construction/Natural Replacement | space heating | High Efficient 65% Heat Recovery Ventilation High Use Group (Multi-Residential, Health Care, Nursing Homes) | HRV with Minimum 65% Sensible Heat Recovery Effectiveness at 32°F | HRV with Minimum 55% Sensible Heat Recovery Effectiveness as per Ontario Building Code 2017 |  |  | CFM | TRM Version 5.0 | 2020-11-12 | 0 | 0.7 | 0 | 0 | 0 | 0 | 0 | 1 | 14 | Direct Install | 0.05 | 1 | 1
COM-HRV-SH-346-02 | Current |  | Commercial | Heat Recovery Ventialation | Hotels | New Construction/Natural Replacement | space heating | High Efficient 65% Heat Recovery Ventilation Medium Use Group (Hotel, Restaurant, Retail) | HRV with Minimum 65% Sensible Heat Recovery Effectiveness at 32°F | HRV with Minimum 55% Sensible Heat Recovery Effectiveness as per Ontario Building Code 2017 |  |  | CFM | TRM Version 5.0 | 2020-11-12 | 0 | 0.5 | 0 | 0 | 0 | 0 | 0 | 1 | 14 | Direct Install | 0.05 | 1 | 1
COM-HRV-SH-347-02 | Current |  | Commercial | Heat Recovery Ventialation | Restaurant | New Construction/Natural Replacement | space heating | High Efficient 65% Heat Recovery Ventilation Medium Use Group (Hotel, Restaurant, Retail) | HRV with Minimum 65% Sensible Heat Recovery Effectiveness at 32°F | HRV with Minimum 55% Sensible Heat Recovery Effectiveness as per Ontario Building Code 2017 |  |  | CFM | TRM Version 5.0 | 2020-11-12 | 0 | 0.36 | 0 | 0 | 0 | 0 | 0 | 1 | 14 | Direct Install | 0.05 | 1 | 1
COM-HRV-SH-348-02 | Current |  | Commercial | Heat Recovery Ventialation | Retail | New Construction/Natural Replacement | space heating | High Efficient 65% Heat Recovery Ventilation Medium Use Group (Hotel, Restaurant, Retail) | HRV with Minimum 65% Sensible Heat Recovery Effectiveness at 32°F | HRV with Minimum 55% Sensible Heat Recovery Effectiveness as per Ontario Building Code 2017 |  |  | CFM | TRM Version 5.0 | 2020-11-12 | 0 | 0.3 | 0 | 0 | 0 | 0 | 0 | 1 | 14 | Direct Install | 0.05 | 1 | 1
COM-HRV-SH-349-02 | Current |  | Commercial | Heat Recovery Ventialation | Office | New Construction/Natural Replacement | space heating | High Efficient 65% Heat Recovery Ventilation Low Use Group (Office, Warehouse, School) | HRV with Minimum 65% Sensible Heat Recovery Effectiveness at 32°F | HRV with Minimum 55% Sensible Heat Recovery Effectiveness as per Ontario Building Code 2017 |  |  | CFM | TRM Version 5.0 | 2020-11-12 | 0 | 0.27 | 0 | 0 | 0 | 0 | 0 | 1 | 14 | Direct Install | 0.05 | 1 | 1
COM-HRV-SH-350-02 | Current |  | Commercial | Heat Recovery Ventialation | Warehouse | New Construction/Natural Replacement | space heating | High Efficient 65% Heat Recovery Ventilation Low Use Group (Office, Warehouse, School) | HRV with Minimum 65% Sensible Heat Recovery Effectiveness at 32°F | HRV with Minimum 55% Sensible Heat Recovery Effectiveness as per Ontario Building Code 2017 |  |  | CFM | TRM Version 5.0 | 2020-11-12 | 0 | 0.25 | 0 | 0 | 0 | 0 | 0 | 1 | 14 | Direct Install | 0.05 | 1 | 1
COM-HRV-SH-351-02 | Current |  | Commercial | Heat Recovery Ventialation | School | New Construction/Natural Replacement | space heating | High Efficient 65% Heat Recovery Ventilation Low Use Group (Office, Warehouse, School) | HRV with Minimum 65% Sensible Heat Recovery Effectiveness at 32°F | HRV with Minimum 55% Sensible Heat Recovery Effectiveness as per Ontario Building Code 2017 |  |  | CFM | TRM Version 5.0 | 2020-11-12 | 0 | 0.22 | 0 | 0 | 0 | 0 | 0 | 1 | 14 | Direct Install | 0.05 | 1 | 1
COM-HRV-SH-339-02 | Current |  | Commercial | Heat Recovery Ventialation | High Use | New Construction/Natural Replacement | space heating | High Efficient 75% Heat Recovery Ventilation High Use Group (Multi-Residential, Health Care, Nursing Homes) | HRV with Minimum 75% Sensible Heat Recovery Effectiveness at 32°F | HRV with Minimum 55% Sensible Heat Recovery Effectiveness as per Ontario Building Code 2017 |  |  | CFM | TRM Version 5.0 | 2020-11-12 | 0 | 1.39 | 0 | 0 | 0 | 0 | 0 | 2 | 14 | Direct Install | 0.05 | 1 | 1
COM-HRV-SH-340-02 | Current |  | Commercial | Heat Recovery Ventialation | Low Use | New Construction/Natural Replacement | space heating | High Efficient 75% Heat Recovery Ventilation Low Use Group (Office, Warehouse, School) | HRV with Minimum 75% Sensible Heat Recovery Effectiveness at 32°F | HRV with Minimum 55% Sensible Heat Recovery Effectiveness as per Ontario Building Code 2017 |  |  | CFM | TRM Version 5.0 | 2020-11-12 | 0 | 0.5 | 0 | 0 | 0 | 0 | 0 | 2 | 14 | Direct Install | 0.05 | 1 | 1
COM-HRV-SH-341-02 | Current |  | Commercial | Heat Recovery Ventialation | Medium Use | New Construction/Natural Replacement | space heating | High Efficient 75% Heat Recovery Ventilation Medium Use Group (Hotel, Restaurant, Retail) | HRV with Minimum 75% Sensible Heat Recovery Effectiveness at 32°F | HRV with Minimum 55% Sensible Heat Recovery Effectiveness as per Ontario Building Code 2017 |  |  | CFM | TRM Version 5.0 | 2020-11-12 | 0 | 0.78 | 0 | 0 | 0 | 0 | 0 | 2 | 14 | Direct Install | 0.05 | 1 | 1
COM-HRV-SH-352-02 | Current |  | Commercial | Heat Recovery Ventialation | Multi-Family, Health Care and Nursing Homes | New Construction/Natural Replacement | space heating | High Efficient 75% Heat Recovery Ventilation High Use Group (Multi-Residential, Health Care, Nursing Homes) | HRV with Minimum 75% Sensible Heat Recovery Effectiveness at 32°F | HRV with Minimum 55% Sensible Heat Recovery Effectiveness as per Ontario Building Code 2017 |  |  | CFM | TRM Version 5.0 | 2020-11-12 | 0 | 1.39 | 0 | 0 | 0 | 0 | 0 | 2 | 14 | Direct Install | 0.05 | 1 | 1
COM-HRV-SH-353-02 | Current |  | Commercial | Heat Recovery Ventialation | Hotels | New Construction/Natural Replacement | space heating | High Efficient 75% Heat Recovery Ventilation Medium Use Group (Hotel, Restaurant, Retail) | HRV with Minimum 75% Sensible Heat Recovery Effectiveness at 32°F | HRV with Minimum 55% Sensible Heat Recovery Effectiveness as per Ontario Building Code 2017 |  |  | CFM | TRM Version 5.0 | 2020-11-12 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 2 | 14 | Direct Install | 0.05 | 1 | 1
COM-HRV-SH-354-02 | Current |  | Commercial | Heat Recovery Ventialation | Restaurant | New Construction/Natural Replacement | space heating | High Efficient 75% Heat Recovery Ventilation Medium Use Group (Hotel, Restaurant, Retail) | HRV with Minimum 75% Sensible Heat Recovery Effectiveness at 32°F | HRV with Minimum 55% Sensible Heat Recovery Effectiveness as per Ontario Building Code 2017 |  |  | CFM | TRM Version 5.0 | 2020-11-12 | 0 | 0.72 | 0 | 0 | 0 | 0 | 0 | 2 | 14 | Direct Install | 0.05 | 1 | 1
COM-HRV-SH-355-02 | Current |  | Commercial | Heat Recovery Ventialation | Retail | New Construction/Natural Replacement | space heating | High Efficient 75% Heat Recovery Ventilation Medium Use Group (Hotel, Restaurant, Retail) | HRV with Minimum 75% Sensible Heat Recovery Effectiveness at 32°F | HRV with Minimum 55% Sensible Heat Recovery Effectiveness as per Ontario Building Code 2017 |  |  | CFM | TRM Version 5.0 | 2020-11-12 | 0 | 0.61 | 0 | 0 | 0 | 0 | 0 | 2 | 14 | Direct Install | 0.05 | 1 | 1
COM-HRV-SH-356-02 | Current |  | Commercial | Heat Recovery Ventialation | Office | New Construction/Natural Replacement | space heating | High Efficient 75% Heat Recovery Ventilation Low Use Group (Office, Warehouse, School) | HRV with Minimum 75% Sensible Heat Recovery Effectiveness at 32°F | HRV with Minimum 55% Sensible Heat Recovery Effectiveness as per Ontario Building Code 2017 |  |  | CFM | TRM Version 5.0 | 2020-11-12 | 0 | 0.53 | 0 | 0 | 0 | 0 | 0 | 2 | 14 | Direct Install | 0.05 | 1 | 1
COM-HRV-SH-357-02 | Current |  | Commercial | Heat Recovery Ventialation | Warehouse | New Construction/Natural Replacement | space heating | High Efficient 75% Heat Recovery Ventilation Low Use Group (Office, Warehouse, School) | HRV with Minimum 75% Sensible Heat Recovery Effectiveness at 32°F | HRV with Minimum 55% Sensible Heat Recovery Effectiveness as per Ontario Building Code 2017 |  |  | CFM | TRM Version 5.0 | 2020-11-12 | 0 | 0.51 | 0 | 0 | 0 | 0 | 0 | 2 | 14 | Direct Install | 0.05 | 1 | 1
COM-HRV-SH-358-02 | Current |  | Commercial | Heat Recovery Ventialation | School | New Construction/Natural Replacement | space heating | High Efficient 75% Heat Recovery Ventilation Low Use Group (Office, Warehouse, School) | HRV with Minimum 75% Sensible Heat Recovery Effectiveness at 32°F | HRV with Minimum 55% Sensible Heat Recovery Effectiveness as per Ontario Building Code 2017 |  |  | CFM | TRM Version 5.0 | 2020-11-12 | 0 | 0.45 | 0 | 0 | 0 | 0 | 0 | 2 | 14 | Direct Install | 0.05 | 1 | 1
COM-HRV-SH-342-02 | Current |  | Commercial | Heat Recovery Ventialation | High Use | New Construction/Natural Replacement | space heating | High Efficient 85% Heat Recovery Ventilation High Use Group (Multi-Residential, Health Care, Nursing Homes) | HRV with Minimum 85% Sensible Heat Recovery Effectiveness at 32°F | HRV with Minimum 55% Sensible Heat Recovery Effectiveness as per Ontario Building Code 2017 |  |  | CFM | TRM Version 5.0 | 2020-11-12 | 0 | 2.09 | 0 | 0 | 0 | 0 | 0 | 3 | 14 | Direct Install | 0.05 | 1 | 1
COM-HRV-SH-343-02 | Current |  | Commercial | Heat Recovery Ventialation | Low Use | New Construction/Natural Replacement | space heating | High Efficient 85% Heat Recovery Ventilation Low Use Group (Office, Warehouse, School) | HRV with Minimum 85% Sensible Heat Recovery Effectiveness at 32°F | HRV with Minimum 55% Sensible Heat Recovery Effectiveness as per Ontario Building Code 2017 |  |  | CFM | TRM Version 5.0 | 2020-11-12 | 0 | 0.74 | 0 | 0 | 0 | 0 | 0 | 3 | 14 | Direct Install | 0.05 | 1 | 1
COM-HRV-SH-344-02 | Current |  | Commercial | Heat Recovery Ventialation | Medium Use | New Construction/Natural Replacement | space heating | High Efficient 85% Heat Recovery Ventilation Medium Use Group (Hotel, Restaurant, Retail) | HRV with Minimum 85% Sensible Heat Recovery Effectiveness at 32°F | HRV with Minimum 55% Sensible Heat Recovery Effectiveness as per Ontario Building Code 2017 |  |  | CFM | TRM Version 5.0 | 2020-11-12 | 0 | 1.16 | 0 | 0 | 0 | 0 | 0 | 3 | 14 | Direct Install | 0.05 | 1 | 1
COM-HRV-SH-359-02 | Current |  | Commercial | Heat Recovery Ventialation | Multi-Family, Health Care and Nursing Homes | New Construction/Natural Replacement | space heating | High Efficient 85% Heat Recovery Ventilation High Use Group (Multi-Residential, Health Care, Nursing Homes) | HRV with Minimum 85% Sensible Heat Recovery Effectiveness at 32°F | HRV with Minimum 55% Sensible Heat Recovery Effectiveness as per Ontario Building Code 2017 |  |  | CFM | TRM Version 5.0 | 2020-11-12 | 0 | 2.09 | 0 | 0 | 0 | 0 | 0 | 3 | 14 | Direct Install | 0.05 | 1 | 1
COM-HRV-SH-360-02 | Current |  | Commercial | Heat Recovery Ventialation | Hotels | New Construction/Natural Replacement | space heating | High Efficient 85% Heat Recovery Ventilation Medium Use Group (Hotel, Restaurant, Retail) | HRV with Minimum 85% Sensible Heat Recovery Effectiveness at 32°F | HRV with Minimum 55% Sensible Heat Recovery Effectiveness as per Ontario Building Code 2017 |  |  | CFM | TRM Version 5.0 | 2020-11-12 | 0 | 1.49 | 0 | 0 | 0 | 0 | 0 | 3 | 14 | Direct Install | 0.05 | 1 | 1
COM-HRV-SH-361-02 | Current |  | Commercial | Heat Recovery Ventialation | Restaurant | New Construction/Natural Replacement | space heating | High Efficient 85% Heat Recovery Ventilation Medium Use Group (Hotel, Restaurant, Retail) | HRV with Minimum 85% Sensible Heat Recovery Effectiveness at 32°F | HRV with Minimum 55% Sensible Heat Recovery Effectiveness as per Ontario Building Code 2017 |  |  | CFM | TRM Version 5.0 | 2020-11-12 | 0 | 1.08 | 0 | 0 | 0 | 0 | 0 | 3 | 14 | Direct Install | 0.05 | 1 | 1
COM-IH-SH-578-01 | Retired | retired in TRM 6.0 | Commercial | Infrared Heaters |  | Retrofit | space heating | 2-Stage Infrared Heaters | 50,000 - 164,999 BTU/hr | Regular Unit Heater |  |  | kBtu/hr input capacity | TRM Version 5.0 | 2020-11-12 | 0 | 13.1 | 300 | 0 | 0 | 0 | 0 | 30.28 | 17 | Downstream | 0.89 | 1 | 1.0268
COM-IH-SH-581-01 | Retired | retired in TRM 6.0 | Commercial | Infrared Heaters |  | New Construction | space heating | 2-Stage Infrared Heaters | 50,000 - 164,999 BTU/hr | Regular Unit Heater |  |  | kBtu/hr input capacity | TRM Version 5.0 | 2020-11-12 | 0 | 9.8 | 225 | 0 | 0 | 0 | 0 | 11.22 | 17 | Downstream | 0.89 | 1 | 1.0268
COM-IH-SH-584-01 | Retired | retired in TRM 6.0 | Commercial | Infrared Heaters |  | Retrofit | space heating | Single Stage & High Intensity Infrared Heaters | 50,000 - 164,999 BTU/hr | Regular Unit Heater |  |  | kBtu/hr input capacity | TRM Version 5.0 | 2020-11-12 | 0 | 11.5 | 300 | 0 | 0 | 0 | 0 | 30.28 | 17 | Downstream | 0.89 | 1 | 1.0268
COM-IH-SH-587-01 | Retired | retired in TRM 6.0 | Commercial | Infrared Heaters |  | New Construction | space heating | Single Stage & High Intensity Infrared Heaters | 50,000 - 164,999 BTU/hr | Regular Unit Heater |  |  | kBtu/hr input capacity | TRM Version 5.0 | 2020-11-12 | 0 | 8.6 | 225 | 0 | 0 | 0 | 0 | 11.22 | 17 | Downstream | 0.89 | 1 | 1.0268
COM-HRV-SH-362-02 | Current |  | Commercial | Heat Recovery Ventialation | Retail | New Construction/Natural Replacement | space heating | High Efficient 85% Heat Recovery Ventilation Medium Use Group (Hotel, Restaurant, Retail) | HRV with Minimum 85% Sensible Heat Recovery Effectiveness at 32°F | HRV with Minimum 55% Sensible Heat Recovery Effectiveness as per Ontario Building Code 2017 |  |  | CFM | TRM Version 5.0 | 2020-11-12 | 0 | 0.91 | 0 | 0 | 0 | 0 | 0 | 3 | 14 | Direct Install | 0.05 | 1 | 1
COM-HRV-SH-363-02 | Current |  | Commercial | Heat Recovery Ventialation | Office | New Construction/Natural Replacement | space heating | High Efficient 85% Heat Recovery Ventilation Low Use Group (Office, Warehouse, School) | HRV with Minimum 85% Sensible Heat Recovery Effectiveness at 32°F | HRV with Minimum 55% Sensible Heat Recovery Effectiveness as per Ontario Building Code 2017 |  |  | CFM | TRM Version 5.0 | 2020-11-12 | 0 | 0.8 | 0 | 0 | 0 | 0 | 0 | 3 | 14 | Direct Install | 0.05 | 1 | 1
COM-HRV-SH-364-02 | Current |  | Commercial | Heat Recovery Ventialation | Warehouse | New Construction/Natural Replacement | space heating | High Efficient 85% Heat Recovery Ventilation Low Use Group (Office, Warehouse, School) | HRV with Minimum 85% Sensible Heat Recovery Effectiveness at 32°F | HRV with Minimum 55% Sensible Heat Recovery Effectiveness as per Ontario Building Code 2017 |  |  | CFM | TRM Version 5.0 | 2020-11-12 | 0 | 0.76 | 0 | 0 | 0 | 0 | 0 | 3 | 14 | Direct Install | 0.05 | 1 | 1
COM-HRV-SH-365-02 | Current |  | Commercial | Heat Recovery Ventialation | School | New Construction/Natural Replacement | space heating | High Efficient 85% Heat Recovery Ventilation Low Use Group (Office, Warehouse, School) | HRV with Minimum 85% Sensible Heat Recovery Effectiveness at 32°F | HRV with Minimum 55% Sensible Heat Recovery Effectiveness as per Ontario Building Code 2017 |  |  | CFM | TRM Version 5.0 | 2020-11-12 | 0 | 0.67 | 0 | 0 | 0 | 0 | 0 | 3 | 14 | Direct Install | 0.05 | 1 | 1
MRS-FA-WH-462-08 | Current |  | Commercial | Faucet Aerator | Multi-residential | Retrofit | water heating | Faucet Aerator | Kitchen, 1.0 GPM | Standard flow kitchen aerator (code compliant) | 2.2 GPM | unit |  | TRM Version 7.0 | 2022-11-30 | 20.57 | 0 | 0 | 0 | 7742 | 0 | 1.14 | 0 | 10 | Direct Install | 0.1 | 1 | 1
RES-FA-WH-462-05 | Current |  | Residential | Faucet Aerator |  | Retrofit | water heating | Faucet Aerator | Kitchen, 1.0 GPM | Standard flow kitchen aerator (code compliant) | 2.2 GPM | unit |  | TRM Version 7.0 | 2022-11-30 | 20.57 | 0 | 0 | 0 | 7742 | 0 | 1.14 | 0 | 10 | Direct Install | 0 | 1 | 1
MRS-FA-WH-463-08 | Current |  | Commercial | Faucet Aerator | Multi-residential | Retrofit | water heating | Faucet Aerator | Kitchen, 1.5 GPM | Standard flow kitchen aerator (code compliant) | 2.2 GPM | unit |  | TRM Version 7.0 | 2022-11-30 | 12 | 0 | 0 | 0 | 4516 | 0 | 1.14 | 0 | 10 | Direct Install | 0.1 | 1 | 1
RES-FA-WH-463-05 | Current |  | Residential | Faucet Aerator |  | Retrofit | water heating | Faucet Aerator | Kitchen, 1.5 GPM | Standard flow kitchen aerator (code compliant) | 2.2 GPM | unit |  | TRM Version 7.0 | 2022-11-30 | 12 | 0 | 0 | 0 | 4516 | 0 | 1.14 | 0 | 10 | Direct Install | 0 | 1 | 1
COM-ERV-SH-380-11 | Current |  | Commercial | Energy Recovery Ventilation | High Use Group | New Construction/Natural Replacement | space heating | High Efficient 65% Energy Recovery Ventilation High Use Group (Multi-Residential, Health Care, Nursing Homes) | Minimum 65% Sensible Heat Recovery Effectiveness and 63% Total Energy Recovery Effectiveness at 32°F | Minimum 55% Energy Recovery Effectiveness as per Ontario Building Code 2017 |  |  | CFM | TRM Version 5.0 | 2020-11-12 | 0 | 0.85 | 0 | 0 | 0 | 0 | 0 | 1 | 14 | Direct Install | 0.05 | 1 | 1
COM-ERV-SH-381-11 | Current |  | Commercial | Energy Recovery Ventilation | Medium Use Group | New Construction/Natural Replacement | space heating | High Efficient 65% Energy Recovery Ventilation Medium Use Group (Hotel, Restaurant, Retail) | Minimum 65% Sensible Heat Recovery Effectiveness and 63% Total Energy Recovery Effectiveness at 32°F | Minimum 55% Energy Recovery Effectiveness as per Ontario Building Code 2017 |  |  | CFM | TRM Version 5.0 | 2020-11-12 | 0 | 0.47 | 0 | 0 | 0 | 0 | 0 | 1 | 14 | Direct Install | 0.05 | 1 | 1
COM-ERV-SH-382-11 | Current |  | Commercial | Energy Recovery Ventilation | Low Use Group | New Construction/Natural Replacement | space heating | High Efficient 65% Energy Recovery Ventilation Low Use Group (Office, Warehouse, School) | Minimum 65% Sensible Heat Recovery Effectiveness and 63% Total Energy Recovery Effectiveness at 32°F | Minimum 55% Energy Recovery Effectiveness as per Ontario Building Code 2017 |  |  | CFM | TRM Version 5.0 | 2020-11-12 | 0 | 0.3 | 0 | 0 | 0 | 0 | 0 | 1 | 14 | Direct Install | 0.05 | 1 | 1
COM-ERV-SH-383-11 | Current |  | Commercial | Energy Recovery Ventilation | Multi-Residential, Health Care, Nursing Homes | New Construction/Natural Replacement | space heating | High Efficient 65% Energy Recovery Ventilation High Use Group (Multi-Residential, Health Care, Nursing Homes) | Minimum 65% Sensible Heat Recovery Effectiveness and 63% Total Energy Recovery Effectiveness at 32°F | Minimum 55% Energy Recovery Effectiveness as per Ontario Building Code 2017 |  |  | CFM | TRM Version 5.0 | 2020-11-12 | 0 | 0.85 | 0 | 0 | 0 | 0 | 0 | 1 | 14 | Direct Install | 0.05 | 1 | 1
COM-ERV-SH-384-11 | Current |  | Commercial | Energy Recovery Ventilation | Hotel | New Construction/Natural Replacement | space heating | High Efficient 65% Energy Recovery Ventilation Medium Use Group (Hotel, Restaurant, Retail) | Minimum 65% Sensible Heat Recovery Effectiveness and 63% Total Energy Recovery Effectiveness at 32°F | Minimum 55% Energy Recovery Effectiveness as per Ontario Building Code 2017 |  |  | CFM | TRM Version 5.0 | 2020-11-12 | 0 | 0.61 | 0 | 0 | 0 | 0 | 0 | 1 | 14 | Direct Install | 0.05 | 1 | 1
COM-ERV-SH-385-11 | Current |  | Commercial | Energy Recovery Ventilation | Restaurant | New Construction/Natural Replacement | space heating | High Efficient 65% Energy Recovery Ventilation Medium Use Group (Hotel, Restaurant, Retail) | Minimum 65% Sensible Heat Recovery Effectiveness and 63% Total Energy Recovery Effectiveness at 32°F | Minimum 55% Energy Recovery Effectiveness as per Ontario Building Code 2017 |  |  | CFM | TRM Version 5.0 | 2020-11-12 | 0 | 0.44 | 0 | 0 | 0 | 0 | 0 | 1 | 14 | Direct Install | 0.05 | 1 | 1
COM-ERV-SH-386-11 | Current |  | Commercial | Energy Recovery Ventilation | Retail | New Construction/Natural Replacement | space heating | High Efficient 65% Energy Recovery Ventilation Medium Use Group (Hotel, Restaurant, Retail) | Minimum 65% Sensible Heat Recovery Effectiveness and 63% Total Energy Recovery Effectiveness at 32°F | Minimum 55% Energy Recovery Effectiveness as per Ontario Building Code 2017 |  |  | CFM | TRM Version 5.0 | 2020-11-12 | 0 | 0.37 | 0 | 0 | 0 | 0 | 0 | 1 | 14 | Direct Install | 0.05 | 1 | 1
COM-ERV-SH-387-11 | Current |  | Commercial | Energy Recovery Ventilation | Office | New Construction/Natural Replacement | space heating | High Efficient 65% Energy Recovery Ventilation Low Use Group (Office, Warehouse, School) | Minimum 65% Sensible Heat Recovery Effectiveness and 63% Total Energy Recovery Effectiveness at 32°F | Minimum 55% Energy Recovery Effectiveness as per Ontario Building Code 2017 |  |  | CFM | TRM Version 5.0 | 2020-11-12 | 0 | 0.32 | 0 | 0 | 0 | 0 | 0 | 1 | 14 | Direct Install | 0.05 | 1 | 1
COM-ERV-SH-388-11 | Current |  | Commercial | Energy Recovery Ventilation | Warehouse | New Construction/Natural Replacement | space heating | High Efficient 65% Energy Recovery Ventilation Low Use Group (Office, Warehouse, School) | Minimum 65% Sensible Heat Recovery Effectiveness and 63% Total Energy Recovery Effectiveness at 32°F | Minimum 55% Energy Recovery Effectiveness as per Ontario Building Code 2017 |  |  | CFM | TRM Version 5.0 | 2020-11-12 | 0 | 0.31 | 0 | 0 | 0 | 0 | 0 | 1 | 14 | Direct Install | 0.05 | 1 | 1
COM-ERV-SH-389-11 | Current |  | Commercial | Energy Recovery Ventilation | School | New Construction/Natural Replacement | space heating | High Efficient 65% Energy Recovery Ventilation Low Use Group (Office, Warehouse, School) | Minimum 65% Sensible Heat Recovery Effectiveness and 63% Total Energy Recovery Effectiveness at 32°F | Minimum 55% Energy Recovery Effectiveness as per Ontario Building Code 2017 |  |  | CFM | TRM Version 5.0 | 2020-11-12 | 0 | 0.27 | 0 | 0 | 0 | 0 | 0 | 1 | 14 | Direct Install | 0.05 | 1 | 1
COM-ERV-SH-380-15 | Current |  | Commercial | Energy Recovery Ventilation | High Use Group | New Construction/Natural Replacement | space heating | High Efficient 75% Energy Recovery Ventilation High Use Group (Multi-Residential, Health Care, Nursing Homes) | Minimum 75% Sensible Heat Recovery Effectiveness and 73% Total Energy Recovery Effectiveness at 32°F | Minimum 55% Energy Recovery Effectiveness as per Ontario Building Code 2017 |  |  | CFM | TRM Version 5.0 | 2020-11-12 | 0 | 1.7 | 0 | 0 | 0 | 0 | 0 | 2 | 14 | Direct Install | 0.05 | 1 | 1
COM-ERV-SH-381-15 | Current |  | Commercial | Energy Recovery Ventilation | Medium Use Group | New Construction/Natural Replacement | space heating | High Efficient 75% Energy Recovery Ventilation Medium Use Group (Hotel, Restaurant, and Retail) | Minimum 75% Sensible Heat Recovery Effectiveness and 73% Total Energy Recovery Effectiveness at 32°F | Minimum 55% Energy Recovery Effectiveness as per Ontario Building Code 2017 |  |  | CFM | TRM Version 5.0 | 2020-11-12 | 0 | 0.95 | 0 | 0 | 0 | 0 | 0 | 2 | 14 | Direct Install | 0.05 | 1 | 1
COM-ERV-SH-382-15 | Current |  | Commercial | Energy Recovery Ventilation | Low Use Group | New Construction/Natural Replacement | space heating | High Efficient 75% Energy Recovery Ventilation Low Use Group (Office, Warehouse, School) | Minimum 75% Sensible Heat Recovery Effectiveness and 73% Total Energy Recovery Effectiveness at 32°F | Minimum 55% Energy Recovery Effectiveness as per Ontario Building Code 2017 |  |  | CFM | TRM Version 5.0 | 2020-11-12 | 0 | 0.61 | 0 | 0 | 0 | 0 | 0 | 2 | 14 | Direct Install | 0.05 | 1 | 1
COM-ERV-SH-383-15 | Current |  | Commercial | Energy Recovery Ventilation | Multi-Residential, Health Care, Nursing Homes | New Construction/Natural Replacement | space heating | High Efficient 75% Energy Recovery Ventilation High Use Group (Multi-Residential, Health Care, Nursing Homes) | Minimum 75% Sensible Heat Recovery Effectiveness and 73% Total Energy Recovery Effectiveness at 32°F | Minimum 55% Energy Recovery Effectiveness as per Ontario Building Code 2017 |  |  | CFM | TRM Version 5.0 | 2020-11-12 | 0 | 1.7 | 0 | 0 | 0 | 0 | 0 | 2 | 14 | Direct Install | 0.05 | 1 | 1
COM-ERV-SH-384-15 | Current |  | Commercial | Energy Recovery Ventilation | Hotel | New Construction/Natural Replacement | space heating | High Efficient 75% Energy Recovery Ventilation Medium Use Group (Hotel, Restaurant, and Retail) | Minimum 75% Sensible Heat Recovery Effectiveness and 73% Total Energy Recovery Effectiveness at 32°F | Minimum 55% Energy Recovery Effectiveness as per Ontario Building Code 2017 |  |  | CFM | TRM Version 5.0 | 2020-11-12 | 0 | 1.22 | 0 | 0 | 0 | 0 | 0 | 2 | 14 | Direct Install | 0.05 | 1 | 1
COM-ERV-SH-385-15 | Current |  | Commercial | Energy Recovery Ventilation | Restaurant | New Construction/Natural Replacement | space heating | High Efficient 75% Energy Recovery Ventilation Medium Use Group (Hotel, Restaurant, and Retail) | Minimum 75% Sensible Heat Recovery Effectiveness and 73% Total Energy Recovery Effectiveness at 32°F | Minimum 55% Energy Recovery Effectiveness as per Ontario Building Code 2017 |  |  | CFM | TRM Version 5.0 | 2020-11-12 | 0 | 0.88 | 0 | 0 | 0 | 0 | 0 | 2 | 14 | Direct Install | 0.05 | 1 | 1
COM-ERV-SH-386-15 | Current |  | Commercial | Energy Recovery Ventilation | Retail | New Construction/Natural Replacement | space heating | High Efficient 75% Energy Recovery Ventilation Medium Use Group (Hotel, Restaurant, and Retail) | Minimum 75% Sensible Heat Recovery Effectiveness and 73% Total Energy Recovery Effectiveness at 32°F | Minimum 55% Energy Recovery Effectiveness as per Ontario Building Code 2017 |  |  | CFM | TRM Version 5.0 | 2020-11-12 | 0 | 0.74 | 0 | 0 | 0 | 0 | 0 | 2 | 14 | Direct Install | 0.05 | 1 | 1
COM-ERV-SH-387-15 | Current |  | Commercial | Energy Recovery Ventilation | Office | New Construction/Natural Replacement | space heating | High Efficient 75% Energy Recovery Ventilation Low Use Group (Office, Warehouse, School) | Minimum 75% Sensible Heat Recovery Effectiveness and 73% Total Energy Recovery Effectiveness at 32°F | Minimum 55% Energy Recovery Effectiveness as per Ontario Building Code 2017 |  |  | CFM | TRM Version 5.0 | 2020-11-12 | 0 | 0.65 | 0 | 0 | 0 | 0 | 0 | 2 | 14 | Direct Install | 0.05 | 1 | 1
COM-ERV-SH-388-15 | Current |  | Commercial | Energy Recovery Ventilation | Warehouse | New Construction/Natural Replacement | space heating | High Efficient 75% Energy Recovery Ventilation Low Use Group (Office, Warehouse, School) | Minimum 75% Sensible Heat Recovery Effectiveness and 73% Total Energy Recovery Effectiveness at 32°F | Minimum 55% Energy Recovery Effectiveness as per Ontario Building Code 2017 |  |  | CFM | TRM Version 5.0 | 2020-11-12 | 0 | 0.62 | 0 | 0 | 0 | 0 | 0 | 2 | 14 | Direct Install | 0.05 | 1 | 1
COM-ERV-SH-389-15 | Current |  | Commercial | Energy Recovery Ventilation | School | New Construction/Natural Replacement | space heating | High Efficient 75% Energy Recovery Ventilation Low Use Group (Office, Warehouse, School) | Minimum 75% Sensible Heat Recovery Effectiveness and 73% Total Energy Recovery Effectiveness at 32°F | Minimum 55% Energy Recovery Effectiveness as per Ontario Building Code 2017 |  |  | CFM | TRM Version 5.0 | 2020-11-12 | 0 | 0.55 | 0 | 0 | 0 | 0 | 0 | 2 | 14 | Direct Install | 0.05 | 1 | 1
COM-ERV-SH-390-07 | Current |  | Commercial | Energy Recovery Ventilation | High Use Group | New Construction/Natural Replacement | space heating | High Efficient 85% Energy Recovery Ventilation High Use Group (Multi-Residential, Health Care, Nursing Homes) | Minimum 85% Sensible Heat Recovery Effectiveness and 83% Total Energy Recovery Effectiveness at 32°F | Minimum 55% Energy Recovery Effectiveness as per Ontario Building Code 2017 |  |  | CFM | TRM Version 5.0 | 2020-11-12 | 0 | 2.56 | 0 | 0 | 0 | 0 | 0 | 3 | 14 | Direct Install | 0.05 | 1 | 1
COM-ERV-SH-391-07 | Current |  | Commercial | Energy Recovery Ventilation | Medium Use Group | New Construction/Natural Replacement | space heating | High Efficient 85% Energy Recovery Ventilation Medium Use Group (Hotel, Restaurant, Retail) | Minimum 85% Sensible Heat Recovery Effectiveness and 83% Total Energy Recovery Effectiveness at 32°F | Minimum 55% Energy Recovery Effectiveness as per Ontario Building Code 2017 |  |  | CFM | TRM Version 5.0 | 2020-11-12 | 0 | 1.42 | 0 | 0 | 0 | 0 | 0 | 3 | 14 | Direct Install | 0.05 | 1 | 1
COM-ERV-SH-392-07 | Current |  | Commercial | Energy Recovery Ventilation | Low Use Group | New Construction/Natural Replacement | space heating | High Efficient 85% Energy Recovery Ventilation Low Use Group (Office, Warehouse, School) | Minimum 85% Sensible Heat Recovery Effectiveness and 83% Total Energy Recovery Effectiveness at 32°F | Minimum 55% Energy Recovery Effectiveness as per Ontario Building Code 2017 |  |  | CFM | TRM Version 5.0 | 2020-11-12 | 0 | 0.91 | 0 | 0 | 0 | 0 | 0 | 3 | 14 | Direct Install | 0.05 | 1 | 1
COM-ERV-SH-393-07 | Current |  | Commercial | Energy Recovery Ventilation | Multi-Residential, Health Care, Nursing Homes | New Construction/Natural Replacement | space heating | High Efficient 85% Energy Recovery Ventilation High Use Group (Multi-Residential, Health Care, Nursing Homes) | Minimum 85% Sensible Heat Recovery Effectiveness and 83% Total Energy Recovery Effectiveness at 32°F | Minimum 55% Energy Recovery Effectiveness as per Ontario Building Code 2017 |  |  | CFM | TRM Version 5.0 | 2020-11-12 | 0 | 2.56 | 0 | 0 | 0 | 0 | 0 | 3 | 14 | Direct Install | 0.05 | 1 | 1
COM-ERV-SH-394-07 | Current |  | Commercial | Energy Recovery Ventilation | Hotel | New Construction/Natural Replacement | space heating | High Efficient 85% Energy Recovery Ventilation Medium Use Group (Hotel, Restaurant, Retail) | Minimum 85% Sensible Heat Recovery Effectiveness and 83% Total Energy Recovery Effectiveness at 32°F | Minimum 55% Energy Recovery Effectiveness as per Ontario Building Code 2017 |  |  | CFM | TRM Version 5.0 | 2020-11-12 | 0 | 1.83 | 0 | 0 | 0 | 0 | 0 | 3 | 14 | Direct Install | 0.05 | 1 | 1
COM-ERV-SH-395-07 | Current |  | Commercial | Energy Recovery Ventilation | Restaurant | New Construction/Natural Replacement | space heating | High Efficient 85% Energy Recovery Ventilation Medium Use Group (Hotel, Restaurant, Retail) | Minimum 85% Sensible Heat Recovery Effectiveness and 83% Total Energy Recovery Effectiveness at 32°F | Minimum 55% Energy Recovery Effectiveness as per Ontario Building Code 2017 |  |  | CFM | TRM Version 5.0 | 2020-11-12 | 0 | 1.32 | 0 | 0 | 0 | 0 | 0 | 3 | 14 | Direct Install | 0.05 | 1 | 1
COM-ERV-SH-396-07 | Current |  | Commercial | Energy Recovery Ventilation | Retail | New Construction/Natural Replacement | space heating | High Efficient 85% Energy Recovery Ventilation Medium Use Group (Hotel, Restaurant, Retail) | Minimum 85% Sensible Heat Recovery Effectiveness and 83% Total Energy Recovery Effectiveness at 32°F | Minimum 55% Energy Recovery Effectiveness as per Ontario Building Code 2017 |  |  | CFM | TRM Version 5.0 | 2020-11-12 | 0 | 1.11 | 0 | 0 | 0 | 0 | 0 | 3 | 14 | Direct Install | 0.05 | 1 | 1
COM-ERV-SH-397-07 | Current |  | Commercial | Energy Recovery Ventilation | Office | New Construction/Natural Replacement | space heating | High Efficient 85% Energy Recovery Ventilation Low Use Group (Office, Warehouse, School) | Minimum 85% Sensible Heat Recovery Effectiveness and 83% Total Energy Recovery Effectiveness at 32°F | Minimum 55% Energy Recovery Effectiveness as per Ontario Building Code 2017 |  |  | CFM | TRM Version 5.0 | 2020-11-12 | 0 | 0.97 | 0 | 0 | 0 | 0 | 0 | 3 | 14 | Direct Install | 0.05 | 1 | 1
COM-ERV-SH-398-07 | Current |  | Commercial | Energy Recovery Ventilation | Warehouse | New Construction/Natural Replacement | space heating | High Efficient 85% Energy Recovery Ventilation Low Use Group (Office, Warehouse, School) | Minimum 85% Sensible Heat Recovery Effectiveness and 83% Total Energy Recovery Effectiveness at 32°F | Minimum 55% Energy Recovery Effectiveness as per Ontario Building Code 2017 |  |  | CFM | TRM Version 5.0 | 2020-11-12 | 0 | 0.93 | 0 | 0 | 0 | 0 | 0 | 3 | 14 | Direct Install | 0.05 | 1 | 1
COM-ERV-SH-399-07 | Current |  | Commercial | Energy Recovery Ventilation | School | New Construction/Natural Replacement | space heating | High Efficient 85% Energy Recovery Ventilation Low Use Group (Office, Warehouse, School) | Minimum 85% Sensible Heat Recovery Effectiveness and 83% Total Energy Recovery Effectiveness at 32°F | Minimum 55% Energy Recovery Effectiveness as per Ontario Building Code 2017 |  |  | CFM | TRM Version 5.0 | 2020-11-12 | 0 | 0.82 | 0 | 0 | 0 | 0 | 0 | 3 | 14 | Direct Install | 0.05 | 1 | 1
COM-AC-SH-481-02 | Current |  | Commercial | Air Curtain |  | New Construction/Retrofit | space heating | Air Curtains | Pedestrian Doors 2 x (3' x 7') | Exterior doorway without vestibule or air curtain |  | unit |  | TRM Version 5.0 | 2020-11-12 | 1690 | 0 | 212 | 0 | 0 | 0 | 3150 | 0 | 15 | Direct Install | 0.05 | 1 | 1
COM-AC-SH-487-02 | Current |  | Commercial | Air Curtain |  | New Construction/Retrofit | space heating | Air Curtains | Pedestrian Doors 2 x (3' x 7') | Exterior doorway with vestibule and no air curtain |  | unit |  | TRM Version 5.0 | 2020-11-12 | 1082 | 0 | 124 | 0 | 0 | 0 | 3150 | 0 | 15 | Direct Install | 0.05 | 1 | 1
COM-AC-SH-483-02 | Current |  | Commercial | Air Curtain |  | New Construction/Retrofit | space heating | Air Curtains | Pedestrian Doors 2 x (6' x 8') | Exterior doorway without vestibule or air curtain |  | unit |  | TRM Version 5.0 | 2020-11-12 | 3774 | 0 | 431 | 0 | 0 | 0 | 3350 | 0 | 15 | Direct Install | 0.05 | 1 | 1
COM-AC-SH-489-02 | Current |  | Commercial | Air Curtain |  | New Construction/Retrofit | space heating | Air Curtains | Pedestrian Doors 2 x (6' x 8') | Exterior doorway with vestibule and no air curtain |  | unit |  | TRM Version 5.0 | 2020-11-12 | 2416 | 0 | 232 | 0 | 0 | 0 | 3350 | 0 | 15 | Direct Install | 0.05 | 1 | 1
COM-AC-SH-482-02 | Current |  | Commercial | Air Curtain |  | New Construction/Retrofit | space heating | Air Curtains | Pedestrian Doors 2 x (6' x 7') | Exterior doorway without vestibule or air curtain |  | unit |  | TRM Version 5.0 | 2020-11-12 | 3380 | 0 | 367 | 0 | 0 | 0 | 3350 | 0 | 15 | Direct Install | 0.05 | 1 | 1
COM-AC-SH-488-02 | Current |  | Commercial | Air Curtain |  | New Construction/Retrofit | space heating | Air Curtains | Pedestrian Doors 2 x (6' x 7') | Exterior doorway with vestibule and no air curtain |  | unit |  | TRM Version 5.0 | 2020-11-12 | 2164 | 0 | 192 | 0 | 0 | 0 | 3350 | 0 | 15 | Direct Install | 0.05 | 1 | 1
COM-AC-SH-478-02 | Current |  | Commercial | Air Curtain |  | New Construction/Retrofit | space heating | Air Curtains | Pedestrian Doors 3' x 7' | Exterior doorway without vestibule or air curtain |  | unit |  | TRM Version 5.0 | 2020-11-12 | 845 | 0 | 106 | 0 | 0 | 0 | 1645 | 0 | 15 | Direct Install | 0.05 | 1 | 1
COM-AC-SH-484-02 | Current |  | Commercial | Air Curtain |  | New Construction/Retrofit | space heating | Air Curtains | Pedestrian Doors 3' x 7' | Exterior doorway with vestibule and no air curtain |  | unit |  | TRM Version 5.0 | 2020-11-12 | 541 | 0 | 62 | 0 | 0 | 0 | 1645 | 0 | 15 | Direct Install | 0.05 | 1 | 1
COM-AC-SH-479-02 | Current |  | Commercial | Air Curtain |  | New Construction/Retrofit | space heating | Air Curtains | Pedestrian Doors 6' x 7' | Exterior doorway without vestibule or air curtain |  | unit |  | TRM Version 5.0 | 2020-11-12 | 1690 | 0 | 184 | 0 | 0 | 0 | 1745 | 0 | 15 | Direct Install | 0.05 | 1 | 1
COM-AC-SH-485-02 | Current |  | Commercial | Air Curtain |  | New Construction/Retrofit | space heating | Air Curtains | Pedestrian Doors 6' x 7' | Exterior doorway with vestibule and no air curtain |  | unit |  | TRM Version 5.0 | 2020-11-12 | 1082 | 0 | 96 | 0 | 0 | 0 | 1745 | 0 | 15 | Direct Install | 0.05 | 1 | 1
COM-AC-SH-480-02 | Current |  | Commercial | Air Curtain |  | New Construction/Retrofit | space heating | Air Curtains | Pedestrian Doors 6' x 8' | Exterior doorway without vestibule or air curtain |  | unit |  | TRM Version 5.0 | 2020-11-12 | 1887 | 0 | 215 | 0 | 0 | 0 | 1745 | 0 | 15 | Direct Install | 0.05 | 1 | 1
COM-AC-SH-486-02 | Current |  | Commercial | Air Curtain |  | New Construction/Retrofit | space heating | Air Curtains | Pedestrian Doors 6' x 8' | Exterior doorway with vestibule and no air curtain |  | unit |  | TRM Version 5.0 | 2020-11-12 | 1208 | 0 | 116 | 0 | 0 | 0 | 1745 | 0 | 15 | Direct Install | 0.05 | 1 | 1
COM-DCV-SH-527-03 | Current |  | Commercial | Demand Control Ventilation | Office | New Construction/Natural Replacement | space heating | Demand Control Ventilation with CO2 Sensor (Office) | Scheduled Ventilation (Occupied Periods) | New single-zone, constant volume ventilation system | Provides min outdoor air requirements as specificed in Table 6.2.2.1 of ASHRAE Standard 62.1-2013 [1] |  | sq ft | TRM Version 5.0 | 2020-11-12 | 0 | 0.112 | 0 | 0 | 0 | 0 | 750 | 0 | 15 | Direct Install | 0.2 | 1 | 1
COM-DCV-SH-528-03 | Current |  | Commercial | Demand Control Ventilation | Office | Retrofit | space heating | Demand Control Ventilation with CO2 Sensor (Office) | Scheduled Ventilation (Occupied Periods) | New single-zone, constant volume ventilation system | Provides min outdoor air requirements as specificed in Table 6.2.2.1 of ASHRAE Standard 62.1-2013 [1] |  | sq ft | TRM Version 5.0 | 2020-11-12 | 0 | 0.112 | 0 | 0 | 0 | 0 | 1050 | 0 | 15 | Direct Install | 0.05 | 1 | 1
COM-DCV-SH-529-03 | Current |  | Commercial | Demand Control Ventilation | Retail | New Construction/Natural Replacement | space heating | Demand Control Ventilation with CO2 Sensor (Retail) | Scheduled Ventilation (Occupied Periods) | New single-zone, constant volume ventilation system | Provides min outdoor air requirements as specificed in Table 6.2.2.1 of ASHRAE Standard 62.1-2013 [1] |  | sq ft | TRM Version 5.0 | 2020-11-12 | 0 | 0.392 | 0 | 0 | 0 | 0 | 750 | 0 | 15 | Direct Install | 0.2 | 1 | 1
COM-DCV-SH-530-03 | Current |  | Commercial | Demand Control Ventilation | Retail | Retrofit | space heating | Demand Control Ventilation with CO2 Sensor (Retail) | Scheduled Ventilation (Occupied Periods) | New single-zone, constant volume ventilation system | Provides min outdoor air requirements as specificed in Table 6.2.2.1 of ASHRAE Standard 62.1-2013 [1] |  | sq ft | TRM Version 5.0 | 2020-11-12 | 0 | 0.392 | 0 | 0 | 0 | 0 | 1050 | 0 | 15 | Direct Install | 0.05 | 1 | 1
COM-DCV-SH-531-03 | Current |  | Commercial | Demand Control Ventilation | Cinemas and Performing Arts | Retrofit | space heating | Demand Control Ventilation with CO2 Sensor (Cinemas and Performing Arts) | Scheduled Ventilation (Occupied Periods) | Existing single-zone, constant volume ventilation system | Provides min outdoor air requirements as specificed in Table 6.2.2.1 of ASHRAE Standard 62.1-2013 [1] |  | sq ft | TRM Version 5.0 | 2020-11-12 | 0 | 1.69 | 0 | 0 | 0 | 0 | 1050 | 0 | 15 | Direct Install | 0.05 | 1 | 1
COM-DCV-SH-532-03 | Current |  | Commercial | Demand Control Ventilation | Cinemas and Performing Arts | New Construction/Natural Replacement | space heating | Demand Control Ventilation with CO2 Sensor (Cinemas and Performing Arts) | Scheduled Ventilation (Occupied Periods) | Existing single-zone, constant volume ventilation system | Provides min outdoor air requirements as specificed in Table 6.2.2.1 of ASHRAE Standard 62.1-2013 [1] |  | sq ft | TRM Version 5.0 | 2020-11-12 | 0 | 1.69 | 0 | 0 | 0 | 0 | 750 | 0 | 15 | Direct Install | 0.2 | 1 | 1
COM-DCV-SH-533-03 | Current |  | Commercial | Demand Control Ventilation | Community Center Meeting Space | Retrofit | space heating | Demand Control Ventilation with CO2 Sensor (Community Center Meeting Space) | Scheduled Ventilation (Occupied Periods) | Existing single-zone, constant volume ventilation system | Provides min outdoor air requirements as specificed in Table 6.2.2.1 of ASHRAE Standard 62.1-2013 [1] |  | sq ft | TRM Version 5.0 | 2020-11-12 | 0 | 0.441 | 0 | 0 | 0 | 0 | 1050 | 0 | 15 | Direct Install | 0.05 | 1 | 1
COM-DCV-SH-534-03 | Current |  | Commercial | Demand Control Ventilation | Community Center Meeting Space | New Construction/Natural Replacement | space heating | Demand Control Ventilation with CO2 Sensor (Community Center Meeting Space) | Scheduled Ventilation (Occupied Periods) | Existing single-zone, constant volume ventilation system | Provides min outdoor air requirements as specificed in Table 6.2.2.1 of ASHRAE Standard 62.1-2013 [1] |  | sq ft | TRM Version 5.0 | 2020-11-12 | 0 | 0.441 | 0 | 0 | 0 | 0 | 750 | 0 | 15 | Direct Install | 0.2 | 1 | 1
COM-DCV-SH-535-03 | Current |  | Commercial | Demand Control Ventilation | Exercise Center/Sports Arena | Retrofit | space heating | Demand Control Ventilation with CO2 Sensor (Exercise Center/Sports Arena) | Scheduled Ventilation (Occupied Periods) | Existing single-zone, constant volume ventilation system | Provides min outdoor air requirements as specificed in Table 6.2.2.1 of ASHRAE Standard 62.1-2013 [1] |  | sq ft | TRM Version 5.0 | 2020-11-12 | 0 | 0.435 | 0 | 0 | 0 | 0 | 1050 | 0 | 15 | Direct Install | 0.05 | 1 | 1
COM-DCV-SH-536-03 | Current |  | Commercial | Demand Control Ventilation | Exercise Center/Sports Arena | New Construction/Natural Replacement | space heating | Demand Control Ventilation with CO2 Sensor (Exercise Center/Sports Arena) | Scheduled Ventilation (Occupied Periods) | Existing single-zone, constant volume ventilation system | Provides min outdoor air requirements as specificed in Table 6.2.2.1 of ASHRAE Standard 62.1-2013 [1] |  | sq ft | TRM Version 5.0 | 2020-11-12 | 0 | 0.435 | 0 | 0 | 0 | 0 | 750 | 0 | 15 | Direct Install | 0.2 | 1 | 1
COM-CS-WH-502-01 | Replaced | Replaced in TRM Version 8.0 | Commercial | Condensing Storage Water Heater | Low Utilization | New Construction/Natural Replacement | water heating | Condensing Storage Water Heater - Low Utilization | > 75 kBtu/hr and <=250 kBtu/hr. inputEstimated overall efficiency of units shipped = 94.5% | Non-condensing storage water heater | Non-condensing storage water heaterGreater than 75 kBtu/hr. inputEstimated overall efficiency of units shipped = 80.1% |  | kBtu/hr input capacity | TRM Version 5.0 | 2020-11-12 | 0 | 1.36 | 0 | 0 | 0 | 0 | 2591 | 0 | 15 | Downstream | 0.05 | 1 | 1
COM-CS-WH-503-01 | Replaced | Replaced in TRM Version 8.0 | Commercial | Condensing Storage Water Heater | Medium Utilization | New Construction/Natural Replacement | water heating | Condensing Storage Water Heater - Medium Utilization | > 75 kBtu/hr and <=250 kBtu/hr. inputEstimated overall efficiency of units shipped = 94.5% | Non-condensing storage water heater | Greater than 75 kBtu/hr. inputEstimated overall efficiency of units shipped = 80.1% |  | kBtu/hr input capacity | TRM Version 5.0 | 2020-11-12 | 0 | 2.22 | 0 | 0 | 0 | 0 | 2591 | 0 | 15 | Downstream | 0.05 | 1 | 1
COM-DCV-SH-537-03 | Current |  | Commercial | Demand Control Ventilation | Hotel Conference Rooms | Retrofit | space heating | Demand Control Ventilation with CO2 Sensor (Hotel Conference Rooms) | Scheduled Ventilation (Occupied Periods) | Existing single-zone, constant volume ventilation system | Provides min outdoor air requirements as specificed in Table 6.2.2.1 of ASHRAE Standard 62.1-2013 [1] |  | sq ft | TRM Version 5.0 | 2020-11-12 | 0 | 1.043 | 0 | 0 | 0 | 0 | 1050 | 0 | 15 | Direct Install | 0.05 | 1 | 1
COM-DCV-SH-538-03 | Current |  | Commercial | Demand Control Ventilation | Hotel Conference Rooms | New Construction/Natural Replacement | space heating | Demand Control Ventilation with CO2 Sensor (Hotel Conference Rooms) | Scheduled Ventilation (Occupied Periods) | Existing single-zone, constant volume ventilation system | Provides min outdoor air requirements as specificed in Table 6.2.2.1 of ASHRAE Standard 62.1-2013 [1] |  | sq ft | TRM Version 5.0 | 2020-11-12 | 0 | 1.043 | 0 | 0 | 0 | 0 | 750 | 0 | 15 | Direct Install | 0.2 | 1 | 1
COM-DCV-SH-539-03 | Current |  | Commercial | Demand Control Ventilation | Post-Secondary School Classroom | Retrofit | space heating | Demand Control Ventilation with CO2 Sensor (Post-Secondary School Classroom) | Scheduled Ventilation (Occupied Periods) | Existing single-zone, constant volume ventilation system | Provides min outdoor air requirements as specificed in Table 6.2.2.1 of ASHRAE Standard 62.1-2013 [1] |  | sq ft | TRM Version 5.0 | 2020-11-12 | 0 | 0.601 | 0 | 0 | 0 | 0 | 1050 | 0 | 15 | Direct Install | 0.05 | 1 | 1
COM-DCV-SH-540-03 | Current |  | Commercial | Demand Control Ventilation | Post-Secondary School Classroom | New Construction/Natural Replacement | space heating | Demand Control Ventilation with CO2 Sensor (Post-Secondary School Classroom) | Scheduled Ventilation (Occupied Periods) | Existing single-zone, constant volume ventilation system | Provides min outdoor air requirements as specificed in Table 6.2.2.1 of ASHRAE Standard 62.1-2013 [1] |  | sq ft | TRM Version 5.0 | 2020-11-12 | 0 | 0.601 | 0 | 0 | 0 | 0 | 750 | 0 | 15 | Direct Install | 0.2 | 1 | 1
COM-DCV-SH-541-03 | Current |  | Commercial | Demand Control Ventilation | Primary/Secondary School Gymnasium | Retrofit | space heating | Demand Control Ventilation with CO2 Sensor (Primary/Secondary School Gymnasium) | Scheduled Ventilation (Occupied Periods) | Existing single-zone, constant volume ventilation system | Provides min outdoor air requirements as specificed in Table 6.2.2.1 of ASHRAE Standard 62.1-2013 [1] |  | sq ft | TRM Version 5.0 | 2020-11-12 | 0 | 1.484 | 0 | 0 | 0 | 0 | 1050 | 0 | 15 | Direct Install | 0.05 | 1 | 1
COM-DCV-SH-542-03 | Current |  | Commercial | Demand Control Ventilation | Primary/Secondary School Gymnasium | New Construction/Natural Replacement | space heating | Demand Control Ventilation with CO2 Sensor (Primary/Secondary School Gymnasium) | Scheduled Ventilation (Occupied Periods) | Existing single-zone, constant volume ventilation system | Provides min outdoor air requirements as specificed in Table 6.2.2.1 of ASHRAE Standard 62.1-2013 [1] |  | sq ft | TRM Version 5.0 | 2020-11-12 | 0 | 1.484 | 0 | 0 | 0 | 0 | 750 | 0 | 15 | Direct Install | 0.2 | 1 | 1
COM-DCV-SH-543-03 | Current |  | Commercial | Demand Control Ventilation | Senior/Nursing/Long-Term Care Facility (Common Areas) | Retrofit | space heating | Demand Control Ventilation with CO2 Sensor (Senior/Nursing/Long-Term Care Facility (Common Areas)) | Scheduled Ventilation (Occupied Periods) | Existing single-zone, constant volume ventilation system | Provides min outdoor air requirements as specificed in Table 6.2.2.1 of ASHRAE Standard 62.1-2013 [1] |  | sq ft | TRM Version 5.0 | 2020-11-12 | 0 | 0.636 | 0 | 0 | 0 | 0 | 1050 | 0 | 15 | Direct Install | 0.05 | 1 | 1
COM-DCV-SH-544-03 | Current |  | Commercial | Demand Control Ventilation | Senior/Nursing/Long-Term Care Facility (Common Areas) | New Construction/Natural Replacement | space heating | Demand Control Ventilation with CO2 Sensor (Senior/Nursing/Long-Term Care Facility (Common Areas)) | Scheduled Ventilation (Occupied Periods) | Existing single-zone, constant volume ventilation system | Provides min outdoor air requirements as specificed in Table 6.2.2.1 of ASHRAE Standard 62.1-2013 [1] |  | sq ft | TRM Version 5.0 | 2020-11-12 | 0 | 0.636 | 0 | 0 | 0 | 0 | 750 | 0 | 15 | Direct Install | 0.2 | 1 | 1
COM-AC-SH-471-02 | Current |  | Commercial | Air Curtain |  | New Construction/Retrofit | space heating | Air Curtains | Shipping and Receiving Doors "Dock-In" 10' x 10' | Exterior doorway without air curtain |  | unit |  | TRM Version 5.0 | 2020-11-12 | 5517 | 0 | -2838 | 0 | 0 | 0 | 6345 | 0 | 15 | Direct Install | 0.05 | 1 | 1
COM-AC-SH-470-02 | Current |  | Commercial | Air Curtain |  | New Construction/Retrofit | space heating | Air Curtains | Shipping and Receiving Doors "Dock-In" 8' x 10' | Exterior doorway without air curtain |  | unit |  | TRM Version 5.0 | 2020-11-12 | 4941 | 0 | -1576 | 0 | 0 | 0 | 5663 | 0 | 15 | Direct Install | 0.05 | 1 | 1
COM-AC-SH-468-02 | Current |  | Commercial | Air Curtain |  | New Construction/Retrofit | space heating | Air Curtains | Shipping and Receiving Doors "Dock-In" 8' x 8' | Exterior doorway without air curtain |  | unit |  | TRM Version 5.0 | 2020-11-12 | 4713 | 0 | -1688 | 0 | 0 | 0 | 5663 | 0 | 15 | Direct Install | 0.05 | 1 | 1
COM-AC-SH-469-02 | Current |  | Commercial | Air Curtain |  | New Construction/Retrofit | space heating | Air Curtains | Shipping and Receiving Doors "Dock-In" 8' x 9' | Exterior doorway without air curtain |  | unit |  | TRM Version 5.0 | 2020-11-12 | 4845 | 0 | -1630 | 0 | 0 | 0 | 5663 | 0 | 15 | Direct Install | 0.05 | 1 | 1
COM-AC-SH-472-02 | Current |  | Commercial | Air Curtain |  | New Construction/Retrofit | space heating | Air Curtains | Shipping and Receiving Doors "Drive-In" 10' x 10' | Exterior doorway without air curtain |  | unit |  | TRM Version 5.0 | 2020-11-12 | 4844 | 0 | 540 | 0 | 0 | 0 | 6345 | 0 | 15 | Direct Install | 0.05 | 1 | 1
COM-AC-SH-473-02 | Current |  | Commercial | Air Curtain |  | New Construction/Retrofit | space heating | Air Curtains | Shipping and Receiving Doors "Drive-In" 12' x 12' | Exterior doorway without air curtain |  | unit |  | TRM Version 5.0 | 2020-11-12 | 5753 | 0 | 843 | 0 | 0 | 0 | 11158 | 0 | 15 | Direct Install | 0.05 | 1 | 1
COM-AC-SH-474-02 | Current |  | Commercial | Air Curtain |  | New Construction/Retrofit | space heating | Air Curtains | Shipping and Receiving Doors "Drive-In" 14' x 14' | Exterior doorway without air curtain |  | unit |  | TRM Version 5.0 | 2020-11-12 | 6504 | 0 | 772 | 0 | 0 | 0 | 14159 | 0 | 15 | Direct Install | 0.05 | 1 | 1
COM-AC-SH-475-02 | Current |  | Commercial | Air Curtain |  | New Construction/Retrofit | space heating | Air Curtains | Shipping and Receiving Doors "Drive-In" 16' x 16' | Exterior doorway without air curtain |  | unit |  | TRM Version 5.0 | 2020-11-12 | 7081 | 0 | 987 | 0 | 0 | 0 | 22226 | 0 | 15 | Direct Install | 0.05 | 1 | 1
COM-AC-SH-476-02 | Current |  | Commercial | Air Curtain |  | New Construction/Retrofit | space heating | Air Curtains | Shipping and Receiving Doors "Drive-In" 18' x 18' | Exterior doorway without air curtain |  | unit |  | TRM Version 5.0 | 2020-11-12 | 7459 | 0 | 488 | 0 | 0 | 0 | 24699 | 0 | 15 | Direct Install | 0.05 | 1 | 1
COM-AC-SH-477-02 | Current |  | Commercial | Air Curtain |  | New Construction/Retrofit | space heating | Air Curtains | Shipping and Receiving Doors "Drive-In" 20' x 20' | Exterior doorway without air curtain |  | unit |  | TRM Version 5.0 | 2020-11-12 | 7605 | 0 | 596 | 0 | 0 | 0 | 45256 | 0 | 15 | Direct Install | 0.05 | 1 | 1
COM-HRV-SH-366-02 | Current |  | Commercial | Heat Recovery Ventialation | High Use | New Construction/Retrofit | space heating | High Efficient 55% Heat Recovery Ventilation High Use Group (Multi-Residential, Health Care, Nursing Homes) | Ventilation with HRV Integrated | Ventilation without HRV |  |  | CFM | TRM Version 5.0 | 2020-11-12 | 0 | 3.84 | 0 | 0 | 0 | 0 | 0 | 5.35 | 14 | Direct Install | 0.05 | 1 | 1
COM-HRV-SH-368-02 | Current |  | Commercial | Heat Recovery Ventialation | Low Use | New Construction/Retrofit | space heating | High Efficient 55% Heat Recovery Ventilation Low Use Group (Office, Warehouse, School) | Ventilation with HRV Integrated | Ventilation without HRV |  |  | CFM | TRM Version 5.0 | 2020-11-12 | 0 | 1.36 | 0 | 0 | 0 | 0 | 0 | 5.35 | 14 | Direct Install | 0.05 | 1 | 1
COM-HRV-SH-370-02 | Current |  | Commercial | Heat Recovery Ventialation | Medium Use | New Construction/Retrofit | space heating | High Efficient 55% Heat Recovery Ventilation Medium Use Group (Hotel, Restaurant, Retail) | Ventilation with HRV Integrated | Ventilation without HRV |  |  | CFM | TRM Version 5.0 | 2020-11-12 | 0 | 2.13 | 0 | 0 | 0 | 0 | 0 | 5.35 | 14 | Direct Install | 0.05 | 1 | 1
COM-HRV-SH-372-02 | Current |  | Commercial | Heat Recovery Ventialation | High Use | New Construction/Retrofit | space heating | High Efficient 65% Heat Recovery Ventilation High Use Group (Multi-Residential, Health Care, Nursing Homes) | Ventilation with HRV Integrated | Ventilation without HRV |  |  | CFM | TRM Version 5.0 | 2020-11-12 | 0 | 4.54 | 0 | 0 | 0 | 0 | 0 | 6.35 | 14 | Direct Install | 0.05 | 1 | 1
COM-HRV-SH-374-02 | Current |  | Commercial | Heat Recovery Ventialation | Low Use | New Construction/Retrofit | space heating | High Efficient 65% Heat Recovery Ventilation Low Use Group (Office, Warehouse, School) | Ventilation with HRV Integrated | Ventilation without HRV |  |  | CFM | TRM Version 5.0 | 2020-11-12 | 0 | 1.61 | 0 | 0 | 0 | 0 | 0 | 6.35 | 14 | Direct Install | 0.05 | 1 | 1
COM-HRV-SH-376-02 | Current |  | Commercial | Heat Recovery Ventialation | Medium Use | New Construction/Retrofit | space heating | High Efficient 65% Heat Recovery Ventilation Medium Use Group (Hotel, Restaurant, Retail) | Ventilation with HRV Integrated | Ventilation without HRV |  |  | CFM | TRM Version 5.0 | 2020-11-12 | 0 | 2.52 | 0 | 0 | 0 | 0 | 0 | 6.35 | 14 | Direct Install | 0.05 | 1 | 1
COM-HRV-SH-378-02 | Current |  | Commercial | Heat Recovery Ventialation | High Use | New Construction/Retrofit | space heating | High Efficient 75% Heat Recovery Ventilation High Use Group (Multi-Residential, Health Care, Nursing Homes) | Ventilation with HRV Integrated | Ventilation without HRV |  |  | CFM | TRM Version 5.0 | 2020-11-12 | 0 | 5.24 | 0 | 0 | 0 | 0 | 0 | 7.35 | 14 | Direct Install | 0.05 | 1 | 1
COM-HRV-SH-380-02 | Current |  | Commercial | Heat Recovery Ventialation | Low Use | New Construction/Retrofit | space heating | High Efficient 75% Heat Recovery Ventilation Low Use Group (Office, Warehouse, School) | Ventilation with HRV Integrated | Ventilation without HRV |  |  | CFM | TRM Version 5.0 | 2020-11-12 | 0 | 1.86 | 0 | 0 | 0 | 0 | 0 | 7.35 | 14 | Direct Install | 0.05 | 1 | 1
COM-HRV-SH-382-02 | Current |  | Commercial | Heat Recovery Ventialation | Medium Use | New Construction/Retrofit | space heating | High Efficient 75% Heat Recovery Ventilation Medium Use Group (Hotel, Restaurant, Retail) | Ventilation with HRV Integrated | Ventilation without HRV |  |  | CFM | TRM Version 5.0 | 2020-11-12 | 0 | 2.91 | 0 | 0 | 0 | 0 | 0 | 7.35 | 14 | Direct Install | 0.05 | 1 | 1
COM-HRV-SH-384-02 | Current |  | Commercial | Heat Recovery Ventialation | High Use | New Construction/Retrofit | space heating | High Efficient 85% Heat Recovery Ventilation High Use Group (Multi-Residential, Health Care, Nursing Homes) | Ventilation with HRV Integrated | Ventilation without HRV |  |  | CFM | TRM Version 5.0 | 2020-11-12 | 0 | 5.93 | 0 | 0 | 0 | 0 | 0 | 8.35 | 14 | Direct Install | 0.05 | 1 | 1
COM-HRV-SH-386-02 | Current |  | Commercial | Heat Recovery Ventialation | Low Use | New Construction/Retrofit | space heating | High Efficient 85% Heat Recovery Ventilation Low Use Group (Office, Warehouse, School) | Ventilation with HRV Integrated | Ventilation without HRV |  |  | CFM | TRM Version 5.0 | 2020-11-12 | 0 | 2.11 | 0 | 0 | 0 | 0 | 0 | 8.35 | 14 | Direct Install | 0.05 | 1 | 1
COM-HRV-SH-388-02 | Current |  | Commercial | Heat Recovery Ventialation | Medium Use | New Construction/Retrofit | space heating | High Efficient 85% Heat Recovery Ventilation Medium Use Group (Hotel, Restaurant, Retail) | Ventilation with HRV Integrated | Ventilation without HRV |  |  | CFM | TRM Version 5.0 | 2020-11-12 | 0 | 3.3 | 0 | 0 | 0 | 0 | 0 | 8.35 | 14 | Direct Install | 0.05 | 1 | 1
COM-HRV-SH-390-02 | Current |  | Commercial | Heat Recovery Ventialation | Multi-Family, Health Care and Nursing Homes | New Construction/Retrofit | space heating | High Efficient 55% Heat Recovery Ventilation High Use Group (Multi-Residential, Health Care, Nursing Homes) | Ventilation with HRV Integrated | Ventilation without HRV |  |  | CFM | TRM Version 5.0 | 2020-11-12 | 0 | 3.84 | 0 | 0 | 0 | 0 | 0 | 5.35 | 14 | Direct Install | 0.05 | 1 | 1
COM-HRV-SH-392-02 | Current |  | Commercial | Heat Recovery Ventialation | Hotels | New Construction/Retrofit | space heating | High Efficient 55% Heat Recovery Ventilation Medium Use Group (Hotel, Restaurant, Retail) | Ventilation with HRV Integrated | Ventilation without HRV |  |  | CFM | TRM Version 5.0 | 2020-11-12 | 0 | 2.74 | 0 | 0 | 0 | 0 | 0 | 5.35 | 14 | Direct Install | 0.05 | 1 | 1
COM-HRV-SH-394-02 | Current |  | Commercial | Heat Recovery Ventialation | Restaurant | New Construction/Retrofit | space heating | High Efficient 55% Heat Recovery Ventilation Medium Use Group (Hotel, Restaurant, Retail) | Ventilation with HRV Integrated | Ventilation without HRV |  |  | CFM | TRM Version 5.0 | 2020-11-12 | 0 | 1.99 | 0 | 0 | 0 | 0 | 0 | 5.35 | 14 | Direct Install | 0.05 | 1 | 1
COM-HRV-SH-396-02 | Current |  | Commercial | Heat Recovery Ventialation | Retail | New Construction/Retrofit | space heating | High Efficient 55% Heat Recovery Ventilation Medium Use Group (Hotel, Restaurant, Retail) | Ventilation with HRV Integrated | Ventilation without HRV |  |  | CFM | TRM Version 5.0 | 2020-11-12 | 0 | 1.67 | 0 | 0 | 0 | 0 | 0 | 5.35 | 14 | Direct Install | 0.05 | 1 | 1
COM-HRV-SH-398-02 | Current |  | Commercial | Heat Recovery Ventialation | Office | New Construction/Retrofit | space heating | High Efficient 55% Heat Recovery Ventilation Low Use Group (Office, Warehouse, School) | Ventilation with HRV Integrated | Ventilation without HRV |  |  | CFM | TRM Version 5.0 | 2020-11-12 | 0 | 1.46 | 0 | 0 | 0 | 0 | 0 | 5.35 | 14 | Direct Install | 0.05 | 1 | 1
COM-HRV-SH-400-02 | Current |  | Commercial | Heat Recovery Ventialation | Warehouse | New Construction/Retrofit | space heating | High Efficient 55% Heat Recovery Ventilation Low Use Group (Office, Warehouse, School) | Ventilation with HRV Integrated | Ventilation without HRV |  |  | CFM | TRM Version 5.0 | 2020-11-12 | 0 | 1.39 | 0 | 0 | 0 | 0 | 0 | 5.35 | 14 | Direct Install | 0.05 | 1 | 1
COM-HRV-SH-402-02 | Current |  | Commercial | Heat Recovery Ventialation | School | New Construction/Retrofit | space heating | High Efficient 55% Heat Recovery Ventilation Low Use Group (Office, Warehouse, School) | Ventilation with HRV Integrated | Ventilation without HRV |  |  | CFM | TRM Version 5.0 | 2020-11-12 | 0 | 1.23 | 0 | 0 | 0 | 0 | 0 | 5.35 | 14 | Direct Install | 0.05 | 1 | 1
COM-HRV-SH-404-02 | Current |  | Commercial | Heat Recovery Ventialation | Multi-Family, Health Care and Nursing Homes | New Construction/Retrofit | space heating | High Efficient 65% Heat Recovery Ventilation High Use Group (Multi-Residential, Health Care, Nursing Homes) | Ventilation with HRV Integrated | Ventilation without HRV |  |  | CFM | TRM Version 5.0 | 2020-11-12 | 0 | 4.54 | 0 | 0 | 0 | 0 | 0 | 6.35 | 14 | Direct Install | 0.05 | 1 | 1
COM-HRV-SH-406-02 | Current |  | Commercial | Heat Recovery Ventialation | Hotels | New Construction/Retrofit | space heating | High Efficient 65% Heat Recovery Ventilation Medium Use Group (Hotel, Restaurant, Retail) | Ventilation with HRV Integrated | Ventilation without HRV |  |  | CFM | TRM Version 5.0 | 2020-11-12 | 0 | 3.24 | 0 | 0 | 0 | 0 | 0 | 6.35 | 14 | Direct Install | 0.05 | 1 | 1
COM-HRV-SH-408-02 | Current |  | Commercial | Heat Recovery Ventialation | Restaurant | New Construction/Retrofit | space heating | High Efficient 65% Heat Recovery Ventilation Medium Use Group (Hotel, Restaurant, Retail) | Ventilation with HRV Integrated | Ventilation without HRV |  |  | CFM | TRM Version 5.0 | 2020-11-12 | 0 | 2.35 | 0 | 0 | 0 | 0 | 0 | 6.35 | 14 | Direct Install | 0.05 | 1 | 1
COM-HRV-SH-410-02 | Current |  | Commercial | Heat Recovery Ventialation | Retail | New Construction/Retrofit | space heating | High Efficient 65% Heat Recovery Ventilation Medium Use Group (Hotel, Restaurant, Retail) | Ventilation with HRV Integrated | Ventilation without HRV |  |  | CFM | TRM Version 5.0 | 2020-11-12 | 0 | 1.97 | 0 | 0 | 0 | 0 | 0 | 6.35 | 14 | Direct Install | 0.05 | 1 | 1
COM-HRV-SH-412-02 | Current |  | Commercial | Heat Recovery Ventialation | Office | New Construction/Retrofit | space heating | High Efficient 65% Heat Recovery Ventilation Low Use Group (Office, Warehouse, School) | Ventilation with HRV Integrated | Ventilation without HRV |  |  | CFM | TRM Version 5.0 | 2020-11-12 | 0 | 1.73 | 0 | 0 | 0 | 0 | 0 | 6.35 | 14 | Direct Install | 0.05 | 1 | 1
COM-HRV-SH-414-02 | Current |  | Commercial | Heat Recovery Ventialation | Warehouse | New Construction/Retrofit | space heating | High Efficient 65% Heat Recovery Ventilation Low Use Group (Office, Warehouse, School) | Ventilation with HRV Integrated | Ventilation without HRV |  |  | CFM | TRM Version 5.0 | 2020-11-12 | 0 | 1.65 | 0 | 0 | 0 | 0 | 0 | 6.35 | 14 | Direct Install | 0.05 | 1 | 1
COM-HRV-SH-416-02 | Current |  | Commercial | Heat Recovery Ventialation | School | New Construction/Retrofit | space heating | High Efficient 65% Heat Recovery Ventilation Low Use Group (Office, Warehouse, School) | Ventilation with HRV Integrated | Ventilation without HRV |  |  | CFM | TRM Version 5.0 | 2020-11-12 | 0 | 1.46 | 0 | 0 | 0 | 0 | 0 | 6.35 | 14 | Direct Install | 0.05 | 1 | 1
COM-HRV-SH-418-02 | Current |  | Commercial | Heat Recovery Ventialation | Multi-Family, Health Care and Nursing Homes | New Construction/Retrofit | space heating | High Efficient 75% Heat Recovery Ventilation High Use Group (Multi-Residential, Health Care, Nursing Homes) | Ventilation with HRV Integrated | Ventilation without HRV |  |  | CFM | TRM Version 5.0 | 2020-11-12 | 0 | 5.24 | 0 | 0 | 0 | 0 | 0 | 7.35 | 14 | Direct Install | 0.05 | 1 | 1
COM-HRV-SH-420-02 | Current |  | Commercial | Heat Recovery Ventialation | Hotels | New Construction/Retrofit | space heating | High Efficient 75% Heat Recovery Ventilation Medium Use Group (Hotel, Restaurant, Retail) | Ventilation with HRV Integrated | Ventilation without HRV |  |  | CFM | TRM Version 5.0 | 2020-11-12 | 0 | 3.74 | 0 | 0 | 0 | 0 | 0 | 7.35 | 14 | Direct Install | 0.05 | 1 | 1
COM-HRV-SH-422-02 | Current |  | Commercial | Heat Recovery Ventialation | Restaurant | New Construction/Retrofit | space heating | High Efficient 75% Heat Recovery Ventilation Medium Use Group (Hotel, Restaurant, Retail) | Ventilation with HRV Integrated | Ventilation without HRV |  |  | CFM | TRM Version 5.0 | 2020-11-12 | 0 | 2.71 | 0 | 0 | 0 | 0 | 0 | 7.35 | 14 | Direct Install | 0.05 | 1 | 1
COM-HRV-SH-424-02 | Current |  | Commercial | Heat Recovery Ventialation | Retail | New Construction/Retrofit | space heating | High Efficient 75% Heat Recovery Ventilation Medium Use Group (Hotel, Restaurant, Retail) | Ventilation with HRV Integrated | Ventilation without HRV |  |  | CFM | TRM Version 5.0 | 2020-11-12 | 0 | 2.28 | 0 | 0 | 0 | 0 | 0 | 7.35 | 14 | Direct Install | 0.05 | 1 | 1
COM-HRV-SH-426-02 | Current |  | Commercial | Heat Recovery Ventialation | Office | New Construction/Retrofit | space heating | High Efficient 75% Heat Recovery Ventilation Low Use Group (Office, Warehouse, School) | Ventilation with HRV Integrated | Ventilation without HRV |  |  | CFM | TRM Version 5.0 | 2020-11-12 | 0 | 1.99 | 0 | 0 | 0 | 0 | 0 | 7.35 | 14 | Direct Install | 0.05 | 1 | 1
COM-HRV-SH-428-02 | Current |  | Commercial | Heat Recovery Ventialation | Warehouse | New Construction/Retrofit | space heating | High Efficient 75% Heat Recovery Ventilation Low Use Group (Office, Warehouse, School) | Ventilation with HRV Integrated | Ventilation without HRV |  |  | CFM | TRM Version 5.0 | 2020-11-12 | 0 | 1.9 | 0 | 0 | 0 | 0 | 0 | 7.35 | 14 | Direct Install | 0.05 | 1 | 1
COM-HRV-SH-430-02 | Current |  | Commercial | Heat Recovery Ventialation | School | New Construction/Retrofit | space heating | High Efficient 75% Heat Recovery Ventilation Low Use Group (Office, Warehouse, School) | Ventilation with HRV Integrated | Ventilation without HRV |  |  | CFM | TRM Version 5.0 | 2020-11-12 | 0 | 1.68 | 0 | 0 | 0 | 0 | 0 | 7.35 | 14 | Direct Install | 0.05 | 1 | 1
COM-HRV-SH-432-02 | Current |  | Commercial | Heat Recovery Ventialation | Multi-Family, Health Care and Nursing Homes | New Construction/Retrofit | space heating | High Efficient 85% Heat Recovery Ventilation High Use Group (Multi-Residential, Health Care, Nursing Homes) | Ventilation with HRV Integrated | Ventilation without HRV |  |  | CFM | TRM Version 5.0 | 2020-11-12 | 0 | 5.93 | 0 | 0 | 0 | 0 | 0 | 8.35 | 14 | Direct Install | 0.05 | 1 | 1
COM-HRV-SH-434-02 | Current |  | Commercial | Heat Recovery Ventialation | Hotels | New Construction/Retrofit | space heating | High Efficient 85% Heat Recovery Ventilation Medium Use Group (Hotel, Restaurant, Retail) | Ventilation with HRV Integrated | Ventilation without HRV |  |  | CFM | TRM Version 5.0 | 2020-11-12 | 0 | 4.24 | 0 | 0 | 0 | 0 | 0 | 8.35 | 14 | Direct Install | 0.05 | 1 | 1
COM-HRV-SH-436-02 | Current |  | Commercial | Heat Recovery Ventialation | Restaurant | New Construction/Retrofit | space heating | High Efficient 85% Heat Recovery Ventilation Medium Use Group (Hotel, Restaurant, Retail) | Ventilation with HRV Integrated | Ventilation without HRV |  |  | CFM | TRM Version 5.0 | 2020-11-12 | 0 | 3.07 | 0 | 0 | 0 | 0 | 0 | 8.35 | 14 | Direct Install | 0.05 | 1 | 1
COM-HRV-SH-438-02 | Current |  | Commercial | Heat Recovery Ventialation | Retail | New Construction/Retrofit | space heating | High Efficient 85% Heat Recovery Ventilation Medium Use Group (Hotel, Restaurant, Retail) | Ventilation with HRV Integrated | Ventilation without HRV |  |  | CFM | TRM Version 5.0 | 2020-11-12 | 0 | 2.58 | 0 | 0 | 0 | 0 | 0 | 8.35 | 14 | Direct Install | 0.05 | 1 | 1
COM-HRV-SH-440-02 | Current |  | Commercial | Heat Recovery Ventialation | Office | New Construction/Retrofit | space heating | High Efficient 85% Heat Recovery Ventilation Low Use Group (Office, Warehouse, School) | Ventilation with HRV Integrated | Ventilation without HRV |  |  | CFM | TRM Version 5.0 | 2020-11-12 | 0 | 2.26 | 0 | 0 | 0 | 0 | 0 | 8.35 | 14 | Direct Install | 0.05 | 1 | 1
COM-HRV-SH-442-02 | Current |  | Commercial | Heat Recovery Ventialation | Warehouse | New Construction/Retrofit | space heating | High Efficient 85% Heat Recovery Ventilation Low Use Group (Office, Warehouse, School) | Ventilation with HRV Integrated | Ventilation without HRV |  |  | CFM | TRM Version 5.0 | 2020-11-12 | 0 | 2.15 | 0 | 0 | 0 | 0 | 0 | 8.35 | 14 | Direct Install | 0.05 | 1 | 1
COM-HRV-SH-444-02 | Current |  | Commercial | Heat Recovery Ventialation | School | New Construction/Retrofit | space heating | High Efficient 85% Heat Recovery Ventilation Low Use Group (Office, Warehouse, School) | Ventilation with HRV Integrated | Ventilation without HRV |  |  | CFM | TRM Version 5.0 | 2020-11-12 | 0 | 1.91 | 0 | 0 | 0 | 0 | 0 | 8.35 | 14 | Direct Install | 0.05 | 1 | 1
COM-HRV-SH-367-02 | Current |  | Commercial | Heat Recovery Ventialation | High Use | New Construction/Retrofit | space heating | High Efficient 55% Heat Recovery Ventilation High Use Group (Multi-Residential, Health Care, Nursing Homes) | Ventilation with HRV Standalone | Ventilation without HRV |  |  | CFM | TRM Version 5.0 | 2020-11-12 | 0 | 3.84 | 0 | -4.39 | 0 | 0 | 0 | 8.28 | 14 | Direct Install | 0.05 | 1 | 1
COM-HRV-SH-369-02 | Current |  | Commercial | Heat Recovery Ventialation | Low Use | New Construction/Retrofit | space heating | High Efficient 55% Heat Recovery Ventilation Low Use Group (Office, Warehouse, School) | Ventilation with HRV Standalone | Ventilation without HRV |  |  | CFM | TRM Version 5.0 | 2020-11-12 | 0 | 1.36 | 0 | -1.56 | 0 | 0 | 0 | 8.28 | 14 | Direct Install | 0.05 | 1 | 1
COM-HRV-SH-371-02 | Current |  | Commercial | Heat Recovery Ventialation | Medium Use | New Construction/Retrofit | space heating | High Efficient 55% Heat Recovery Ventilation Medium Use Group (Hotel, Restaurant, Retail) | Ventilation with HRV Standalone | Ventilation without HRV |  |  | CFM | TRM Version 5.0 | 2020-11-12 | 0 | 2.13 | 0 | -2.44 | 0 | 0 | 0 | 8.28 | 14 | Direct Install | 0.05 | 1 | 1
COM-HRV-SH-373-02 | Current |  | Commercial | Heat Recovery Ventialation | High Use | New Construction/Retrofit | space heating | High Efficient 65% Heat Recovery Ventilation High Use Group (Multi-Residential, Health Care, Nursing Homes) | Ventilation with HRV Standalone | Ventilation without HRV |  |  | CFM | TRM Version 5.0 | 2020-11-12 | 0 | 4.54 | 0 | -4.39 | 0 | 0 | 0 | 9.28 | 14 | Direct Install | 0.05 | 1 | 1
COM-HRV-SH-375-02 | Current |  | Commercial | Heat Recovery Ventialation | Low Use | New Construction/Retrofit | space heating | High Efficient 65% Heat Recovery Ventilation Low Use Group (Office, Warehouse, School) | Ventilation with HRV Standalone | Ventilation without HRV |  |  | CFM | TRM Version 5.0 | 2020-11-12 | 0 | 1.61 | 0 | -1.56 | 0 | 0 | 0 | 9.28 | 14 | Direct Install | 0.05 | 1 | 1
COM-HRV-SH-377-02 | Current |  | Commercial | Heat Recovery Ventialation | Medium Use | New Construction/Retrofit | space heating | High Efficient 65% Heat Recovery Ventilation Medium Use Group (Hotel, Restaurant, Retail) | Ventilation with HRV Standalone | Ventilation without HRV |  |  | CFM | TRM Version 5.0 | 2020-11-12 | 0 | 2.52 | 0 | -2.44 | 0 | 0 | 0 | 9.28 | 14 | Direct Install | 0.05 | 1 | 1
COM-HRV-SH-379-02 | Current |  | Commercial | Heat Recovery Ventialation | High Use | New Construction/Retrofit | space heating | High Efficient 75% Heat Recovery Ventilation High Use Group (Multi-Residential, Health Care, Nursing Homes) | Ventilation with HRV Standalone | Ventilation without HRV |  |  | CFM | TRM Version 5.0 | 2020-11-12 | 0 | 5.24 | 0 | -4.39 | 0 | 0 | 0 | 10.28 | 14 | Direct Install | 0.05 | 1 | 1
COM-HRV-SH-381-02 | Current |  | Commercial | Heat Recovery Ventialation | Low Use | New Construction/Retrofit | space heating | High Efficient 75% Heat Recovery Ventilation Low Use Group (Office, Warehouse, School) | Ventilation with HRV Standalone | Ventilation without HRV |  |  | CFM | TRM Version 5.0 | 2020-11-12 | 0 | 1.86 | 0 | -1.56 | 0 | 0 | 0 | 10.28 | 14 | Direct Install | 0.05 | 1 | 1
COM-HRV-SH-383-02 | Current |  | Commercial | Heat Recovery Ventialation | Medium Use | New Construction/Retrofit | space heating | High Efficient 75% Heat Recovery Ventilation Medium Use Group (Hotel, Restaurant, Retail) | Ventilation with HRV Standalone | Ventilation without HRV |  |  | CFM | TRM Version 5.0 | 2020-11-12 | 0 | 2.91 | 0 | -2.44 | 0 | 0 | 0 | 10.28 | 14 | Direct Install | 0.05 | 1 | 1
COM-HRV-SH-385-02 | Current |  | Commercial | Heat Recovery Ventialation | High Use | New Construction/Retrofit | space heating | High Efficient 85% Heat Recovery Ventilation High Use Group (Multi-Residential, Health Care, Nursing Homes) | Ventilation with HRV Standalone | Ventilation without HRV |  |  | CFM | TRM Version 5.0 | 2020-11-12 | 0 | 5.93 | 0 | -4.39 | 0 | 0 | 0 | 11.28 | 14 | Direct Install | 0.05 | 1 | 1
COM-HRV-SH-387-02 | Current |  | Commercial | Heat Recovery Ventialation | Low Use | New Construction/Retrofit | space heating | High Efficient 85% Heat Recovery Ventilation Low Use Group (Office, Warehouse, School) | Ventilation with HRV Standalone | Ventilation without HRV |  |  | CFM | TRM Version 5.0 | 2020-11-12 | 0 | 2.11 | 0 | -1.56 | 0 | 0 | 0 | 11.28 | 14 | Direct Install | 0.05 | 1 | 1
COM-HRV-SH-389-02 | Current |  | Commercial | Heat Recovery Ventialation | Medium Use | New Construction/Retrofit | space heating | High Efficient 85% Heat Recovery Ventilation Medium Use Group (Hotel, Restaurant, Retail) | Ventilation with HRV Standalone | Ventilation without HRV |  |  | CFM | TRM Version 5.0 | 2020-11-12 | 0 | 3.3 | 0 | -2.44 | 0 | 0 | 0 | 11.28 | 14 | Direct Install | 0.05 | 1 | 1
COM-HRV-SH-391-02 | Current |  | Commercial | Heat Recovery Ventialation | Multi-Family, Health Care and Nursing Homes | New Construction/Retrofit | space heating | High Efficient 55% Heat Recovery Ventilation High Use Group (Multi-Residential, Health Care, Nursing Homes) | Ventilation with HRV Standalone | Ventilation without HRV |  |  | CFM | TRM Version 5.0 | 2020-11-12 | 0 | 3.84 | 0 | -4.39 | 0 | 0 | 0 | 8.28 | 14 | Direct Install | 0.05 | 1 | 1
COM-HRV-SH-393-02 | Current |  | Commercial | Heat Recovery Ventialation | Hotels | New Construction/Retrofit | space heating | High Efficient 55% Heat Recovery Ventilation Medium Use Group (Hotel, Restaurant, Retail) | Ventilation with HRV Standalone | Ventilation without HRV |  |  | CFM | TRM Version 5.0 | 2020-11-12 | 0 | 2.74 | 0 | -3.14 | 0 | 0 | 0 | 8.28 | 14 | Direct Install | 0.05 | 1 | 1
COM-HRV-SH-395-02 | Current |  | Commercial | Heat Recovery Ventialation | Restaurant | New Construction/Retrofit | space heating | High Efficient 55% Heat Recovery Ventilation Medium Use Group (Hotel, Restaurant, Retail) | Ventilation with HRV Standalone | Ventilation without HRV |  |  | CFM | TRM Version 5.0 | 2020-11-12 | 0 | 1.99 | 0 | -2.28 | 0 | 0 | 0 | 8.28 | 14 | Direct Install | 0.05 | 1 | 1
COM-HRV-SH-397-02 | Current |  | Commercial | Heat Recovery Ventialation | Retail | New Construction/Retrofit | space heating | High Efficient 55% Heat Recovery Ventilation Medium Use Group (Hotel, Restaurant, Retail) | Ventilation with HRV Standalone | Ventilation without HRV |  |  | CFM | TRM Version 5.0 | 2020-11-12 | 0 | 1.67 | 0 | -1.91 | 0 | 0 | 0 | 8.28 | 14 | Direct Install | 0.05 | 1 | 1
COM-HRV-SH-399-02 | Current |  | Commercial | Heat Recovery Ventialation | Office | New Construction/Retrofit | space heating | High Efficient 55% Heat Recovery Ventilation Low Use Group (Office, Warehouse, School) | Ventilation with HRV Standalone | Ventilation without HRV |  |  | CFM | TRM Version 5.0 | 2020-11-12 | 0 | 1.46 | 0 | -1.67 | 0 | 0 | 0 | 8.28 | 14 | Direct Install | 0.05 | 1 | 1
COM-HRV-SH-401-02 | Current |  | Commercial | Heat Recovery Ventialation | Warehouse | New Construction/Retrofit | space heating | High Efficient 55% Heat Recovery Ventilation Low Use Group (Office, Warehouse, School) | Ventilation with HRV Standalone | Ventilation without HRV |  |  | CFM | TRM Version 5.0 | 2020-11-12 | 0 | 1.39 | 0 | -1.6 | 0 | 0 | 0 | 8.28 | 14 | Direct Install | 0.05 | 1 | 1
COM-HRV-SH-403-02 | Current |  | Commercial | Heat Recovery Ventialation | School | New Construction/Retrofit | space heating | High Efficient 55% Heat Recovery Ventilation Low Use Group (Office, Warehouse, School) | Ventilation with HRV Standalone | Ventilation without HRV |  |  | CFM | TRM Version 5.0 | 2020-11-12 | 0 | 1.23 | 0 | -1.41 | 0 | 0 | 0 | 8.28 | 14 | Direct Install | 0.05 | 1 | 1
COM-HRV-SH-405-02 | Current |  | Commercial | Heat Recovery Ventialation | Multi-Family, Health Care and Nursing Homes | New Construction/Retrofit | space heating | High Efficient 65% Heat Recovery Ventilation High Use Group (Multi-Residential, Health Care, Nursing Homes) | Ventilation with HRV Standalone | Ventilation without HRV |  |  | CFM | TRM Version 5.0 | 2020-11-12 | 0 | 4.54 | 0 | -4.39 | 0 | 0 | 0 | 9.28 | 14 | Direct Install | 0.05 | 1 | 1
COM-HRV-SH-407-02 | Current |  | Commercial | Heat Recovery Ventialation | Hotels | New Construction/Retrofit | space heating | High Efficient 65% Heat Recovery Ventilation Medium Use Group (Hotel, Restaurant, Retail) | Ventilation with HRV Standalone | Ventilation without HRV |  |  | CFM | TRM Version 5.0 | 2020-11-12 | 0 | 3.24 | 0 | -3.14 | 0 | 0 | 0 | 9.28 | 14 | Direct Install | 0.05 | 1 | 1
COM-HRV-SH-409-02 | Current |  | Commercial | Heat Recovery Ventialation | Restaurant | New Construction/Retrofit | space heating | High Efficient 65% Heat Recovery Ventilation Medium Use Group (Hotel, Restaurant, Retail) | Ventilation with HRV Standalone | Ventilation without HRV |  |  | CFM | TRM Version 5.0 | 2020-11-12 | 0 | 2.35 | 0 | -2.28 | 0 | 0 | 0 | 9.28 | 14 | Direct Install | 0.05 | 1 | 1
COM-HRV-SH-411-02 | Current |  | Commercial | Heat Recovery Ventialation | Retail | New Construction/Retrofit | space heating | High Efficient 65% Heat Recovery Ventilation Medium Use Group (Hotel, Restaurant, Retail) | Ventilation with HRV Standalone | Ventilation without HRV |  |  | CFM | TRM Version 5.0 | 2020-11-12 | 0 | 1.97 | 0 | -1.91 | 0 | 0 | 0 | 9.28 | 14 | Direct Install | 0.05 | 1 | 1
COM-HRV-SH-413-02 | Current |  | Commercial | Heat Recovery Ventialation | Office | New Construction/Retrofit | space heating | High Efficient 65% Heat Recovery Ventilation Low Use Group (Office, Warehouse, School) | Ventilation with HRV Standalone | Ventilation without HRV |  |  | CFM | TRM Version 5.0 | 2020-11-12 | 0 | 1.73 | 0 | -1.67 | 0 | 0 | 0 | 9.28 | 14 | Direct Install | 0.05 | 1 | 1
COM-HRV-SH-415-02 | Current |  | Commercial | Heat Recovery Ventialation | Warehouse | New Construction/Retrofit | space heating | High Efficient 65% Heat Recovery Ventilation Low Use Group (Office, Warehouse, School) | Ventilation with HRV Standalone | Ventilation without HRV |  |  | CFM | TRM Version 5.0 | 2020-11-12 | 0 | 1.65 | 0 | -1.6 | 0 | 0 | 0 | 9.28 | 14 | Direct Install | 0.05 | 1 | 1
COM-HRV-SH-417-02 | Current |  | Commercial | Heat Recovery Ventialation | School | New Construction/Retrofit | space heating | High Efficient 65% Heat Recovery Ventilation Low Use Group (Office, Warehouse, School) | Ventilation with HRV Standalone | Ventilation without HRV |  |  | CFM | TRM Version 5.0 | 2020-11-12 | 0 | 1.46 | 0 | -1.41 | 0 | 0 | 0 | 9.28 | 14 | Direct Install | 0.05 | 1 | 1
COM-HRV-SH-419-02 | Current |  | Commercial | Heat Recovery Ventialation | Multi-Family, Health Care and Nursing Homes | New Construction/Retrofit | space heating | High Efficient 75% Heat Recovery Ventilation High Use Group (Multi-Residential, Health Care, Nursing Homes) | Ventilation with HRV Standalone | Ventilation without HRV |  |  | CFM | TRM Version 5.0 | 2020-11-12 | 0 | 5.24 | 0 | -4.39 | 0 | 0 | 0 | 10.28 | 14 | Direct Install | 0.05 | 1 | 1
COM-HRV-SH-421-02 | Current |  | Commercial | Heat Recovery Ventialation | Hotels | New Construction/Retrofit | space heating | High Efficient 75% Heat Recovery Ventilation Medium Use Group (Hotel, Restaurant, Retail) | Ventilation with HRV Standalone | Ventilation without HRV |  |  | CFM | TRM Version 5.0 | 2020-11-12 | 0 | 3.74 | 0 | -3.14 | 0 | 0 | 0 | 10.28 | 14 | Direct Install | 0.05 | 1 | 1
COM-HRV-SH-423-02 | Current |  | Commercial | Heat Recovery Ventialation | Restaurant | New Construction/Retrofit | space heating | High Efficient 75% Heat Recovery Ventilation Medium Use Group (Hotel, Restaurant, Retail) | Ventilation with HRV Standalone | Ventilation without HRV |  |  | CFM | TRM Version 5.0 | 2020-11-12 | 0 | 2.71 | 0 | -2.28 | 0 | 0 | 0 | 10.28 | 14 | Direct Install | 0.05 | 1 | 1
COM-HRV-SH-425-02 | Current |  | Commercial | Heat Recovery Ventialation | Retail | New Construction/Retrofit | space heating | High Efficient 75% Heat Recovery Ventilation Medium Use Group (Hotel, Restaurant, Retail) | Ventilation with HRV Standalone | Ventilation without HRV |  |  | CFM | TRM Version 5.0 | 2020-11-12 | 0 | 2.28 | 0 | -1.91 | 0 | 0 | 0 | 10.28 | 14 | Direct Install | 0.05 | 1 | 1
COM-HRV-SH-427-02 | Current |  | Commercial | Heat Recovery Ventialation | Office | New Construction/Retrofit | space heating | High Efficient 75% Heat Recovery Ventilation Low Use Group (Office, Warehouse, School) | Ventilation with HRV Standalone | Ventilation without HRV |  |  | CFM | TRM Version 5.0 | 2020-11-12 | 0 | 1.99 | 0 | -1.67 | 0 | 0 | 0 | 10.28 | 14 | Direct Install | 0.05 | 1 | 1
COM-HRV-SH-429-02 | Current |  | Commercial | Heat Recovery Ventialation | Warehouse | New Construction/Retrofit | space heating | High Efficient 75% Heat Recovery Ventilation Low Use Group (Office, Warehouse, School) | Ventilation with HRV Standalone | Ventilation without HRV |  |  | CFM | TRM Version 5.0 | 2020-11-12 | 0 | 1.9 | 0 | -1.6 | 0 | 0 | 0 | 10.28 | 14 | Direct Install | 0.05 | 1 | 1
COM-HRV-SH-431-02 | Current |  | Commercial | Heat Recovery Ventialation | School | New Construction/Retrofit | space heating | High Efficient 75% Heat Recovery Ventilation Low Use Group (Office, Warehouse, School) | Ventilation with HRV Standalone | Ventilation without HRV |  |  | CFM | TRM Version 5.0 | 2020-11-12 | 0 | 1.68 | 0 | -1.41 | 0 | 0 | 0 | 10.28 | 14 | Direct Install | 0.05 | 1 | 1
COM-HRV-SH-433-02 | Current |  | Commercial | Heat Recovery Ventialation | Multi-Family, Health Care and Nursing Homes | New Construction/Retrofit | space heating | High Efficient 85% Heat Recovery Ventilation High Use Group (Multi-Residential, Health Care, Nursing Homes) | Ventilation with HRV Standalone | Ventilation without HRV |  |  | CFM | TRM Version 5.0 | 2020-11-12 | 0 | 5.93 | 0 | -4.39 | 0 | 0 | 0 | 11.28 | 14 | Direct Install | 0.05 | 1 | 1
COM-HRV-SH-435-02 | Current |  | Commercial | Heat Recovery Ventialation | Hotels | New Construction/Retrofit | space heating | High Efficient 85% Heat Recovery Ventilation Medium Use Group (Hotel, Restaurant, Retail) | Ventilation with HRV Standalone | Ventilation without HRV |  |  | CFM | TRM Version 5.0 | 2020-11-12 | 0 | 4.24 | 0 | -3.14 | 0 | 0 | 0 | 11.28 | 14 | Direct Install | 0.05 | 1 | 1
COM-HRV-SH-437-02 | Current |  | Commercial | Heat Recovery Ventialation | Restaurant | New Construction/Retrofit | space heating | High Efficient 85% Heat Recovery Ventilation Medium Use Group (Hotel, Restaurant, Retail) | Ventilation with HRV Standalone | Ventilation without HRV |  |  | CFM | TRM Version 5.0 | 2020-11-12 | 0 | 3.07 | 0 | -2.28 | 0 | 0 | 0 | 11.28 | 14 | Direct Install | 0.05 | 1 | 1
COM-HRV-SH-439-02 | Current |  | Commercial | Heat Recovery Ventialation | Retail | New Construction/Retrofit | space heating | High Efficient 85% Heat Recovery Ventilation Medium Use Group (Hotel, Restaurant, Retail) | Ventilation with HRV Standalone | Ventilation without HRV |  |  | CFM | TRM Version 5.0 | 2020-11-12 | 0 | 2.58 | 0 | -1.91 | 0 | 0 | 0 | 11.28 | 14 | Direct Install | 0.05 | 1 | 1
COM-HRV-SH-441-02 | Current |  | Commercial | Heat Recovery Ventialation | Office | New Construction/Retrofit | space heating | High Efficient 85% Heat Recovery Ventilation Low Use Group (Office, Warehouse, School) | Ventilation with HRV Standalone | Ventilation without HRV |  |  | CFM | TRM Version 5.0 | 2020-11-12 | 0 | 2.26 | 0 | -1.67 | 0 | 0 | 0 | 11.28 | 14 | Direct Install | 0.05 | 1 | 1
COM-HRV-SH-443-02 | Current |  | Commercial | Heat Recovery Ventialation | Warehouse | New Construction/Retrofit | space heating | High Efficient 85% Heat Recovery Ventilation Low Use Group (Office, Warehouse, School) | Ventilation with HRV Standalone | Ventilation without HRV |  |  | CFM | TRM Version 5.0 | 2020-11-12 | 0 | 2.15 | 0 | -1.6 | 0 | 0 | 0 | 11.28 | 14 | Direct Install | 0.05 | 1 | 1
COM-HRV-SH-445-02 | Current |  | Commercial | Heat Recovery Ventialation | School | New Construction/Retrofit | space heating | High Efficient 85% Heat Recovery Ventilation Low Use Group (Office, Warehouse, School) | Ventilation with HRV Standalone | Ventilation without HRV |  |  | CFM | TRM Version 5.0 | 2020-11-12 | 0 | 1.91 | 0 | -1.41 | 0 | 0 | 0 | 11.28 | 14 | Direct Install | 0.05 | 1 | 1
COM-CM-SH-498-02 | Current |  | Commercial | Condensing Make Up Air Unit | Commercial | New Construction/Natural Replacement | space heating | Condensing Make Up Air Unit (MUA) - Commercial | VFD | Conventional MUA | 80% Thermal Efficiency |  | CFM | TRM Version 5.0 | 2020-11-12 | 0 | 2.03 | 0 | 2.04 | 0 | 0 | 870 | 1.02 | 20 | Direct Install | 0.05 | 1 | 1
COM-CM-SH-501-02 | Current |  | Commercial | Condensing Make Up Air Unit | Multi-Residential and Long Term Care | New Construction/Natural Replacement | space heating | Condensing Make Up Air Unit (MUA) - Commercial | VFD | Conventional MUA | 80% Thermal Efficiency |  | CFM | TRM Version 5.0 | 2020-11-12 | 0 | 3 | 0 | 2.3 | 0 | 0 | 870 | 1.02 | 20 | Direct Install | 0.05 | 1 | 1
COM-CMB-FS-621-03 | Current |  | Commercial | Combination Oven |  | New Construction/Natural Replacement | food service | Energy Star Combination Oven | Energy Star Rated Combiniation Oven, 15-28 pan | Conventional combination oven |  | unit |  | TRM Version 6.0 | 2021-12-16 | 1295 | 0 | 4747 | 0 | 51684 | 0 | 5007 | 0 | 12 | Direct Install | 0.2 | 1 | 1
COM-CMB-FS-622-03 | Current |  | Commercial | Combination Oven |  | New Construction/Natural Replacement | food service | Energy Star Combination Oven | Energy Star Rated Combiniation Oven, 29+ pan | Conventional combination oven |  | unit |  | TRM Version 6.0 | 2021-12-16 | 1048 | 0 | 485 | 0 | 599459 | 0 | 8507 | 0 | 12 | Direct Install | 0.2 | 1 | 1
COM-CMB-FS-623-03 | Current |  | Commercial | Combination Oven |  | New Construction/Natural Replacement | food service | Energy Star Combination Oven | Energy Star Rated Combiniation Oven, average | Conventional combination oven |  | unit |  | TRM Version 6.0 | 2021-12-16 | 1186 | 0 | 2088 | 0 | 145120 | 0 | 4440 | 0 | 12 | Direct Install | 0.2 | 1 | 1
COM-CO-FS-520-02 | Current |  | Commercial | Convection Ovens |  | New Construction/Natural Replacement | food service | Energy Star Convection Ovens | Energy Star Rated Convection Oven (Full Size) | Conventional Convection Oven (Full Size) |  | unit |  | TRM Version 6.0 | 2021-12-16 | 954 | 0 | 44.2 | 0 | 0 | 0 | 1200 | 0 | 12 | Direct Install | 0.2 | 1 | 1
COM-RO-FS-651-03 | Current |  | Commercial | Rack Oven |  | New Construction/Natural Replacement | food service | ENERGY STAR Rack Oven | Energy Star Rated Rack Oven, Double | Conventiona rack oven |  | unit |  | TRM Version 6.0 | 2021-12-16 | 1187 | 0 | 1858 | 0 | 0 | 0 | 2591 | 0 | 12 | Direct Install | 0.2 | 1 | 1
COM-RO-FS-650-03 | Current |  | Commercial | Rack Oven |  | New Construction/Natural Replacement | food service | ENERGY STAR Rack Oven | Energy Star Rated Rack Oven, Single | Conventiona rack oven |  | unit |  | TRM Version 6.0 | 2021-12-16 | 915 | 0 | 826 | 0 | 0 | 0 | 1544 | 0 | 12 | Direct Install | 0.2 | 1 | 1
COM-OL-WH-329-02 | Current |  | Commercial | Ozone Laundry |  | New Construction/Retrofit | water heating | Commercial Ozone Laundry Treatment | Ozone Treatment Tunnel Washer <= 120 lbs | Commercial laundry with no ozone treatment system |  |  | lbs/yr | TRM Version 7.0 | 2022-11-30 | 0 | 0.0295 | 0 | 0.0015 | 0 | 1.29 | 71429 | 0 | 15 | Direct Install | 0.08 | 1 | 1
COM-OL-WH-331-02 | Current |  | Commercial | Ozone Laundry |  | New Construction/Retrofit | water heating | Commercial Ozone Laundry Treatment | Ozone Treatment Tunnel Washer=> 500 lbs | Commercial laundry with no ozone treatment system |  |  | lbs/yr | TRM Version 7.0 | 2022-11-30 | 0 | 0.0295 | 0 | 0.0015 | 0 | 1.29 | 228571 | 0 | 15 | Direct Install | 0.08 | 1 | 1
COM-OL-WH-330-02 | Current |  | Commercial | Ozone Laundry |  | New Construction/Retrofit | water heating | Commercial Ozone Laundry Treatment | Ozone Treatment Tunnel Washer 121 lbs to 499 lbs | Commercial laundry with no ozone treatment system |  |  | lbs/yr | TRM Version 7.0 | 2022-11-30 | 0 | 0.0295 | 0 | 0.0015 | 0 | 1.29 | 150000 | 0 | 15 | Direct Install | 0.08 | 1 | 1
COM-OL-WH-326-02 | Current |  | Commercial | Ozone Laundry |  | New Construction/Retrofit | water heating | Commercial Ozone Laundry Treatment | Ozone Treatment Washer extractor =< 60 lbs | Commercial laundry with no ozone treatment system |  |  | lbs/yr | TRM Version 7.0 | 2022-11-30 | 0 | 0.0376 | 0 | 0.00211 | 0 | 2.1 | 15714 | 0 | 15 | Direct Install | 0.08 | 1 | 1
COM-OL-WH-327-02 | Current |  | Commercial | Ozone Laundry |  | New Construction/Retrofit | water heating | Commercial Ozone Laundry Treatment | Ozone Treatment Washer extractor 61 lbs to 499 lbs | Commercial laundry with no ozone treatment system |  |  | lbs/yr | TRM Version 7.0 | 2022-11-30 | 0 | 0.0376 | 0 | 0.00211 | 0 | 2.1 | 35714 | 0 | 15 | Direct Install | 0.08 | 1 | 1
COM-OL-WH-328-02 | Current |  | Commercial | Ozone Laundry |  | New Construction/Retrofit | water heating | Commercial Ozone Laundry Treatment | Ozone Treatment Washer extractor=> 500 lbs | Commercial laundry with no ozone treatment system |  |  | lbs/yr | TRM Version 7.0 | 2022-11-30 | 0 | 0.0376 | 0 | 0.00211 | 0 | 2.1 | 44286 | 0 | 15 | Direct Install | 0.08 | 1 | 1
COM-CMB-FS-620-03 | Current |  | Commercial | Combination Oven |  | New Construction/Natural Replacement | food service | Energy Star Combination Oven | Energy Star Rated Combination Oven, 6-14 pan | Conventional combination oven |  | unit |  | TRM Version 6.0 | 2021-12-16 | 1104 | 0 | 72 | 0 | 209664 | 0 | 3941 | 0 | 12 | Direct Install | 0.2 | 1 | 1
COM-GR-FS-800-03 | Current |  | Commercial | Griddles |  | New Construction/Natural Replacement | food service | Energy Star Griddle | ENERGY STAR Certified Griddle | Non-ENERGY STAR Griddle |  |  | ft | TRM Version 7.0 | 2022-11-30 | 0 | 439 | 0 | 0 | 0 | 0 | 0 | 1096 | 12 | Direct Install | 0.2 | 1 | 1
COM-GR-FS-801-03 | Current |  | Commercial | Griddles |  | New Construction/Natural Replacement | food service | Energy Star Griddle | ENERGY STAR Certified Griddle | Non-ENERGY STAR Griddle |  | unit |  | TRM Version 7.0 | 2022-11-30 | 1974 | 0 | 0 | 0 | 0 | 0 | 4581 | 0 | 12 | Direct Install | 0.2 | 1 | 1
COM-FR-FS-325-02 | Current | Split measure into two Vat sizes | Commercial | Fryer |  | New Construction/Natural Replacement | food service | Energy Star Fryer, Standard Vat | Energy Star Rated Fryer | Non-Energy Star rated Fryer |  | unit |  | TRM Version 7.0 | 2022-11-30 | 1466 | 0 | 0 | 0 | 0 | 0 | 2657 | 0 | 12 | Direct Install | 0.2 | 1 | 1
COM-FR-FS-326-02 | Current | Split measure into two Vat sizes | Commercial | Fryer |  | New Construction/Natural Replacement | food service | Energy Star Fryer, Large Vat | Energy Star Rated Fryer | Non-Energy Star rated Fryer |  | unit |  | TRM Version 7.0 | 2022-11-30 | 1709 | 0 | 0 | 0 | 0 | 0 | 3113 | 0 | 12 | Direct Install | 0.2 | 1 | 1
COM-SC-FS-325-02 | Current |  | Commercial | Steam Cookers |  | New Construction/Natural Replacement | food service | Energy Star Steam Cookers | Energy Star Rated Steam Cooker | Boiler-based steam cooker |  | unit |  | TRM Version 7.0 | 2022-11-30 | 8461 | 0 | 0 | 0 | 1109458 | 0 | 3045 | 0 | 12 | Direct Install | 0.2 | 1 | 1
COM-CNB-FS-810-03 | Current | New measure in TRM V7.0 | Commercial | Conveyor Broiler |  | New Construction/Natural Replacement | food service | Energy-Efficient Conveyor Broiler, <22" width | high-efficiency conveyor broiler with a catalyst and an idle input rate less than the rates listed below or a dual stage or modulating gas valve with a capability of throttling the input rate below the idle rates <40,000 Btu/h | Conventional Conveyor Broiler |  | unit |  | TRM Version 7.0 | 2022-11-30 | 1954 | 0 | 2443 | 0 | 0 | 0 | 3154 | 0 | 12 | Direct Install | 0.2 | 1 | 1
COM-CNB-FS-811-03 | Current | New measure in TRM V7.0 | Commercial | Conveyor Broiler |  | New Construction/Natural Replacement | food service | Energy-Efficient Conveyor Broiler, 22" - 26" width | high-efficiency conveyor broiler with a catalyst and an idle input rate less than the rates listed below or a dual stage or modulating gas valve with a capability of throttling the input rate below the idle rates <60,000 Btu/h | Conventional Conveyor Broiler |  | unit |  | TRM Version 7.0 | 2022-11-30 | 3070 | 0 | 3839 | 0 | 0 | 0 | 3933 | 0 | 12 | Direct Install | 0.2 | 1 | 1
COM-CNB-FS-812-03 | Current | New measure in TRM V7.0 | Commercial | Conveyor Broiler |  | New Construction/Natural Replacement | food service | Energy-Efficient Conveyor Broiler, > 26" width | high-efficiency conveyor broiler with a catalyst and an idle input rate less than the rates listed below or a dual stage or modulating gas valve with a capability of throttling the input rate below the idle rates <70,000 Btu/h | Conventional Conveyor Broiler |  | unit |  | TRM Version 7.0 | 2022-11-30 | 3768 | 0 | 4712 | 0 | 0 | 0 | 4586 | 0 | 12 | Direct Install | 0.2 | 1 | 1
COM-CNO-FS-806-03 | Current | New measure in TRM V7.0 | Commercial | Conveyor Oven |  | New Construction/Natural Replacement | food service | Energy-Efficient Conveyor Oven, large ≥ 1520 sq in | Large Conveyor Oven Chamber Area ≥ 1520 sq in, 45% cooking efficiency | Conventional Conveyor Oven |  | unit |  | TRM Version 7.0 | 2022-11-30 | 1519 | 0 | 2601 | 0 | 0 | 0 | 1994 | 0 | 12 | Direct Install | 0.2 | 1 | 1
COM-UB-FS-332-02 | Current |  | Commercial | Under-Fired Broilers |  | New Construction/Natural Replacement | food service | High Efficiency Under-Fired Broilers - 3 foot | low idle energy rate (≤22,000 Btu/hr per linear foot) | Conventional Efficiency Under-Fired Broiler | conventional underfired broiler | unit |  | TRM Version 7.0 | 2022-11-30 | 2636 | 0 | 0 | 0 | 0 | 0 | 1868 | 0 | 12 | Direct Install | 0.2 | 1 | 1
COM-UB-FS-333-02 | Current |  | Commercial | Under-Fired Broilers |  | New Construction/Natural Replacement | food service | High Efficiency Under-Fired Broilers - 4 foot | low idle energy rate (≤22,000 Btu/hr per linear foot) | Conventional Efficiency Under-Fired Broiler | conventional underfired broiler | unit |  | TRM Version 7.0 | 2022-11-30 | 3515 | 0 | 0 | 0 | 0 | 0 | 2948 | 0 | 12 | Direct Install | 0.2 | 1 | 1
COM-UB-FS-334-02 | Current |  | Commercial | Under-Fired Broilers |  | New Construction/Natural Replacement | food service | High Efficiency Under-Fired Broilers - 5 foot | low idle energy rate (≤22,000 Btu/hr per linear foot) | Conventional Efficiency Under-Fired Broiler | conventional underfired broiler | unit |  | TRM Version 7.0 | 2022-11-30 | 4393 | 0 | 0 | 0 | 0 | 0 | 3820 | 0 | 12 | Direct Install | 0.2 | 1 | 1
COM-UB-FS-335-02 | Current |  | Commercial | Under-Fired Broilers |  | New Construction/Natural Replacement | food service | High Efficiency Under-Fired Broilers - 6 foot | low idle energy rate (≤22,000 Btu/hr per linear foot) | Conventional Efficiency Under-Fired Broiler | conventional underfired broiler | unit |  | TRM Version 7.0 | 2022-11-30 | 5272 | 0 | 0 | 0 | 0 | 0 | 4134 | 0 | 12 | Direct Install | 0.2 | 1 | 1
COM-UB-FS-336-02 | Current |  | Commercial | Under-Fired Broilers |  | New Construction/Natural Replacement | food service | High Efficiency Under-Fired Broilers - 2 foot | low idle energy rate (≤22,000 Btu/hr per linear foot) | Conventional Efficiency Under-Fired Broiler | conventional underfired broiler | unit |  | TRM Version 7.0 | 2022-11-30 | 1757 | 0 | 0 | 0 | 0 | 0 | 1264 | 0 | 12 | Direct Install | 0.2 | 1 | 1
COM-DW-WH-555-03 | Current | revised from TRM Version 5.0: natural gas, electric savings, and water savings | Commercial | Dishwasher |  | New Construction/Natural Replacement | water heating | Energy Star Dishwasher | Multi Tank Conveyor - High Temperature | Non-Energy Star Dishwasher |  | unit |  | TRM Version 7.0 | 2022-11-30 | 2970 | 0 | 14386 | 0 | 437533 | 0 | 1216 | 0 | 20 | Direct Install | 0.27 | 1 | 1
COM-DW-WH-556-03 | Current | revised from TRM Version 5.0: natural gas, electric savings, and water savings | Commercial | Dishwasher |  | New Construction/Natural Replacement | water heating | Energy Star Dishwasher | Multi Tank Conveyor - Low Temperature | Non-Energy Star Dishwasher |  | unit |  | TRM Version 7.0 | 2022-11-30 | 3447 | 0 | 3375 | 0 | 507851 | 0 | 1216 | 0 | 20 | Direct Install | 0.27 | 1 | 1
COM-DW-WH-553-03 | Current | revised from TRM Version 5.0: natural gas, electric savings, and water savings | Commercial | Dishwasher |  | New Construction/Natural Replacement | water heating | Energy Star Dishwasher | Single Tank Conveyor – High Temperature | Non-Energy Star Dishwasher |  | unit |  | TRM Version 7.0 | 2022-11-30 | 1167 | 0 | 7599 | 0 | 171888 | 0 | 2570 | 0 | 20 | Direct Install | 0.27 | 1 | 1
COM-DW-WH-554-03 | Current | revised from TRM Version 5.0: natural gas, electric savings, and water savings | Commercial | Dishwasher |  | New Construction/Natural Replacement | water heating | Energy Star Dishwasher | Single Tank Conveyor - Low Temperature | Non-Energy Star Dishwasher |  | unit |  | TRM Version 7.0 | 2022-11-30 | 2546 | 0 | 3474 | 0 | 375028 | 0 | 0 | 0 | 20 | Direct Install | 0.27 | 1 | 1
COM-CNO-FS-805-03 | Current | New measure in TRM V7.0 | Commercial | Conveyor Oven |  | New Construction/Natural Replacement | food service | Energy-Efficient Conveyor Oven, small < 1520 sq in | Small Conveyor Oven Chamber Area <1520 sq in, 37% cooking efficiency | Conventional Conveyor Oven |  | unit |  | TRM Version 7.0 | 2022-11-30 | 562 | 0 | 619 | 0 | 0 | 0 | 859 | 0 | 12 | Direct Install | 0.2 | 1 | 1
COM-DW-WH-551-03 | Current | revised from TRM Version 5.0: natural gas, electric savings, and water savings | Commercial | Dishwasher |  | New Construction/Natural Replacement | water heating | Energy Star Dishwasher | Stationary Single Tank Door – High Temperature | Non-Energy Star Dishwasher |  | unit |  | TRM Version 7.0 | 2022-11-30 | 1262 | 0 | 6032 | 0 | 185951 | 0 | 1247 | 0 | 15 | Direct Install | 0.2 | 1 | 1
COM-DW-WH-552-03 | Current | revised from TRM Version 5.0: natural gas, electric savings, and water savings | Commercial | Dishwasher |  | New Construction/Natural Replacement | water heating | Energy Star Dishwasher | Stationary Single Tank Door – Low Temperature | Non-Energy Star Dishwasher |  | unit |  | TRM Version 7.0 | 2022-11-30 | 2846 | 0 | 946 | 0 | 419302 | 0 | 830 | 0 | 15 | Direct Install | 0.2 | 1 | 1
COM-DW-WH-549-03 | Current | revised from TRM Version 5.0: natural gas, electric savings, and water savings | Commercial | Dishwasher |  | New Construction/Natural Replacement | water heating | Energy Star Dishwasher | Undercounter – High Temperature | Non-Energy Star Dishwasher |  | unit |  | TRM Version 7.0 | 2022-11-30 | 285 | 0 | 2767 | 0 | 41995 | 0 | 2538 | 0 | 10 | Direct Install | 0.4 | 1 | 1
COM-DW-WH-550-03 | Current | revised from TRM Version 5.0: natural gas, electric savings, and water savings | Commercial | Dishwasher |  | New Construction/Natural Replacement | water heating | Energy Star Dishwasher | Undercounter – Low Temperature | Non-Energy Star Dishwasher |  | unit |  | TRM Version 7.0 | 2022-11-30 | 438 | 0 | 1405 | 0 | 64458 | 0 | 293 | 0 | 10 | Direct Install | 0.4 | 1 | 1
COM-DK-SH-527-03 | Current | Updated savings values | Commercial | Demand Control Kitchen Ventilation |  | Retrofit | space heating | Demand Control Kitchen Ventilation | 0 - 5,000 CFM | Constant Volume Kitchen Ventilation |  | unit |  | TRM Version 8.0 | 2024-04-30 | 4307 | 0 | 15865 | 0 | 0 | 0 | 10980 | 0 | 15 | Direct Install | 0.05 | 1 | 1
COM-DK-SH-528-03 | Current | Updated savings values | Commercial | Demand Control Kitchen Ventilation |  | Retrofit | space heating | Demand Control Kitchen Ventilation | 10,001 - 15,000 CFM | Constant Volume Kitchen Ventilation |  | unit |  | TRM Version 8.0 | 2024-04-30 | 17947 | 0 | 29586 | 0 | 0 | 0 | 45750 | 0 | 15 | Direct Install | 0.05 | 1 | 1
COM-DK-SH-529-03 | Current | Updated savings values | Commercial | Demand Control Kitchen Ventilation |  | Retrofit | space heating | Demand Control Kitchen Ventilation | 5,001 - 10,000 CFM | Constant Volume Kitchen Ventilation |  | unit |  | TRM Version 8.0 | 2024-04-30 | 10768 | 0 | 22364 | 0 | 0 | 0 | 27450 | 0 | 15 | Direct Install | 0.05 | 1 | 1
COM-DK-SH-524-03 | Current | Updated savings values | Commercial | Demand Control Kitchen Ventilation |  | New Construction/Natural Replacement | space heating | Demand Control Kitchen Ventilation | 0 - 5,000 CFM | Constant Volume Kitchen Ventilation |  | unit |  | TRM Version 8.0 | 2024-04-30 | 4307 | 0 | 15865 | 0 | 0 | 0 | 5490 | 0 | 15 | Direct Install | 0.05 | 1 | 1
COM-DK-SH-526-03 | Current | Updated savings values | Commercial | Demand Control Kitchen Ventilation |  | New Construction/Natural Replacement | space heating | Demand Control Kitchen Ventilation | 10,001 - 15,000 CFM | Constant Volume Kitchen Ventilation |  | unit |  | TRM Version 8.0 | 2024-04-30 | 17947 | 0 | 29586 | 0 | 0 | 0 | 22875 | 0 | 15 | Direct Install | 0.05 | 1 | 1
COM-DK-SH-525-03 | Current | Updated savings values | Commercial | Demand Control Kitchen Ventilation |  | New Construction/Natural Replacement | space heating | Demand Control Kitchen Ventilation | 5,001 - 10,000 CFM | Constant Volume Kitchen Ventilation |  | unit |  | TRM Version 8.0 | 2024-04-30 | 10768 | 0 | 22364 | 0 | 0 | 0 | 13725 | 0 | 15 | Direct Install | 0.05 | 1 | 1
COM-CU-SH-515-02 | Current | Updated size descriptions in eTRM to match TRM, entered energy savings that appear to be new from last TRM | Commercial | Condensing Unit Heater |  | Natural Replacement | space heating | Condensing Unit Heater | 125-225 kBtu/hr 90% Thermal Efficiency, 89% Annual Efficiency | Non-Condensing Unit Heater | 80% Thermal Efficiency, 78% Annual Efficiency |  | kBtu/hr input capacity | TRM Version 8.0 | 2024-04-30 | 0 | 6.52 | -438 | 0 | 0 | 0 | 0 | 16.07 | 18 | Direct Install | 0 | 1 | 1
COM-CU-SH-516-02 | Current | Entered energy savings that appear to be new from last TRM | Commercial | Condensing Unit Heater |  | Natural Replacement | space heating | Condensing Unit Heater | 225-300 kBtu/hr 90% Thermal Efficiency, 89% Annual Efficiency | Non-Condensing Unit Heater | 80% Thermal Efficiency, 78% Annual Efficiency |  | kBtu/hr input capacity | TRM Version 8.0 | 2024-04-30 | 0 | 6.52 | -451 | 0 | 0 | 0 | 0 | 16.07 | 18 | Direct Install | 0 | 1 | 1
COM-CU-SH-514-02 | Current | Updated size descriptions in eTRM to match TRM, entered energy savings that appear to be new from last TRM | Commercial | Condensing Unit Heater |  | Natural Replacement | space heating | Condensing Unit Heater | 30-125 kBtu/hr - 90% Thermal Efficiency, 89% Annual Efficiency | Non-Condensing Unit Heater | 80% Thermal Efficiency, 78% Annual Efficiency |  | kBtu/hr input capacity | TRM Version 8.0 | 2024-04-30 | 0 | 6.52 | -244 | 0 | 0 | 0 | 0 | 16.07 | 18 | Direct Install | 0 | 1 | 1
COM-CU-SH-518-02 | Current | Updated size descriptions in eTRM to match TRM, entered energy savings that appear to be new from last TRM | Commercial | Condensing Unit Heater |  | New Construction | space heating | Condensing Unit Heater | 125-225 kBtu/hr 90% Thermal Efficiency, 89% Annual Efficiency | Non-Condensing Unit Heater | 80% Thermal Efficiency, 78% Annual Efficiency |  | kBtu/hr input capacity | TRM Version 8.0 | 2024-04-30 | 0 | 4.62 | -310 | 0 | 0 | 0 | 0 | 16.07 | 18 | Direct Install | 0 | 1 | 1
COM-CU-SH-519-02 | Current | Entered energy savings that appear to be new from last TRM | Commercial | Condensing Unit Heater |  | New Construction | space heating | Condensing Unit Heater | 225-300 kBtu/hr 90% Thermal Efficiency, 89% Annual Efficiency | Non-Condensing Unit Heater | 80% Thermal Efficiency, 78% Annual Efficiency |  | kBtu/hr input capacity | TRM Version 8.0 | 2024-04-30 | 0 | 4.62 | -320 | 0 | 0 | 0 | 0 | 16.07 | 18 | Direct Install | 0 | 1 | 1
COM-CU-SH-517-02 | Current | Updated size descriptions in eTRM to match TRM, entered energy savings that appear to be new from last TRM | Commercial | Condensing Unit Heater |  | New Construction | space heating | Condensing Unit Heater | 30-125 kBtu/hr - 90% Thermal Efficiency, 89% Annual Efficiency | Non-Condensing Unit Heater | 80% Thermal Efficiency, 78% Annual Efficiency |  | kBtu/hr input capacity | TRM Version 8.0 | 2024-04-30 | 0 | 4.62 | -173 | 0 | 0 | 0 | 0 | 16.07 | 18 | Direct Install | 0 | 1 | 1
COM-CT-WH-533-05 | Current | Updated size descriptions in eTRM to match TRM. Split New Construction and Natural Replacement to effectively represent baseline. Updated technology descriptions. Updated energy savings. | Commercial | Condensing Tankless Water Heater | High Utilization | Natural Replacement | water heating | Condensing Tankless Water Heater - High Utilization | <200 kBtu/hr UEF >= 0.90 Stand-by Loss = negligible | Non-Condensing Storage Water Heater | Storage Water Heater 75 kBtu/hr. and greater Uniform Energy Factor (UEF)=0.6597-0.00024Vs | unit | kBtu/hr input capacity | TRM Version 8.0 | 2024-04-30 | 212 | 4.349 | 0 | 0 | 0 | 0 | 3030 | 0 | 20 | Direct Install | 0.02 | 1 | 1
COM-CT-WH-533-06 | Current | Split New Construction and Natural Replacement to effectively represent baseline. Updated technology descriptions. Updated energy savings. | Commercial | Condensing Tankless Water Heater | High Utilization | Natural Replacement | water heating | Condensing Tankless Water Heater - High Utilization | >=200 kBtu/hr Thermal efficiency >= 94% Stand-by Loss = negligible | Non-Condensing Storage Water Heater | Storage Water Heater 75 kBtu/hr. and greater Thermal efficiency = 80% Stand-by Loss Q/800 +110√V0 Btu/hr | unit | kBtu/hr input capacity | TRM Version 8.0 | 2024-04-30 | 351 | 1.954 | 0 | 0 | 0 | 0 | 3030 | 0 | 20 | Direct Install | 0.02 | 1 | 1
COM-CT-WH-533-07 | Current | Updated size descriptions in eTRM to match TRM. Split New Construction and Natural Replacement to effectively represent baseline. Updated technology descriptions. Updated energy savings. | Commercial | Condensing Tankless Water Heater | High Utilization | Natural Replacement | water heating | Condensing Tankless Water Heater - High Utilization | <200 kBtu/hr UEF >= 0.95 Stand-by Loss = negligible | Non-Condensing Storage Water Heater | Storage Water Heater 75 kBtu/hr. and greater Uniform Energy Factor (UEF)=0.6597-0.00024Vs | unit | kBtu/hr input capacity | TRM Version 8.0 | 2024-04-30 | 212 | 5.211 | 0 | 0 | 0 | 0 | 3030 | 0 | 20 | Direct Install | 0.02 | 1 | 1
COM-CT-WH-533-08 | Current | Split New Construction and Natural Replacement to effectively represent baseline. Updated technology descriptions. Updated energy savings. | Commercial | Condensing Tankless Water Heater | High Utilization | Natural Replacement | water heating | Condensing Tankless Water Heater - High Utilization | >=200 kBtu/hr Thermal efficiency >= 96% Stand-by Loss = negligible | Non-Condensing Storage Water Heater | Storage Water Heater 75 kBtu/hr. and greater Thermal efficiency = 80% Stand-by Loss Q/800 +110√V0 Btu/hr | unit | kBtu/hr input capacity | TRM Version 8.0 | 2024-04-30 | 521 | 2.233 | 0 | 0 | 0 | 0 | 3030 | 0 | 20 | Direct Install | 0.02 | 1 | 1
COM-CT-WH-533-09 | Current | Split New Construction and Natural Replacement to effectively represent baseline. Updated technology descriptions. Updated energy savings. | Commercial | Condensing Tankless Water Heater | High Utilization | Natural Replacement | water heating | Condensing Tankless Water Heater - High Utilization | >=200 kBtu/hr Thermal efficiency >= 98% Stand-by Loss = negligible | Non-Condensing Storage Water Heater | Storage Water Heater 75 kBtu/hr. and greater Thermal efficiency = 80% Stand-by Loss Q/800 +110√V0 Btu/hr | unit | kBtu/hr input capacity | TRM Version 8.0 | 2024-04-30 | 867 | 2.512 | 0 | 0 | 0 | 0 | 3030 | 0 | 20 | Direct Install | 0.02 | 1 | 1
COM-CT-WH-534-04 | Current | Updated size descriptions in eTRM to match TRM. Split New Construction and Natural Replacement to effectively represent baseline. Updated technology descriptions. Updated energy savings. | Commercial | Condensing Tankless Water Heater | High Utilization | New Construction | water heating | Condensing Tankless Water Heater - High Utilization | <200 kBtu/hr UEF >= 0.95 Stand-by Loss = negligible | Non-Condensing Storage Water Heater | Storage Water Heater 75 kBtu/hr. and greater Uniform Energy Factor (UEF)=0.8107-0.00021Vs | unit | kBtu/hr input capacity | TRM Version 8.0 | 2024-04-30 | 178 | 2.09 | 0 | 0 | 0 | 0 | 1030 | 0 | 20 | Direct Install | 0.02 | 1 | 1
COM-CT-WH-534-05 | Current | Split New Construction and Natural Replacement to effectively represent baseline. Updated technology descriptions. Updated energy savings. | Commercial | Condensing Tankless Water Heater | High Utilization | New Construction | water heating | Condensing Tankless Water Heater - High Utilization | >=200 kBtu/hr Thermal efficiency >= 96% Stand-by Loss = negligible | Non-Condensing Storage Water Heater | Storage Water Heater 75 kBtu/hr. and greater Thermal efficiency = 90% Stand-by Loss 0.84(Q/800 +110√V0)Btu/hr | unit | kBtu/hr input capacity | TRM Version 8.0 | 2024-04-30 | 295 | 0.744 | 0 | 0 | 0 | 0 | 1030 | 0 | 20 | Direct Install | 0.02 | 1 | 1
COM-CT-WH-534-06 | Current | Split New Construction and Natural Replacement to effectively represent baseline. Updated technology descriptions. Updated energy savings. | Commercial | Condensing Tankless Water Heater | High Utilization | New Construction | water heating | Condensing Tankless Water Heater - High Utilization | >=1000 < 2500 kBtu/hr Thermal efficiency >= 98% Stand-by Loss = negligible | Non-Condensing Storage Water Heater | Storage Water Heater 75 kBtu/hr. and greater Thermal efficiency = 80% Stand-by Loss Q/800 +110√V0 Btu/hr | unit | kBtu/hr input capacity | TRM Version 8.0 | 2024-04-30 | 438 | 0.992 | 0 | 0 | 0 | 0 | 1030 | 0 | 20 | Direct Install | 0.02 | 1 | 1
COM-CT-WH-534-07 | Current | Split New Construction and Natural Replacement to effectively represent baseline. Updated technology descriptions. Updated energy savings. | Commercial | Condensing Tankless Water Heater | High Utilization | New Construction | water heating | Condensing Tankless Water Heater - High Utilization | >=2500 kBtu/hr Thermal efficiency >= 98% Stand-by Loss = negligible | Non-Condensing Storage Water Heater | Storage Water Heater 75 kBtu/hr. and greater Thermal efficiency = 80% Stand-by Loss Q/800 +110√V0 Btu/hr | unit | kBtu/hr input capacity | TRM Version 8.0 | 2024-04-30 | 728 | 0.992 | 0 | 0 | 0 | 0 | 1030 | 0 | 20 | Direct Install | 0.02 | 1 | 1
COM-CT-WH-535-05 | Current | Updated size descriptions in eTRM to match TRM. Split New Construction and Natural Replacement to effectively represent baseline. Updated technology descriptions. Updated energy savings. | Commercial | Condensing Tankless Water Heater | Low Utilization | Natural Replacement | water heating | Condensing Tankless Water Heater - Low Utilization | <200 kBtu/hr UEF >= 0.90 Stand-by Loss = negligible | Non-Condensing Storage Water Heater | Storage Water Heater 75 kBtu/hr. and greater Uniform Energy Factor (UEF)=0.6597-0.00024Vs | unit | kBtu/hr input capacity | TRM Version 8.0 | 2024-04-30 | 212 | 1.918 | 0 | 0 | 0 | 0 | 3030 | 0 | 20 | Direct Install | 0.02 | 1 | 1
COM-CT-WH-535-06 | Current | Split New Construction and Natural Replacement to effectively represent baseline. Updated technology descriptions. Updated energy savings. | Commercial | Condensing Tankless Water Heater | Low Utilization | Natural Replacement | water heating | Condensing Tankless Water Heater - Low Utilization | >=200 kBtu/hr Thermal efficiency >= 94% Stand-by Loss = negligible | Non-Condensing Storage Water Heater | Storage Water Heater 75 kBtu/hr. and greater Thermal efficiency = 80% Stand-by Loss Q/800 +110√V0 Btu/hr | unit | kBtu/hr input capacity | TRM Version 8.0 | 2024-04-30 | 351 | 0.862 | 0 | 0 | 0 | 0 | 3030 | 0 | 20 | Direct Install | 0.02 | 1 | 1
COM-CT-WH-535-07 | Current | Updated size descriptions in eTRM to match TRM. Split New Construction and Natural Replacement to effectively represent baseline. Updated technology descriptions. Updated energy savings. | Commercial | Condensing Tankless Water Heater | Low Utilization | Natural Replacement | water heating | Condensing Tankless Water Heater - Low Utilization | <200 kBtu/hr UEF >= 0.95 Stand-by Loss = negligible | Non-Condensing Storage Water Heater | Storage Water Heater 75 kBtu/hr. and greater Uniform Energy Factor (UEF)=0.6597-0.00024Vs | unit | kBtu/hr input capacity | TRM Version 8.0 | 2024-04-30 | 212 | 2.299 | 0 | 0 | 0 | 0 | 3030 | 0 | 20 | Direct Install | 0.02 | 1 | 1
COM-CT-WH-535-08 | Current | Split New Construction and Natural Replacement to effectively represent baseline. Updated technology descriptions. Updated energy savings. | Commercial | Condensing Tankless Water Heater | Low Utilization | Natural Replacement | water heating | Condensing Tankless Water Heater - Low Utilization | >=200 kBtu/hr Thermal efficiency >= 96% Stand-by Loss = negligible | Non-Condensing Storage Water Heater | Storage Water Heater 75 kBtu/hr. and greater Thermal efficiency = 80% Stand-by Loss Q/800 +110√V0 Btu/hr | unit | kBtu/hr input capacity | TRM Version 8.0 | 2024-04-30 | 521 | 0.985 | 0 | 0 | 0 | 0 | 3030 | 0 | 20 | Direct Install | 0.02 | 1 | 1
COM-CT-WH-535-09 | Current | Split New Construction and Natural Replacement to effectively represent baseline. Updated technology descriptions. Updated energy savings. | Commercial | Condensing Tankless Water Heater | Low Utilization | Natural Replacement | water heating | Condensing Tankless Water Heater - Low Utilization | >=200 kBtu/hr Thermal efficiency >= 98% Stand-by Loss = negligible | Non-Condensing Storage Water Heater | Storage Water Heater 75 kBtu/hr. and greater Thermal efficiency = 80% Stand-by Loss Q/800 +110√V0 Btu/hr | unit | kBtu/hr input capacity | TRM Version 8.0 | 2024-04-30 | 867 | 1.108 | 0 | 0 | 0 | 0 | 3030 | 0 | 20 | Direct Install | 0.02 | 1 | 1
COM-CT-WH-536-04 | Current | Updated size descriptions in eTRM to match TRM. Split New Construction and Natural Replacement to effectively represent baseline. Updated technology descriptions. Updated energy savings. | Commercial | Condensing Tankless Water Heater | Low Utilization | New Construction | water heating | Condensing Tankless Water Heater - Low Utilization | <200 kBtu/hr UEF >= 0.95 Stand-by Loss = negligible | Non-Condensing Storage Water Heater | Storage Water Heater 75 kBtu/hr. and greater Uniform Energy Factor (UEF)=0.8107-0.00021Vs | unit | kBtu/hr input capacity | TRM Version 8.0 | 2024-04-30 | 178 | 0.922 | 0 | 0 | 0 | 0 | 1030 | 0 | 20 | Direct Install | 0.02 | 1 | 1
COM-CT-WH-536-05 | Current | Split New Construction and Natural Replacement to effectively represent baseline. Updated technology descriptions. Updated energy savings. | Commercial | Condensing Tankless Water Heater | Low Utilization | New Construction | water heating | Condensing Tankless Water Heater - Low Utilization | >=200 kBtu/hr Thermal efficiency >= 96% Stand-by Loss = negligible | Non-Condensing Storage Water Heater | Storage Water Heater 75 kBtu/hr. and greater Thermal efficiency = 90% Stand-by Loss 0.84(Q/800 +110√V0)Btu/hr | unit | kBtu/hr input capacity | TRM Version 8.0 | 2024-04-30 | 295 | 0.328 | 0 | 0 | 0 | 0 | 1030 | 0 | 20 | Direct Install | 0.02 | 1 | 1
COM-CT-WH-536-06 | Current | Split New Construction and Natural Replacement to effectively represent baseline. Updated technology descriptions. Updated energy savings. | Commercial | Condensing Tankless Water Heater | Low Utilization | New Construction | water heating | Condensing Tankless Water Heater - Low Utilization | >=1000 < 2500 kBtu/hr Thermal efficiency >= 98% Stand-by Loss = negligible | Non-Condensing Storage Water Heater | Storage Water Heater 75 kBtu/hr. and greater Thermal efficiency = 80% Stand-by Loss Q/800 +110√V0 Btu/hr | unit | kBtu/hr input capacity | TRM Version 8.0 | 2024-04-30 | 438 | 0.438 | 0 | 0 | 0 | 0 | 1030 | 0 | 20 | Direct Install | 0.02 | 1 | 1
COM-CT-WH-536-07 | Current | Split New Construction and Natural Replacement to effectively represent baseline. Updated technology descriptions. Updated energy savings. | Commercial | Condensing Tankless Water Heater | Low Utilization | New Construction | water heating | Condensing Tankless Water Heater - Low Utilization | >=2500 kBtu/hr Thermal efficiency >= 98% Stand-by Loss = negligible | Non-Condensing Storage Water Heater | Storage Water Heater 75 kBtu/hr. and greater Thermal efficiency = 80% Stand-by Loss Q/800 +110√V0 Btu/hr | unit | kBtu/hr input capacity | TRM Version 8.0 | 2024-04-30 | 728 | 0.438 | 0 | 0 | 0 | 0 | 1030 | 0 | 20 | Direct Install | 0.02 | 1 | 1
COM-CT-WH-537-05 | Current | Updated size descriptions in eTRM to match TRM. Split New Construction and Natural Replacement to effectively represent baseline. Updated technology descriptions. Updated energy savings. | Commercial | Condensing Tankless Water Heater | Medium Utilization | Natural Replacement | water heating | Condensing Tankless Water Heater - Medium Utilization | <200 kBtu/hr UEF >= 0.90 Stand-by Loss = negligible | Non-Condensing Storage Water Heater | Storage Water Heater 75 kBtu/hr. and greater Uniform Energy Factor (UEF)=0.6597-0.00024Vs | unit | kBtu/hr input capacity | TRM Version 8.0 | 2024-04-30 | 212 | 3.128 | 0 | 0 | 0 | 0 | 3030 | 0 | 20 | Direct Install | 0.02 | 1 | 1
COM-CT-WH-537-06 | Current | Split New Construction and Natural Replacement to effectively represent baseline. Updated technology descriptions. Updated energy savings. | Commercial | Condensing Tankless Water Heater | Medium Utilization | Natural Replacement | water heating | Condensing Tankless Water Heater - Medium Utilization | >=200 kBtu/hr Thermal efficiency >= 94% Stand-by Loss = negligible | Non-Condensing Storage Water Heater | Storage Water Heater 75 kBtu/hr. and greater Thermal efficiency = 80% Stand-by Loss Q/800 +110√V0 Btu/hr | unit | kBtu/hr input capacity | TRM Version 8.0 | 2024-04-30 | 351 | 1.405 | 0 | 0 | 0 | 0 | 3030 | 0 | 20 | Direct Install | 0.02 | 1 | 1
COM-CT-WH-537-07 | Current | Updated size descriptions in eTRM to match TRM. Split New Construction and Natural Replacement to effectively represent baseline. Updated technology descriptions. Updated energy savings. | Commercial | Condensing Tankless Water Heater | Medium Utilization | Natural Replacement | water heating | Condensing Tankless Water Heater - Medium Utilization | <200 kBtu/hr UEF >= 0.95 Stand-by Loss = negligible | Non-Condensing Storage Water Heater | Storage Water Heater 75 kBtu/hr. and greater Uniform Energy Factor (UEF)=0.6597-0.00024Vs | unit | kBtu/hr input capacity | TRM Version 8.0 | 2024-04-30 | 212 | 3.748 | 0 | 0 | 0 | 0 | 3030 | 0 | 20 | Direct Install | 0.02 | 1 | 1
COM-CT-WH-537-08 | Current | Split New Construction and Natural Replacement to effectively represent baseline. Updated technology descriptions. Updated energy savings. | Commercial | Condensing Tankless Water Heater | Medium Utilization | Natural Replacement | water heating | Condensing Tankless Water Heater - Medium Utilization | >=200 kBtu/hr Thermal efficiency >= 96% Stand-by Loss = negligible | Non-Condensing Storage Water Heater | Storage Water Heater 75 kBtu/hr. and greater Thermal efficiency = 80% Stand-by Loss Q/800 +110√V0 Btu/hr | unit | kBtu/hr input capacity | TRM Version 8.0 | 2024-04-30 | 521 | 1.606 | 0 | 0 | 0 | 0 | 3030 | 0 | 20 | Direct Install | 0.02 | 1 | 1
COM-CT-WH-537-09 | Current | Split New Construction and Natural Replacement to effectively represent baseline. Updated technology descriptions. Updated energy savings. | Commercial | Condensing Tankless Water Heater | Medium Utilization | Natural Replacement | water heating | Condensing Tankless Water Heater - Medium Utilization | >=200 kBtu/hr Thermal efficiency >= 98% Stand-by Loss = negligible | Non-Condensing Storage Water Heater | Storage Water Heater 75 kBtu/hr. and greater Thermal efficiency = 80% Stand-by Loss Q/800 +110√V0 Btu/hr | unit | kBtu/hr input capacity | TRM Version 8.0 | 2024-04-30 | 867 | 1.807 | 0 | 0 | 0 | 0 | 3030 | 0 | 20 | Direct Install | 0.02 | 1 | 1
COM-CT-WH-538-04 | Current | Updated size descriptions in eTRM to match TRM. Split New Construction and Natural Replacement to effectively represent baseline. Updated technology descriptions. Updated energy savings. | Commercial | Condensing Tankless Water Heater | Medium Utilization | New Construction | water heating | Condensing Tankless Water Heater - Medium Utilization | <200 kBtu/hr UEF >= 0.95 Stand-by Loss = negligible | Non-Condensing Storage Water Heater | Storage Water Heater 75 kBtu/hr. and greater Uniform Energy Factor (UEF)=0.8107-0.00021Vs | unit | kBtu/hr input capacity | TRM Version 8.0 | 2024-04-30 | 178 | 1.503 | 0 | 0 | 0 | 0 | 1030 | 0 | 20 | Direct Install | 0.02 | 1 | 1
COM-CT-WH-538-05 | Current | Split New Construction and Natural Replacement to effectively represent baseline. Updated technology descriptions. Updated energy savings. | Commercial | Condensing Tankless Water Heater | Medium Utilization | New Construction | water heating | Condensing Tankless Water Heater - Medium Utilization | >=200 kBtu/hr Thermal efficiency >= 96% Stand-by Loss = negligible | Non-Condensing Storage Water Heater | Storage Water Heater 75 kBtu/hr. and greater Thermal efficiency = 90% Stand-by Loss 0.84(Q/800 +110√V0)Btu/hr | unit | kBtu/hr input capacity | TRM Version 8.0 | 2024-04-30 | 295 | 0.535 | 0 | 0 | 0 | 0 | 1030 | 0 | 20 | Direct Install | 0.02 | 1 | 1
COM-CT-WH-538-06 | Current | Split New Construction and Natural Replacement to effectively represent baseline. Updated technology descriptions. Updated energy savings. | Commercial | Condensing Tankless Water Heater | Medium Utilization | New Construction | water heating | Condensing Tankless Water Heater - Medium Utilization | >=1000 < 2500 kBtu/hr Thermal efficiency >= 98% Stand-by Loss = negligible | Non-Condensing Storage Water Heater | Storage Water Heater 75 kBtu/hr. and greater Thermal efficiency = 80% Stand-by Loss Q/800 +110√V0 Btu/hr | unit | kBtu/hr input capacity | TRM Version 8.0 | 2024-04-30 | 438 | 0.714 | 0 | 0 | 0 | 0 | 1030 | 0 | 20 | Direct Install | 0.02 | 1 | 1
COM-CT-WH-538-07 | Current | Split New Construction and Natural Replacement to effectively represent baseline. Updated technology descriptions. Updated energy savings. | Commercial | Condensing Tankless Water Heater | Medium Utilization | New Construction | water heating | Condensing Tankless Water Heater - Medium Utilization | >=2500 kBtu/hr Thermal efficiency >= 98% Stand-by Loss = negligible | Non-Condensing Storage Water Heater | Storage Water Heater 75 kBtu/hr. and greater Thermal efficiency = 80% Stand-by Loss Q/800 +110√V0 Btu/hr | unit | kBtu/hr input capacity | TRM Version 8.0 | 2024-04-30 | 728 | 0.714 | 0 | 0 | 0 | 0 | 1030 | 0 | 20 | Direct Install | 0.02 | 1 | 1
COM-CS-WH-527-08 | Current | Split New Construction and Natural Replacement to effectively represent baseline and efficient efficiencies. Updated savings. | Commercial | Condensing Storage Water Heater | High Utilization | Natural Replacement | water heating | Condensing storage water heater | > 75 kBTU/hr and <= 105 kBTU/hr, rated nominal volume <= 120 US gallon, single-phase power, water temp <180 deg f, UEF >= 0.86 < 0.89 | Non-condensing storage water heater | > 75 kBTU/hr and <= 105 kBTU/hr, rated nominal volume <= 120 US gallon, single-phase power, water temp <180 deg f, UEF = 0.6597 - 0.00024Vs |  | kBtu/hr input capacity | TRM Version 8.0 | 2024-04-30 | 0 | 5.699 | 0 | 0 | 0 | 0 | 2591 | 0 | 15 | Direct Install | 0.05 | 1 | 1
COM-CS-WH-527-09 | Current | Split New Construction and Natural Replacement to effectively represent baseline and efficient efficiencies. Updated savings. | Commercial | Condensing Storage Water Heater | High Utilization | Natural Replacement | water heating | Condensing storage water heater | > 75 kBTU/hr and <= 105 kBTU/hr, rated nominal volume <= 120 US gallon, single-phase power, water temp <180 deg f, UEF >= 0.89 | Non-condensing storage water heater | > 75 kBTU/hr and <= 105 kBTU/hr, rated nominal volume <= 120 US gallon, single-phase power, water temp <180 deg f, UEF = 0.6597 - 0.00024Vs |  | kBtu/hr input capacity | TRM Version 8.0 | 2024-04-30 | 0 | 6.497 | 0 | 0 | 0 | 0 | 2591 | 0 | 15 | Direct Install | 0.05 | 1 | 1
COM-CS-WH-527-10 | Current | Split New Construction and Natural Replacement to effectively represent baseline and efficient efficiencies. Updated savings. | Commercial | Condensing Storage Water Heater | High Utilization | Natural Replacement | water heating | Condensing storage water heater | All water heaters not described by UEF baseline definition with thermal efficiency >= 92% < 95%, <= 250 kBTU/hr | Non-condensing storage water heater | All water heaters not described by UEF baseline definition with thermal efficiency >= 80% |  | kBtu/hr input capacity | TRM Version 8.0 | 2024-04-30 | 0 | 2.577 | 0 | 0 | 0 | 0 | 2591 | 0 | 15 | Direct Install | 0.05 | 1 | 1
COM-CS-WH-527-11 | Current | Split New Construction and Natural Replacement to effectively represent baseline and efficient efficiencies. Updated savings. | Commercial | Condensing Storage Water Heater | High Utilization | Natural Replacement | water heating | Condensing storage water heater | All water heaters not described by UEF baseline definition with thermal efficiency >= 95% < 97%, <= 250 kBTU/hr | Non-condensing storage water heater | All water heaters not described by UEF baseline definition with thermal efficiency >= 80% |  | kBtu/hr input capacity | TRM Version 8.0 | 2024-04-30 | 0 | 3.221 | 0 | 0 | 0 | 0 | 2591 | 0 | 15 | Direct Install | 0.05 | 1 | 1
COM-CS-WH-527-12 | Current | Split New Construction and Natural Replacement to effectively represent baseline and efficient efficiencies. Updated savings. | Commercial | Condensing Storage Water Heater | High Utilization | Natural Replacement | water heating | Condensing storage water heater | All water heaters not described by UEF baseline definition with thermal efficiency >= 97%, <= 250 kBTU/hr | Non-condensing storage water heater | All water heaters not described by UEF baseline definition with thermal efficiency >= 80% |  | kBtu/hr input capacity | TRM Version 8.0 | 2024-04-30 | 0 | 3.651 | 0 | 0 | 0 | 0 | 2591 | 0 | 15 | Direct Install | 0.05 | 1 | 1
COM-CS-WH-527-13 | Current | Split New Construction and Natural Replacement to effectively represent baseline and efficient efficiencies. Updated savings. | Commercial | Condensing Storage Water Heater | High Utilization | Natural Replacement | water heating | Condensing storage water heater | All water heaters not described by UEF baseline definition with thermal efficiency >= 92% < 95%, > 250 kBTU/hr | Non-condensing storage water heater | All water heaters not described by UEF baseline definition with thermal efficiency >= 80% |  | kBtu/hr input capacity | TRM Version 8.0 | 2024-04-30 | 0 | 2.577 | 0 | 0 | 0 | 0 | 4464 | 0 | 15 | Direct Install | 0.05 | 1 | 1
COM-CS-WH-527-14 | Current | Split New Construction and Natural Replacement to effectively represent baseline and efficient efficiencies. Updated savings. | Commercial | Condensing Storage Water Heater | High Utilization | Natural Replacement | water heating | Condensing storage water heater | All water heaters not described by UEF baseline definition with thermal efficiency >= 95% < 97%, > 250 kBTU/hr | Non-condensing storage water heater | All water heaters not described by UEF baseline definition with thermal efficiency >= 80% |  | kBtu/hr input capacity | TRM Version 8.0 | 2024-04-30 | 0 | 3.221 | 0 | 0 | 0 | 0 | 4464 | 0 | 15 | Direct Install | 0.05 | 1 | 1
COM-CS-WH-527-15 | Current | Split New Construction and Natural Replacement to effectively represent baseline and efficient efficiencies. Updated savings. | Commercial | Condensing Storage Water Heater | High Utilization | Natural Replacement | water heating | Condensing storage water heater | All water heaters not described by UEF baseline definition with thermal efficiency >= 97%, > 250 kBTU/hr | Non-condensing storage water heater | All water heaters not described by UEF baseline definition with thermal efficiency >= 80% |  | kBtu/hr input capacity | TRM Version 8.0 | 2024-04-30 | 0 | 3.651 | 0 | 0 | 0 | 0 | 4464 | 0 | 15 | Direct Install | 0.05 | 1 | 1
COM-CS-WH-528-06 | Current | Split New Construction and Natural Replacement to effectively represent baseline and efficient efficiencies. Updated savings. | Commercial | Condensing Storage Water Heater | High Utilization | New Construction | water heating | Condensing storage water heater | > 75 kBTU/hr and <= 105 kBTU/hr, rated nominal volume <= 120 US gallon, single-phase power, water temp <180 deg f, UEF >= 0.86 < 0.89 | Non-condensing storage water heater | > 75 kBTU/hr and <= 105 kBTU/hr, rated nominal volume <= 120 US gallon, single-phase power, water temp <180 deg f, UEF = 0.8107 - 0.00021Vs |  | kBtu/hr input capacity | TRM Version 8.0 | 2024-04-30 | 0 | 1.323 | 0 | 0 | 0 | 0 | 2591 | 0 | 15 | Direct Install | 0.05 | 1 | 1
COM-CS-WH-528-07 | Current | Split New Construction and Natural Replacement to effectively represent baseline and efficient efficiencies. Updated savings. | Commercial | Condensing Storage Water Heater | High Utilization | New Construction | water heating | Condensing storage water heater | > 75 kBTU/hr and <= 105 kBTU/hr, rated nominal volume <= 120 US gallon, single-phase power, water temp <180 deg f, UEF >= 0.89 | Non-condensing storage water heater | > 75 kBTU/hr and <= 105 kBTU/hr, rated nominal volume <= 120 US gallon, single-phase power, water temp <180 deg f, UEF = 0.8107 - 0.00021Vs |  | kBtu/hr input capacity | TRM Version 8.0 | 2024-04-30 | 0 | 1.968 | 0 | 0 | 0 | 0 | 2591 | 0 | 15 | Direct Install | 0.05 | 1 | 1
COM-CS-WH-528-08 | Current | Split New Construction and Natural Replacement to effectively represent baseline and efficient efficiencies. Updated savings. | Commercial | Condensing Storage Water Heater | High Utilization | New Construction | water heating | Condensing storage water heater | All water heaters not described by UEF baseline definition with thermal efficiency >= 95 < 97%, <= 250 kBTU/hr | Non-condensing storage water heater | All water heaters not described by UEF baseline definition with thermal efficiency = 90% |  | kBtu/hr input capacity | TRM Version 8.0 | 2024-04-30 | 0 | 0.954 | 0 | 0 | 0 | 0 | 2591 | 0 | 15 | Direct Install | 0.05 | 1 | 1
COM-CS-WH-528-09 | Current | Split New Construction and Natural Replacement to effectively represent baseline and efficient efficiencies. Updated savings. | Commercial | Condensing Storage Water Heater | High Utilization | New Construction | water heating | Condensing storage water heater | All water heaters not described by UEF baseline definition with thermal efficiency >= 97%, <= 250 kBTU/hr | Non-condensing storage water heater | All water heaters not described by UEF baseline definition with thermal efficiency = 90% |  | kBtu/hr input capacity | TRM Version 8.0 | 2024-04-30 | 0 | 1.336 | 0 | 0 | 0 | 0 | 2591 | 0 | 15 | Direct Install | 0.05 | 1 | 1
COM-CS-WH-528-10 | Current | Split New Construction and Natural Replacement to effectively represent baseline and efficient efficiencies. Updated savings. | Commercial | Condensing Storage Water Heater | High Utilization | New Construction | water heating | Condensing storage water heater | All water heaters not described by UEF baseline definition with thermal efficiency >= 95 < 97%, > 250 kBTU/hr | Non-condensing storage water heater | All water heaters not described by UEF baseline definition with thermal efficiency = 90% |  | kBtu/hr input capacity | TRM Version 8.0 | 2024-04-30 | 0 | 0.954 | 0 | 0 | 0 | 0 | 4464 | 0 | 15 | Direct Install | 0.05 | 1 | 1
COM-CS-WH-528-11 | Current | Split New Construction and Natural Replacement to effectively represent baseline and efficient efficiencies. Updated savings. | Commercial | Condensing Storage Water Heater | High Utilization | New Construction | water heating | Condensing storage water heater | All water heaters not described by UEF baseline definition with thermal efficiency >= 97%, > 250 kBTU/hr | Non-condensing storage water heater | All water heaters not described by UEF baseline definition with thermal efficiency = 90% |  | kBtu/hr input capacity | TRM Version 8.0 | 2024-04-30 | 0 | 1.336 | 0 | 0 | 0 | 0 | 4464 | 0 | 15 | Direct Install | 0.05 | 1 | 1
COM-CS-WH-529-08 | Current | Split New Construction and Natural Replacement to effectively represent baseline and efficient efficiencies. Updated savings. | Commercial | Condensing Storage Water Heater | Low Utilization | Natural Replacement | water heating | Condensing storage water heater | > 75 kBTU/hr and <= 105 kBTU/hr, rated nominal volume <= 120 US gallon, single-phase power, water temp <180 deg f, UEF >= 0.86 < 0.89 | Non-condensing storage water heater | > 75 kBTU/hr and <= 105 kBTU/hr, rated nominal volume <= 120 US gallon, single-phase power, water temp <180 deg f, UEF = 0.6597 - 0.00024Vs |  | kBtu/hr input capacity | TRM Version 8.0 | 2024-04-30 | 0 | 2.515 | 0 | 0 | 0 | 0 | 2591 | 0 | 15 | Direct Install | 0.05 | 1 | 1
COM-CS-WH-529-09 | Current | Split New Construction and Natural Replacement to effectively represent baseline and efficient efficiencies. Updated savings. | Commercial | Condensing Storage Water Heater | Low Utilization | Natural Replacement | water heating | Condensing storage water heater | > 75 kBTU/hr and <= 105 kBTU/hr, rated nominal volume <= 120 US gallon, single-phase power, water temp <180 deg f, UEF >= 0.89 | Non-condensing storage water heater | > 75 kBTU/hr and <= 105 kBTU/hr, rated nominal volume <= 120 US gallon, single-phase power, water temp <180 deg f, UEF = 0.6597 - 0.00024Vs |  | kBtu/hr input capacity | TRM Version 8.0 | 2024-04-30 | 0 | 2.868 | 0 | 0 | 0 | 0 | 2591 | 0 | 15 | Direct Install | 0.05 | 1 | 1
COM-CS-WH-529-10 | Current | Split New Construction and Natural Replacement to effectively represent baseline and efficient efficiencies. Updated savings. | Commercial | Condensing Storage Water Heater | Low Utilization | Natural Replacement | water heating | Condensing storage water heater | All water heaters not described by UEF baseline definition with thermal efficiency >= 92% < 95%, <= 250 kBTU/hr | Non-condensing storage water heater | All water heaters not described by UEF baseline definition with thermal efficiency >= 80% |  | kBtu/hr input capacity | TRM Version 8.0 | 2024-04-30 | 0 | 1.137 | 0 | 0 | 0 | 0 | 2591 | 0 | 15 | Direct Install | 0.05 | 1 | 1
COM-CS-WH-529-11 | Current | Split New Construction and Natural Replacement to effectively represent baseline and efficient efficiencies. Updated savings. | Commercial | Condensing Storage Water Heater | Low Utilization | Natural Replacement | water heating | Condensing storage water heater | All water heaters not described by UEF baseline definition with thermal efficiency >= 95% < 97%, <= 250 kBTU/hr | Non-condensing storage water heater | All water heaters not described by UEF baseline definition with thermal efficiency >= 80% |  | kBtu/hr input capacity | TRM Version 8.0 | 2024-04-30 | 0 | 1.422 | 0 | 0 | 0 | 0 | 2591 | 0 | 15 | Direct Install | 0.05 | 1 | 1
COM-CS-WH-529-12 | Current | Split New Construction and Natural Replacement to effectively represent baseline and efficient efficiencies. Updated savings. | Commercial | Condensing Storage Water Heater | Low Utilization | Natural Replacement | water heating | Condensing storage water heater | All water heaters not described by UEF baseline definition with thermal efficiency >= 97%, <= 250 kBTU/hr | Non-condensing storage water heater | All water heaters not described by UEF baseline definition with thermal efficiency >= 80% |  | kBtu/hr input capacity | TRM Version 8.0 | 2024-04-30 | 0 | 1.611 | 0 | 0 | 0 | 0 | 2591 | 0 | 15 | Direct Install | 0.05 | 1 | 1
COM-CS-WH-529-13 | Current | Split New Construction and Natural Replacement to effectively represent baseline and efficient efficiencies. Updated savings. | Commercial | Condensing Storage Water Heater | Low Utilization | Natural Replacement | water heating | Condensing storage water heater | All water heaters not described by UEF baseline definition with thermal efficiency >= 92% < 95%, > 250 kBTU/hr | Non-condensing storage water heater | All water heaters not described by UEF baseline definition with thermal efficiency >= 80% |  | kBtu/hr input capacity | TRM Version 8.0 | 2024-04-30 | 0 | 1.137 | 0 | 0 | 0 | 0 | 4464 | 0 | 15 | Direct Install | 0.05 | 1 | 1
COM-CS-WH-529-14 | Current | Split New Construction and Natural Replacement to effectively represent baseline and efficient efficiencies. Updated savings. | Commercial | Condensing Storage Water Heater | Low Utilization | Natural Replacement | water heating | Condensing storage water heater | All water heaters not described by UEF baseline definition with thermal efficiency >= 95% < 97%, > 250 kBTU/hr | Non-condensing storage water heater | All water heaters not described by UEF baseline definition with thermal efficiency >= 80% |  | kBtu/hr input capacity | TRM Version 8.0 | 2024-04-30 | 0 | 1.422 | 0 | 0 | 0 | 0 | 4464 | 0 | 15 | Direct Install | 0.05 | 1 | 1
COM-CS-WH-529-15 | Current | Split New Construction and Natural Replacement to effectively represent baseline and efficient efficiencies. Updated savings. | Commercial | Condensing Storage Water Heater | Low Utilization | Natural Replacement | water heating | Condensing storage water heater | All water heaters not described by UEF baseline definition with thermal efficiency >= 97%, > 250 kBTU/hr | Non-condensing storage water heater | All water heaters not described by UEF baseline definition with thermal efficiency >= 80% |  | kBtu/hr input capacity | TRM Version 8.0 | 2024-04-30 | 0 | 1.611 | 0 | 0 | 0 | 0 | 4464 | 0 | 15 | Direct Install | 0.05 | 1 | 1
COM-CS-WH-530-06 | Current | Split New Construction and Natural Replacement to effectively represent baseline and efficient efficiencies. Updated savings. | Commercial | Condensing Storage Water Heater | Low Utilization | New Construction | water heating | Condensing storage water heater | > 75 kBTU/hr and <= 105 kBTU/hr, rated nominal volume <= 120 US gallon, single-phase power, water temp <180 deg f, UEF >= 0.86 < 0.89 | Non-condensing storage water heater | > 75 kBTU/hr and <= 105 kBTU/hr, rated nominal volume <= 120 US gallon, single-phase power, water temp <180 deg f, UEF = 0.8107 - 0.00021Vs |  | kBtu/hr input capacity | TRM Version 8.0 | 2024-04-30 | 0 | 0.584 | 0 | 0 | 0 | 0 | 2591 | 0 | 15 | Direct Install | 0.05 | 1 | 1
COM-CS-WH-530-07 | Current | Split New Construction and Natural Replacement to effectively represent baseline and efficient efficiencies. Updated savings. | Commercial | Condensing Storage Water Heater | Low Utilization | New Construction | water heating | Condensing storage water heater | > 75 kBTU/hr and <= 105 kBTU/hr, rated nominal volume <= 120 US gallon, single-phase power, water temp <180 deg f, UEF >= 0.89 | Non-condensing storage water heater | > 75 kBTU/hr and <= 105 kBTU/hr, rated nominal volume <= 120 US gallon, single-phase power, water temp <180 deg f, UEF = 0.8107 - 0.00021Vs |  | kBtu/hr input capacity | TRM Version 8.0 | 2024-04-30 | 0 | 0.869 | 0 | 0 | 0 | 0 | 2591 | 0 | 15 | Direct Install | 0.05 | 1 | 1
COM-CS-WH-530-08 | Current | Split New Construction and Natural Replacement to effectively represent baseline and efficient efficiencies. Updated savings. | Commercial | Condensing Storage Water Heater | Low Utilization | New Construction | water heating | Condensing storage water heater | All water heaters not described by UEF baseline definition with thermal efficiency >= 95 < 97%, <= 250 kBTU/hr | Non-condensing storage water heater | All water heaters not described by UEF baseline definition with thermal efficiency = 90% |  | kBtu/hr input capacity | TRM Version 8.0 | 2024-04-30 | 0 | 0.421 | 0 | 0 | 0 | 0 | 2591 | 0 | 15 | Direct Install | 0.05 | 1 | 1
COM-CS-WH-530-09 | Current | Split New Construction and Natural Replacement to effectively represent baseline and efficient efficiencies. Updated savings. | Commercial | Condensing Storage Water Heater | Low Utilization | New Construction | water heating | Condensing storage water heater | All water heaters not described by UEF baseline definition with thermal efficiency >= 97%, <= 250 kBTU/hr | Non-condensing storage water heater | All water heaters not described by UEF baseline definition with thermal efficiency = 90% |  | kBtu/hr input capacity | TRM Version 8.0 | 2024-04-30 | 0 | 0.59 | 0 | 0 | 0 | 0 | 2591 | 0 | 15 | Direct Install | 0.05 | 1 | 1
COM-CS-WH-530-10 | Current | Split New Construction and Natural Replacement to effectively represent baseline and efficient efficiencies. Updated savings. | Commercial | Condensing Storage Water Heater | Low Utilization | New Construction | water heating | Condensing storage water heater | All water heaters not described by UEF baseline definition with thermal efficiency >= 95 < 97%, > 250 kBTU/hr | Non-condensing storage water heater | All water heaters not described by UEF baseline definition with thermal efficiency = 90% |  | kBtu/hr input capacity | TRM Version 8.0 | 2024-04-30 | 0 | 0.421 | 0 | 0 | 0 | 0 | 4464 | 0 | 15 | Direct Install | 0.05 | 1 | 1
COM-CS-WH-530-11 | Current | Split New Construction and Natural Replacement to effectively represent baseline and efficient efficiencies. Updated savings. | Commercial | Condensing Storage Water Heater | Low Utilization | New Construction | water heating | Condensing storage water heater | All water heaters not described by UEF baseline definition with thermal efficiency >= 97%, > 250 kBTU/hr | Non-condensing storage water heater | All water heaters not described by UEF baseline definition with thermal efficiency = 90% |  | kBtu/hr input capacity | TRM Version 8.0 | 2024-04-30 | 0 | 0.59 | 0 | 0 | 0 | 0 | 4464 | 0 | 15 | Direct Install | 0.05 | 1 | 1
COM-CS-WH-531-08 | Current | Split New Construction and Natural Replacement to effectively represent baseline and efficient efficiencies. Updated savings. | Commercial | Condensing Storage Water Heater | Medium Utilization | Natural Replacement | water heating | Condensing storage water heater | > 75 kBTU/hr and <= 105 kBTU/hr, rated nominal volume <= 120 US gallon, single-phase power, water temp <180 deg f, UEF >= 0.86 < 0.89 | Non-condensing storage water heater | > 75 kBTU/hr and <= 105 kBTU/hr, rated nominal volume <= 120 US gallon, single-phase power, water temp <180 deg f, UEF = 0.6597 - 0.00024Vs |  | kBtu/hr input capacity | TRM Version 8.0 | 2024-04-30 | 0 | 4.103 | 0 | 0 | 0 | 0 | 2591 | 0 | 15 | Direct Install | 0.05 | 1 | 1
COM-CS-WH-531-09 | Current | Split New Construction and Natural Replacement to effectively represent baseline and efficient efficiencies. Updated savings. | Commercial | Condensing Storage Water Heater | Medium Utilization | Natural Replacement | water heating | Condensing storage water heater | > 75 kBTU/hr and <= 105 kBTU/hr, rated nominal volume <= 120 US gallon, single-phase power, water temp <180 deg f, UEF >= 0.89 | Non-condensing storage water heater | > 75 kBTU/hr and <= 105 kBTU/hr, rated nominal volume <= 120 US gallon, single-phase power, water temp <180 deg f, UEF = 0.6597 - 0.00024Vs |  | kBtu/hr input capacity | TRM Version 8.0 | 2024-04-30 | 0 | 4.677 | 0 | 0 | 0 | 0 | 2591 | 0 | 15 | Direct Install | 0.05 | 1 | 1
COM-CS-WH-531-10 | Current | Split New Construction and Natural Replacement to effectively represent baseline and efficient efficiencies. Updated savings. | Commercial | Condensing Storage Water Heater | Medium Utilization | Natural Replacement | water heating | Condensing storage water heater | All water heaters not described by UEF baseline definition with thermal efficiency >= 92% < 95%, <= 250 kBTU/hr | Non-condensing storage water heater | All water heaters not described by UEF baseline definition with thermal efficiency >= 80% |  | kBtu/hr input capacity | TRM Version 8.0 | 2024-04-30 | 0 | 1.855 | 0 | 0 | 0 | 0 | 2591 | 0 | 15 | Direct Install | 0.05 | 1 | 1
COM-CS-WH-531-11 | Current | Split New Construction and Natural Replacement to effectively represent baseline and efficient efficiencies. Updated savings. | Commercial | Condensing Storage Water Heater | Medium Utilization | Natural Replacement | water heating | Condensing storage water heater | All water heaters not described by UEF baseline definition with thermal efficiency >= 95% < 97%, <= 250 kBTU/hr | Non-condensing storage water heater | All water heaters not described by UEF baseline definition with thermal efficiency >= 80% |  | kBtu/hr input capacity | TRM Version 8.0 | 2024-04-30 | 0 | 2.319 | 0 | 0 | 0 | 0 | 2591 | 0 | 15 | Direct Install | 0.05 | 1 | 1
COM-CS-WH-531-12 | Current | Split New Construction and Natural Replacement to effectively represent baseline and efficient efficiencies. Updated savings. | Commercial | Condensing Storage Water Heater | Medium Utilization | Natural Replacement | water heating | Condensing storage water heater | All water heaters not described by UEF baseline definition with thermal efficiency >= 97%, <= 250 kBTU/hr | Non-condensing storage water heater | All water heaters not described by UEF baseline definition with thermal efficiency >= 80% |  | kBtu/hr input capacity | TRM Version 8.0 | 2024-04-30 | 0 | 2.628 | 0 | 0 | 0 | 0 | 2591 | 0 | 15 | Direct Install | 0.05 | 1 | 1
COM-CS-WH-531-13 | Current | Split New Construction and Natural Replacement to effectively represent baseline and efficient efficiencies. Updated savings. | Commercial | Condensing Storage Water Heater | Medium Utilization | Natural Replacement | water heating | Condensing storage water heater | All water heaters not described by UEF baseline definition with thermal efficiency >= 92% < 95%, > 250 kBTU/hr | Non-condensing storage water heater | All water heaters not described by UEF baseline definition with thermal efficiency >= 80% |  | kBtu/hr input capacity | TRM Version 8.0 | 2024-04-30 | 0 | 1.855 | 0 | 0 | 0 | 0 | 4464 | 0 | 15 | Direct Install | 0.05 | 1 | 1
COM-CS-WH-531-14 | Current | Split New Construction and Natural Replacement to effectively represent baseline and efficient efficiencies. Updated savings. | Commercial | Condensing Storage Water Heater | Medium Utilization | Natural Replacement | water heating | Condensing storage water heater | All water heaters not described by UEF baseline definition with thermal efficiency >= 95% < 97%, > 250 kBTU/hr | Non-condensing storage water heater | All water heaters not described by UEF baseline definition with thermal efficiency >= 80% |  | kBtu/hr input capacity | TRM Version 8.0 | 2024-04-30 | 0 | 2.319 | 0 | 0 | 0 | 0 | 4464 | 0 | 15 | Direct Install | 0.05 | 1 | 1
COM-CS-WH-531-15 | Current | Split New Construction and Natural Replacement to effectively represent baseline and efficient efficiencies. Updated savings. | Commercial | Condensing Storage Water Heater | Medium Utilization | Natural Replacement | water heating | Condensing storage water heater | All water heaters not described by UEF baseline definition with thermal efficiency >= 97%, > 250 kBTU/hr | Non-condensing storage water heater | All water heaters not described by UEF baseline definition with thermal efficiency >= 80% |  | kBtu/hr input capacity | TRM Version 8.0 | 2024-04-30 | 0 | 2.628 | 0 | 0 | 0 | 0 | 4464 | 0 | 15 | Direct Install | 0.05 | 1 | 1
COM-CS-WH-532-06 | Current | Split New Construction and Natural Replacement to effectively represent baseline and efficient efficiencies. Updated savings. | Commercial | Condensing Storage Water Heater | Medium Utilization | New Construction | water heating | Condensing storage water heater | > 75 kBTU/hr and <= 105 kBTU/hr, rated nominal volume <= 120 US gallon, single-phase power, water temp <180 deg f, UEF >= 0.86 < 0.89 | Non-condensing storage water heater | > 75 kBTU/hr and <= 105 kBTU/hr, rated nominal volume <= 120 US gallon, single-phase power, water temp <180 deg f, UEF = 0.8107 - 0.00021Vs |  | kBtu/hr input capacity | TRM Version 8.0 | 2024-04-30 | 0 | 0.952 | 0 | 0 | 0 | 0 | 2591 | 0 | 15 | Direct Install | 0.05 | 1 | 1
COM-CS-WH-532-07 | Current | Split New Construction and Natural Replacement to effectively represent baseline and efficient efficiencies. Updated savings. | Commercial | Condensing Storage Water Heater | Medium Utilization | New Construction | water heating | Condensing storage water heater | > 75 kBTU/hr and <= 105 kBTU/hr, rated nominal volume <= 120 US gallon, single-phase power, water temp <180 deg f, UEF >= 0.89 | Non-condensing storage water heater | > 75 kBTU/hr and <= 105 kBTU/hr, rated nominal volume <= 120 US gallon, single-phase power, water temp <180 deg f, UEF = 0.8107 - 0.00021Vs |  | kBtu/hr input capacity | TRM Version 8.0 | 2024-04-30 | 0 | 1.417 | 0 | 0 | 0 | 0 | 2591 | 0 | 15 | Direct Install | 0.05 | 1 | 1
COM-CS-WH-532-08 | Current | Split New Construction and Natural Replacement to effectively represent baseline and efficient efficiencies. Updated savings. | Commercial | Condensing Storage Water Heater | Medium Utilization | New Construction | water heating | Condensing storage water heater | All water heaters not described by UEF baseline definition with thermal efficiency >= 95 < 97%, <= 250 kBTU/hr | Non-condensing storage water heater | All water heaters not described by UEF baseline definition with thermal efficiency = 90% |  | kBtu/hr input capacity | TRM Version 8.0 | 2024-04-30 | 0 | 0.687 | 0 | 0 | 0 | 0 | 2591 | 0 | 15 | Direct Install | 0.05 | 1 | 1
COM-CS-WH-532-09 | Current | Split New Construction and Natural Replacement to effectively represent baseline and efficient efficiencies. Updated savings. | Commercial | Condensing Storage Water Heater | Medium Utilization | New Construction | water heating | Condensing storage water heater | All water heaters not described by UEF baseline definition with thermal efficiency >= 97%, <= 250 kBTU/hr | Non-condensing storage water heater | All water heaters not described by UEF baseline definition with thermal efficiency = 90% |  | kBtu/hr input capacity | TRM Version 8.0 | 2024-04-30 | 0 | 0.962 | 0 | 0 | 0 | 0 | 2591 | 0 | 15 | Direct Install | 0.05 | 1 | 1
COM-CS-WH-532-10 | Current | Split New Construction and Natural Replacement to effectively represent baseline and efficient efficiencies. Updated savings. | Commercial | Condensing Storage Water Heater | Medium Utilization | New Construction | water heating | Condensing storage water heater | All water heaters not described by UEF baseline definition with thermal efficiency >= 95 < 97%, > 250 kBTU/hr | Non-condensing storage water heater | All water heaters not described by UEF baseline definition with thermal efficiency = 90% |  | kBtu/hr input capacity | TRM Version 8.0 | 2024-04-30 | 0 | 0.687 | 0 | 0 | 0 | 0 | 4464 | 0 | 15 | Direct Install | 0.05 | 1 | 1
COM-CS-WH-532-11 | Current | Split New Construction and Natural Replacement to effectively represent baseline and efficient efficiencies. Updated savings. | Commercial | Condensing Storage Water Heater | Medium Utilization | New Construction | water heating | Condensing storage water heater | All water heaters not described by UEF baseline definition with thermal efficiency >= 97%, > 250 kBTU/hr | Non-condensing storage water heater | All water heaters not described by UEF baseline definition with thermal efficiency = 90% |  | kBtu/hr input capacity | TRM Version 8.0 | 2024-04-30 | 0 | 0.962 | 0 | 0 | 0 | 0 | 4464 | 0 | 15 | Direct Install | 0.05 | 1 | 1
COM-CS-WH-504-01 | Replaced | Replaced in TRM Version 8.0 | Commercial | Condensing Storage Water Heater | High Utilization | New Construction/Natural Replacement | water heating | Condensing Storage Water Heater - High Utilization | > 75 kBtu/hr and <=250 kBtu/hr. inputEstimated overall efficiency of units shipped = 94.5% | Non-condensing storage water heater | Greater than 75 kBtu/hr. inputEstimated overall efficiency of units shipped = 80.1% |  | kBtu/hr input capacity | TRM Version 5.0 | 2020-11-12 | 0 | 3.09 | 0 | 0 | 0 | 0 | 2591 | 0 | 15 | Downstream | 0.05 | 1 | 1
COM-CT-WH-511-01 | Replaced | Replaced in TRM Version 8.0 | Commercial | Condensing Tankless Water Heater | Low Utilization | New Construction/Natural Replacement | water heating | Condensing Tankless Water Heater - Low Utilization | >=200 kBtu/hrThermal efficiency = 92.9%Stand-by Loss = negligible | Non-Condensing Storage Water Heater | 75 kBtu/hr. and greaterThermal efficiency of units shipped = 80.1%Stand-by Loss Q/0.8 +110√V0 | unit | kBtu/hr input capacity | TRM Version 5.0 | 2020-11-12 | 326 | 0.79 | 0 | 0 | 0 | 0 | 2227 | 0 | 20 | Downstream | 0.02 | 1 | 1
COM-CT-WH-512-01 | Replaced | Replaced in TRM Version 8.0 | Commercial | Condensing Tankless Water Heater | Medium Utilization | New Construction/Natural Replacement | water heating | Condensing Tankless Water Heater - Medium Utilization | >=200 kBtu/hrThermal efficiency = 92.9%Stand-by Loss = negligible | Non-Condensing Storage Water Heater | 75 kBtu/hr. and greaterThermal efficiency of units shipped = 80.1%Stand-by Loss Q/0.8 +110√V0 | unit | kBtu/hr input capacity | TRM Version 5.0 | 2020-11-12 | 326 | 1.29 | 0 | 0 | 0 | 0 | 2227 | 0 | 20 | Downstream | 0.02 | 1 | 1
COM-CT-WH-513-01 | Replaced | Replaced in TRM Version 8.0 | Commercial | Condensing Tankless Water Heater | High Utilization | New Construction/Natural Replacement | water heating | Condensing Tankless Water Heater - High Utilization | >=200 kBtu/hrThermal efficiency = 92.9%Stand-by Loss = negligible | Non-Condensing Storage Water Heater | 75 kBtu/hr. and greaterThermal efficiency of units shipped = 80.1%Stand-by Loss Q/0.8 +110√V0 | unit | kBtu/hr input capacity | TRM Version 5.0 | 2020-11-12 | 326 | 1.79 | 0 | 0 | 0 | 0 | 2227 | 0 | 20 | Downstream | 0.02 | 1 | 1
COM-CS-WH-505-01 | Replaced | Replaced in TRM Version 8.0 | Commercial | Condensing Storage Water Heater | Low Utilization | New Construction/Natural Replacement | water heating | Condensing Storage Water Heater - Low Utilization | >250 kBtu/hr. inputEstimated overall efficiency of units shipped = 94.5% | Non-condensing storage water heater | Greater than 75 kBtu/hr. inputEstimated overall efficiency of units shipped = 80.1% |  | kBtu/hr input capacity | TRM Version 5.0 | 2020-11-12 | 0 | 1.36 | 0 | 0 | 0 | 0 | 4464 | 0 | 15 | Downstream | 0.05 | 1 | 1
COM-CS-WH-506-01 | Replaced | Replaced in TRM Version 8.0 | Commercial | Condensing Storage Water Heater | Medium Utilization | New Construction/Natural Replacement | water heating | Condensing Storage Water Heater - Medium Utilization | >250 kBtu/hr. inputEstimated overall efficiency of units shipped = 94.5% | Non-condensing storage water heater | Greater than 75 kBtu/hr. inputEstimated overall efficiency of units shipped = 80.1% |  | kBtu/hr input capacity | TRM Version 5.0 | 2020-11-12 | 0 | 2.22 | 0 | 0 | 0 | 0 | 4464 | 0 | 15 | Downstream | 0.05 | 1 | 1
COM-CS-WH-507-01 | Replaced | Replaced in TRM Version 8.0 | Commercial | Condensing Storage Water Heater | High Utilization | New Construction/Natural Replacement | water heating | Condensing Storage Water Heater - High Utilization | >250 kBtu/hr. inputEstimated overall efficiency of units shipped = 94.5% | Non-condensing storage water heater | Greater than 75 kBtu/hr. inputEstimated overall efficiency of units shipped = 80.1% |  | kBtu/hr input capacity | TRM Version 5.0 | 2020-11-12 | 0 | 3.09 | 0 | 0 | 0 | 0 | 4464 | 0 | 15 | Downstream | 0.05 | 1 | 1
COM-CT-WH-508-01 | Replaced | Replaced in TRM Version 8.0 | Commercial | Condensing Tankless Water Heater | Low Utilization | New Construction/Natural Replacement | water heating | Condensing Tankless Water Heater - Low Utilization | >75 and <200 kBtu/hrThermal efficiency = 92.9%Stand-by Loss = negligible | Non-Condensing Storage Water Heater | 75 kBtu/hr. and greaterThermal efficiency of units shipped = 80.1%Stand-by Loss Q/0.8 +110√V0 | unit | kBtu/hr input capacity | TRM Version 5.0 | 2020-11-12 | 212 | 0.79 | 0 | 0 | 0 | 0 | 2227 | 0 | 20 | Downstream | 0.02 | 1 | 1
COM-CT-WH-509-01 | Replaced | Replaced in TRM Version 8.0 | Commercial | Condensing Tankless Water Heater | Medium Utilization | New Construction/Natural Replacement | water heating | Condensing Tankless Water Heater - Medium Utilization | >75 and <200 kBtu/hrThermal efficiency = 92.9%Stand-by Loss = negligible | Non-Condensing Storage Water Heater | 75 kBtu/hr. and greaterThermal efficiency of units shipped = 80.1%Stand-by Loss Q/0.8 +110√V0 | unit | kBtu/hr input capacity | TRM Version 5.0 | 2020-11-12 | 212 | 1.29 | 0 | 0 | 0 | 0 | 2227 | 0 | 20 | Downstream | 0.02 | 1 | 1
COM-CT-WH-510-01 | Replaced | Replaced in TRM Version 8.0 | Commercial | Condensing Tankless Water Heater | High Utilization | New Construction/Natural Replacement | water heating | Condensing Tankless Water Heater - High Utilization | >75 and <200 kBtu/hrThermal efficiency = 92.9%Stand-by Loss = negligible | Non-Condensing Storage Water Heater | 75 kBtu/hr. and greaterThermal efficiency of units shipped = 80.1%Stand-by Loss Q/0.8 +110√V0 | unit | kBtu/hr input capacity | TRM Version 5.0 | 2020-11-12 | 212 | 1.79 | 0 | 0 | 0 | 0 | 2227 | 0 | 20 | Downstream | 0.02 | 1 | 1
COM-DK-SH-521-01 | Replaced | Updated in TRM V8.0 | Commercial | Demand Control Kitchen Ventilation |  | Retrofit - LEGD Rate Zone | space heating | Demand Control Kitchen Ventilation | 0 - 5,000 CFM | Constant Volume Kitchen Ventilation |  | unit |  | TRM Version 5.0 | 2020-11-12 | 4207 | 0 | 4940 | 0 | 0 | 0 | 4766 | 0 | 15 | Downstream | 0.38 | 1 | 1.0274
COM-DK-SH-524-01 | Replaced | Updated in TRM V8.0 | Commercial | Demand Control Kitchen Ventilation |  | New Construction/Natural Replacement - LEGD Rate Zone | space heating | Demand Control Kitchen Ventilation | 0 - 5,000 CFM | Constant Volume Kitchen Ventilation |  | unit |  | TRM Version 5.0 | 2020-11-12 | 4207 | 0 | 4940 | 0 | 0 | 0 | 2383 | 0 | 15 | Downstream | 0.38 | 1 | 1.0274
MRS-SH-WH-569-01 | Replaced | Updated in TRM Version 6.0 | Commercial | Showerhead | Multi-residential | New Construction - LEGD | water heating | Low-flow showerhead | 1.25 GPM |  | 2.0 GPM | unit |  | TRM Version 5.0 | 2020-11-12 | 23 | 0 | 0 | 0 | 8020 | 0 | actual cost |  | 10 | Downstream | 0.1 | 0.845 | 1
MRS-SH-WH-571-01 | Replaced | Updated in TRM Version 6.0 | Commercial | Showerhead | Multi-residential | Retrofit - LEGD | water heating | Low-flow showerhead | 1.25 GPM | Average existing stock | 2.5 GPM | unit |  | TRM Version 5.0 | 2020-11-12 | 38.2 | 0 | 0 | 0 | 12105 | 0 | actual cost |  | 10 | Downstream | 0.1 | 0.845 | 1
MRS-SH-WH-570-01 | Replaced | Updated in TRM Version 6.0 | Commercial | Showerhead | Multi-residential | New Construction - LEGD | water heating | Low-flow showerhead | 1.50 GPM |  | 2.0 GPM | unit |  | TRM Version 5.0 | 2020-11-12 | 15.3 | 0 | 0 | 0 | 4237 | 0 | actual cost |  | 10 | Downstream | 0.1 | 0.845 | 1
MRS-SH-WH-572-01 | Replaced | Updated in TRM Version 6.0 | Commercial | Showerhead | Multi-residential | Retrofit - LEGD | water heating | Low-flow showerhead | 1.50 GPM | Average existing stock | 2.5 GPM | unit |  | TRM Version 5.0 | 2020-11-12 | 30.6 | 0 | 0 | 0 | 8322 | 0 | actual cost |  | 10 | Downstream | 0.1 | 0.845 | 1
COM-DK-SH-523-01 | Replaced | Updated in TRM V8.0 | Commercial | Demand Control Kitchen Ventilation |  | Retrofit - LEGD Rate Zone | space heating | Demand Control Kitchen Ventilation | 10,001 - 15,000 CFM | Constant Volume Kitchen Ventilation |  | unit |  | TRM Version 5.0 | 2020-11-12 | 17529 | 0 | 28929 | 0 | 0 | 0 | 19859 | 0 | 15 | Downstream | 0.38 | 1 | 1.0274
COM-DK-SH-526-01 | Replaced | Updated in TRM V8.0 | Commercial | Demand Control Kitchen Ventilation |  | New Construction/Natural Replacement - LEGD Rate Zone | space heating | Demand Control Kitchen Ventilation | 10,001 - 15,000 CFM | Constant Volume Kitchen Ventilation |  | unit |  | TRM Version 5.0 | 2020-11-12 | 17529 | 0 | 28929 | 0 | 0 | 0 | 9929 | 0 | 15 | Downstream | 0.38 | 1 | 1.0274
COM-CU-SH-515-01 | Replaced | Updated in TRM Version 6.0 with new incremental cost and negative, not positive electric savings. | Commercial | Condensing Unit Heater |  | Natural Replacement | space heating | Condensing Unit Heater | 125-200 kBtu/hr 90% Thermal Efficiency, 89% Annual Efficiency | Non-Condensing Unit Heater | 80% Thermal Efficiency, 78% Annual Efficiency |  | kBtu/hr input capacity | TRM Version 5.0 | 2020-11-12 | 0 | 7.89 | -530 | 0 | 0 | 0 | 0 | 12.9 | 18 | Downstream | 0 | 1 | 1
COM-CU-SH-518-01 | Replaced | Updated in TRM Version 6.0 with new incremental cost and negative, not positive electric savings. | Commercial | Condensing Unit Heater |  | New Construction | space heating | Condensing Unit Heater | 125-200 kBtu/hr 90% Thermal Efficiency, 89% Annual Efficiency | Non-Condensing Unit Heater | 80% Thermal Efficiency, 78% Annual Efficiency |  | kBtu/hr input capacity | TRM Version 5.0 | 2020-11-12 | 0 | 5.92 | -398 | 0 | 0 | 0 | 0 | 12.9 | 18 | Downstream | 0 | 1 | 1
COM-CU-SH-516-01 | Replaced | Updated in TRM Version 6.0 with new incremental cost and negative, not positive electric savings. | Commercial | Condensing Unit Heater |  | Natural Replacement | space heating | Condensing Unit Heater | 225-300 kBtu/hr 90% Thermal Efficiency, 89% Annual Efficiency | Non-Condensing Unit Heater | 80% Thermal Efficiency, 78% Annual Efficiency |  | kBtu/hr input capacity | TRM Version 5.0 | 2020-11-12 | 0 | 7.89 | -546 | 0 | 0 | 0 | 0 | 12.9 | 18 | Downstream | 0 | 1 | 1
COM-CU-SH-519-01 | Replaced | Updated in TRM Version 6.0 with new incremental cost and negative, not positive electric savings. | Commercial | Condensing Unit Heater |  | New Construction | space heating | Condensing Unit Heater | 225-300 kBtu/hr 90% Thermal Efficiency, 89% Annual Efficiency | Non-Condensing Unit Heater | 80% Thermal Efficiency, 78% Annual Efficiency |  | kBtu/hr input capacity | TRM Version 5.0 | 2020-11-12 | 0 | 5.92 | -410 | 0 | 0 | 0 | 0 | 12.9 | 18 | Downstream | 0 | 1 | 1
COM-CU-SH-514-01 | Replaced | Updated in TRM Version 6.0 with new incremental cost and negative, not positive electric savings. | Commercial | Condensing Unit Heater |  | Natural Replacement | space heating | Condensing Unit Heater | 30-100 kBtu/hr - 90% Thermal Efficiency, 89% Annual Efficiency | Non-Condensing Unit Heater | 80% Thermal Efficiency, 78% Annual Efficiency |  | kBtu/hr input capacity | TRM Version 5.0 | 2020-11-12 | 0 | 7.89 | -296 | 0 | 0 | 0 | 0 | 12.9 | 18 | Downstream | 0 | 1 | 1
COM-CU-SH-517-01 | Replaced | Updated in TRM Version 6.0 with new incremental cost and negative, not positive electric savings. | Commercial | Condensing Unit Heater |  | New Construction | space heating | Condensing Unit Heater | 30-100 kBtu/hr - 90% Thermal Efficiency, 89% Annual Efficiency | Non-Condensing Unit Heater | 80% Thermal Efficiency, 78% Annual Efficiency |  | kBtu/hr input capacity | TRM Version 5.0 | 2020-11-12 | 0 | 5.92 | -222 | 0 | 0 | 0 | 0 | 12.9 | 18 | Downstream | 0 | 1 | 1
COM-DK-SH-522-01 | Replaced | Updated in TRM V8.0 | Commercial | Demand Control Kitchen Ventilation |  | Retrofit - LEGD Rate Zone | space heating | Demand Control Kitchen Ventilation | 5,001 - 10,000 CFM | Constant Volume Kitchen Ventilation |  | unit |  | TRM Version 5.0 | 2020-11-12 | 10517 | 0 | 16294 | 0 | 0 | 0 | 11915 | 0 | 15 | Downstream | 0.38 | 1 | 1.0274
COM-DK-SH-525-01 | Replaced | Updated in TRM V8.0 | Commercial | Demand Control Kitchen Ventilation |  | New Construction/Natural Replacement - LEGD Rate Zone | space heating | Demand Control Kitchen Ventilation | 5,001 - 10,000 CFM | Constant Volume Kitchen Ventilation |  | unit |  | TRM Version 5.0 | 2020-11-12 | 10517 | 0 | 16294 | 0 | 0 | 0 | 5958 | 0 | 15 | Downstream | 0.38 | 1 | 1.0274
COM-CO-FS-520-01 | Replaced | Updated in TRM Version 6.0 | Commercial | Convection Ovens |  | New Construction/Natural Replacement | food service | Energy Star Convection Ovens | Energy Star Rated Convection Oven (Full Size) | Conventional Convection Oven (Full Size) |  | unit |  | TRM Version 5.0 | 2020-11-12 | 865 | 0 | 40.1 | 0 | 0 | 0 | 1200 | 0 | 12 | Downstream | 0.2 | 1 | 1
COM-FR-FS-324-01 | Replaced | Updated in TRM Version 7.0 | Commercial | Fryer |  | New Construction/Natural Replacement | food service | Energy Star Fryer | Energy Star Rated Fryer | Non-Energy Star rated Fryer |  | unit |  | TRM Version 5.0 | 2020-11-12 | 1408 | 0 | 0 | 0 | 0 | 0 | 2476 | 0 | 12 | Downstream | 0.2 | 1 | 1
COM-RO-FS-651-01 | Replaced | Updated in V6.0 | Commercial | Rack Oven |  | New Construction/Natural Replacement | food service | ENERGY STAR Rack Oven | Energy Star Rated Rack Oven, Double | Conventiona rack oven |  | unit |  | TRM Version 5.0 | 2020-11-12 | 1076 | 0 | 1685 | 0 | 0 | 0 | 2591 | 0 | 12 | Downstream | 0.2 | 1 | 1
COM-RO-FS-650-01 | Replaced | Updated in V6.0 | Commercial | Rack Oven |  | New Construction/Natural Replacement | food service | ENERGY STAR Rack Oven | Energy Star Rated Rack Oven, Single | Conventiona rack oven |  | unit |  | TRM Version 5.0 | 2020-11-12 | 830 | 0 | 749 | 0 | 0 | 0 | 1544 | 0 | 12 | Downstream | 0.2 | 1 | 1
COM-SC-FS-325-01 | Replaced | Updated in TRM Version 7.0 | Commercial | Steam Cookers |  | New Construction/Natural Replacement | food service | Energy Star Steam Cookers | Energy Star Rated Steam Cooker | Boiler-based steam cooker |  | unit |  | TRM Version 5.0 | 2020-11-12 | 8889 | 0 | 0 | 0 | 340142 | 0 | 3880 | 0 | 12 | Downstream | 0.2 | 1 | 1
COM-DW-WH-555-01 | Replaced | Updated in TRM Version 6.0 | Commercial | Dishwasher |  | New Construction/Natural Replacement | water heating | Energy Star Dishwasher | Multi Tank Conveyor - High Temperature | Non-Energy Star Dishwasher |  | unit |  | TRM Version 5.0 | 2020-11-12 | 2049 | 0 | 9680 | 0 | 304677 | 0 | 1386 | 0 | 20 | Downstream | 0.27 | 1 | 1
COM-DW-WH-556-01 | Replaced | Updated in TRM Version 6.0 | Commercial | Dishwasher |  | New Construction/Natural Replacement | water heating | Energy Star Dishwasher | Multi Tank Conveyor - Low Temperature | Non-Energy Star Dishwasher |  | unit |  | TRM Version 5.0 | 2020-11-12 | 2383 | 0 | 0 | 0 | 354276 | 0 | 1386 | 0 | 20 | Downstream | 0.27 | 1 | 1
COM-OL-WH-329-01 | Replaced | Updated in TRM Version 6.0 | Commercial | Ozone Laundry |  | New Construction/Retrofit | water heating | Commercial Ozone Laundry Treatment | Ozone Treatment Tunnel Washer <= 120 lbs | Commercial laundry with no ozone treatment system |  |  | lbs/yr | TRM Version 5.0 | 2020-11-12 | 0 | 0.0305 | 0 | 0.0015 | 0 | 1.27 | 71429 | 0 | 15 | Downstream | 0.08 | 1 | 1
COM-OL-WH-331-01 | Replaced | Updated in TRM Version 6.0 | Commercial | Ozone Laundry |  | New Construction/Retrofit | water heating | Commercial Ozone Laundry Treatment | Ozone Treatment Tunnel Washer=> 500 lbs | Commercial laundry with no ozone treatment system |  |  | lbs/yr | TRM Version 5.0 | 2020-11-12 | 0 | 0.0305 | 0 | 0.0015 | 0 | 1.27 | 228571 | 0 | 15 | Downstream | 0.08 | 1 | 1
COM-OL-WH-330-01 | Replaced | Updated in TRM Version 6.0 | Commercial | Ozone Laundry |  | New Construction/Retrofit | water heating | Commercial Ozone Laundry Treatment | Ozone Treatment Tunnel Washer121 lbs to 499 lbs | Commercial laundry with no ozone treatment system |  |  | lbs/yr | TRM Version 5.0 | 2020-11-12 | 0 | 0.0305 | 0 | 0.0015 | 0 | 1.27 | 150000 | 0 | 15 | Downstream | 0.08 | 1 | 1
COM-OL-WH-326-01 | Replaced | Updated in TRM Version 6.0 | Commercial | Ozone Laundry |  | New Construction/Retrofit | water heating | Commercial Ozone Laundry Treatment | Ozone Treatment Washer extractor =< 60 lbs | Commercial laundry with no ozone treatment system |  |  | lbs/yr | TRM Version 5.0 | 2020-11-12 | 0 | 0.0383 | 0 | 0.00213 | 0 | 2.08 | 15714 | 0 | 15 | Downstream | 0.08 | 1 | 1
COM-OL-WH-327-01 | Replaced | Updated in TRM Version 6.0 | Commercial | Ozone Laundry |  | New Construction/Retrofit | water heating | Commercial Ozone Laundry Treatment | Ozone Treatment Washer extractor 61 lbs to 499 lbs | Commercial laundry with no ozone treatment system |  |  | lbs/yr | TRM Version 5.0 | 2020-11-12 | 0 | 0.0383 | 0 | 0.00213 | 0 | 2.08 | 35714 | 0 | 15 | Downstream | 0.08 | 1 | 1
COM-OL-WH-328-01 | Replaced | Updated in TRM Version 6.0 | Commercial | Ozone Laundry |  | New Construction/Retrofit | water heating | Commercial Ozone Laundry Treatment | Ozone Treatment Washer extractor=> 500 lbs | Commercial laundry with no ozone treatment system |  |  | lbs/yr | TRM Version 5.0 | 2020-11-12 | 0 | 0.0383 | 0 | 0.00213 | 0 | 2.08 | 44286 | 0 | 15 | Downstream | 0.08 | 1 | 1
COM-UB-FS-332-01 | Replaced | Updated in TRM Version 7.0 | Commercial | Under-Fired Broilers |  | New Construction/Natural Replacement | food service | High Efficiency Under-Fired Broilers - 3 foot | pre-heat =< 40,500 Btu and cooking energy rate =< 72,000 Btu/hr | Conventional Efficiency Under-Fired Broiler | pre-heat =< 48,000 Btu and cooking energy rate =< 96,000 Btu/hr | unit |  | TRM Version 5.0 | 2020-11-12 | 2511 | 0 | 0 | 0 | 0 | 0 | 1900 | 0 | 12 | Downstream | 0.2 | 1 | 1
COM-UB-FS-333-01 | Replaced | Updated in TRM Version 7.0 | Commercial | Under-Fired Broilers |  | New Construction/Natural Replacement | food service | High Efficiency Under-Fired Broilers - 4 foot | pre-heat 40,501 to 54,000 Btu and a cooking energy rate 72,001 to 96,000 Btu/hr | Conventional Efficiency Under-Fired Broiler | pre-heat 48,001 to 64,000 Btu and a cooking energy rate 96,000 to 128,000 Btu/hr | unit |  | TRM Version 5.0 | 2020-11-12 | 3347 | 0 | 0 | 0 | 0 | 0 | 1900 | 0 | 12 | Downstream | 0.2 | 1 | 1
COM-UB-FS-334-01 | Replaced | Updated in TRM Version 7.0 | Commercial | Under-Fired Broilers |  | New Construction/Natural Replacement | food service | High Efficiency Under-Fired Broilers - 5 foot | pre-heat 54,001 to 67,500 Btu and cooking energy rate 96,001 to 120,000 Btu/hr | Conventional Efficiency Under-Fired Broiler | pre-heat 64,001 to 80,000 Btu and cooking energy rate 128,001 to 160,000 Btu/hr | unit |  | TRM Version 5.0 | 2020-11-12 | 4184 | 0 | 0 | 0 | 0 | 0 | 1900 | 0 | 12 | Downstream | 0.2 | 1 | 1
COM-UB-FS-335-01 | Replaced | Updated in TRM Version 7.0 | Commercial | Under-Fired Broilers |  | New Construction/Natural Replacement | food service | High Efficiency Under-Fired Broilers - 6 foot | pre-heat 67,501 to 81,000 Btu and cooking energy rate 120,001 to 144,000 Btu/hr | Conventional Efficiency Under-Fired Broiler | pre-heat 80,001 to 96,000 Btu and cooking energy rate 160,001 to 192,000 Btu/hr | unit |  | TRM Version 5.0 | 2020-11-12 | 5021 | 0 | 0 | 0 | 0 | 0 | 1900 | 0 | 12 | Downstream | 0.2 | 1 | 1
COM-DW-WH-553-01 | Replaced | Updated in TRM Version 6.0 | Commercial | Dishwasher |  | New Construction/Natural Replacement | water heating | Energy Star Dishwasher | Single Tank Conveyor – High Temperature | Non-Energy Star Dishwasher |  | unit |  | TRM Version 5.0 | 2020-11-12 | 540 | 0 | 4251 | 0 | 80303 | 0 | 2929 | 0 | 20 | Downstream | 0.27 | 1 | 1
COM-DW-WH-554-01 | Replaced | Updated in TRM Version 6.0 | Commercial | Dishwasher |  | New Construction/Natural Replacement | water heating | Energy Star Dishwasher | Single Tank Conveyor - Low Temperature | Non-Energy Star Dishwasher |  | unit |  | TRM Version 5.0 | 2020-11-12 | 1652 | 0 | 0 | 0 | 245631 | 0 | 0 | 0 | 20 | Downstream | 0.27 | 1 | 1
COM-DW-WH-551-01 | Replaced | Updated in TRM Version 6.0 | Commercial | Dishwasher |  | New Construction/Natural Replacement | water heating | Energy Star Dishwasher | Stationary Single Tank Door – High Temperature | Non-Energy Star Dishwasher |  | unit |  | TRM Version 5.0 | 2020-11-12 | 890 | 0 | 4173 | 0 | 132263 | 0 | 1100 | 0 | 15 | Downstream | 0.2 | 1 | 1
COM-DW-WH-552-01 | Replaced | Updated in TRM Version 6.0 | Commercial | Dishwasher |  | New Construction/Natural Replacement | water heating | Energy Star Dishwasher | Stationary Single Tank Door – Low Temperature | Non-Energy Star Dishwasher |  | unit |  | TRM Version 5.0 | 2020-11-12 | 2046 | 0 | 0 | 0 | 304205 | 0 | 0 | 0 | 15 | Downstream | 0.2 | 1 | 1
COM-DW-WH-549-01 | Replaced | Updated in TRM Version 6.0 | Commercial | Dishwasher |  | New Construction/Natural Replacement | water heating | Energy Star Dishwasher | Undercounter – High Temperature | Non-Energy Star Dishwasher |  | unit |  | TRM Version 5.0 | 2020-11-12 | 137 | 0 | 1791 | 0 | 20371 | 0 | 171 | 0 | 10 | Downstream | 0.4 | 1 | 1
COM-DW-WH-550-01 | Replaced | Updated in TRM Version 6.0 | Commercial | Dishwasher |  | New Construction/Natural Replacement | water heating | Energy Star Dishwasher | Undercounter – Low Temperature | Non-Energy Star Dishwasher |  | unit |  | TRM Version 5.0 | 2020-11-12 | 322 | 0 | 0 | 0 | 47827 | 0 | 71 | 0 | 10 | Downstream | 0.4 | 1 | 1
COM-CU-SH-515-01 | Replaced | Updated in TRM Version 8.0 | Commercial | Condensing Unit Heater |  | Natural Replacement | space heating | Condensing Unit Heater | 125-200 kBtu/hr 90% Thermal Efficiency, 89% Annual Efficiency | Non-Condensing Unit Heater | 80% Thermal Efficiency, 78% Annual Efficiency |  | kBtu/hr input capacity | TRM Version 6.0 | 2021-12-16 | 0 | 7.89 | -530 | 0 | 0 | 0 | 0 | 16.08 | 18 | Downstream | 0 | 1 | 1
COM-CU-SH-518-01 | Replaced | Updated in TRM Version 8.0 | Commercial | Condensing Unit Heater |  | New Construction | space heating | Condensing Unit Heater | 125-200 kBtu/hr 90% Thermal Efficiency, 89% Annual Efficiency | Non-Condensing Unit Heater | 80% Thermal Efficiency, 78% Annual Efficiency |  | kBtu/hr input capacity | TRM Version 6.0 | 2021-12-16 | 0 | 5.92 | -398 | 0 | 0 | 0 | 0 | 16.08 | 18 | Downstream | 0 | 1 | 1
COM-CU-SH-516-01 | Replaced | Updated in TRM Version 8.0 | Commercial | Condensing Unit Heater |  | Natural Replacement | space heating | Condensing Unit Heater | 225-300 kBtu/hr 90% Thermal Efficiency, 89% Annual Efficiency | Non-Condensing Unit Heater | 80% Thermal Efficiency, 78% Annual Efficiency |  | kBtu/hr input capacity | TRM Version 6.0 | 2021-12-16 | 0 | 7.89 | -546 | 0 | 0 | 0 | 0 | 16.08 | 18 | Downstream | 0 | 1 | 1
COM-CU-SH-519-01 | Replaced | Updated in TRM Version 8.0 | Commercial | Condensing Unit Heater |  | New Construction | space heating | Condensing Unit Heater | 225-300 kBtu/hr 90% Thermal Efficiency, 89% Annual Efficiency | Non-Condensing Unit Heater | 80% Thermal Efficiency, 78% Annual Efficiency |  | kBtu/hr input capacity | TRM Version 6.0 | 2021-12-16 | 0 | 5.92 | -410 | 0 | 0 | 0 | 0 | 16.08 | 18 | Downstream | 0 | 1 | 1
COM-CU-SH-514-01 | Replaced | Updated in TRM Version 8.0 | Commercial | Condensing Unit Heater |  | Natural Replacement | space heating | Condensing Unit Heater | 30-100 kBtu/hr - 90% Thermal Efficiency, 89% Annual Efficiency | Non-Condensing Unit Heater | 80% Thermal Efficiency, 78% Annual Efficiency |  | kBtu/hr input capacity | TRM Version 6.0 | 2021-12-16 | 0 | 7.89 | -296 | 0 | 0 | 0 | 0 | 16.08 | 18 | Downstream | 0 | 1 | 1
COM-CU-SH-517-01 | Replaced | Updated in TRM Version 8.0 | Commercial | Condensing Unit Heater |  | New Construction | space heating | Condensing Unit Heater | 30-100 kBtu/hr - 90% Thermal Efficiency, 89% Annual Efficiency | Non-Condensing Unit Heater | 80% Thermal Efficiency, 78% Annual Efficiency |  | kBtu/hr input capacity | TRM Version 6.0 | 2021-12-16 | 0 | 5.92 | -222 | 0 | 0 | 0 | 0 | 16.08 | 18 | Downstream | 0 | 1 | 1
COM-DW-WH-555-01 | Replaced | Updated in TRM Version 7.0; revised from TRM Version 5.0: natural gas, electric savings, and water savings | Commercial | Dishwasher |  | New Construction/Natural Replacement | water heating | Energy Star Dishwasher | Multi Tank Conveyor - High Temperature | Non-Energy Star Dishwasher |  | unit |  | TRM Version 6.0 | 2021-12-16 | 2260 | 0 | 10673 | 0 | 335926 | 0 | 1386 | 0 | 20 | Downstream | 0.27 | 1 | 1
COM-DW-WH-556-01 | Replaced | Updated in TRM Version 7.0; revised from TRM Version 5.0: natural gas, electric savings, and water savings | Commercial | Dishwasher |  | New Construction/Natural Replacement | water heating | Energy Star Dishwasher | Multi Tank Conveyor - Low Temperature | Non-Energy Star Dishwasher |  | unit |  | TRM Version 6.0 | 2021-12-16 | 2628 | 0 | 0 | 0 | 390612 | 0 | 1386 | 0 | 20 | Downstream | 0.27 | 1 | 1
COM-DW-WH-553-01 | Replaced | Updated in TRM Version 7.0; revised from TRM Version 5.0: natural gas, electric savings, and water savings | Commercial | Dishwasher |  | New Construction/Natural Replacement | water heating | Energy Star Dishwasher | Single Tank Conveyor – High Temperature | Non-Energy Star Dishwasher |  | unit |  | TRM Version 6.0 | 2021-12-16 | 596 | 0 | 4686 | 0 | 88539 | 0 | 2929 | 0 | 20 | Downstream | 0.27 | 1 | 1
COM-DW-WH-554-01 | Replaced | Updated in TRM Version 7.0; revised from TRM Version 5.0: natural gas, electric savings, and water savings | Commercial | Dishwasher |  | New Construction/Natural Replacement | water heating | Energy Star Dishwasher | Single Tank Conveyor - Low Temperature | Non-Energy Star Dishwasher |  | unit |  | TRM Version 6.0 | 2021-12-16 | 1822 | 0 | 0 | 0 | 270824 | 0 | 0 | 0 | 20 | Downstream | 0.27 | 1 | 1
COM-DW-WH-551-01 | Replaced | Updated in TRM Version 7.0; revised from TRM Version 5.0: natural gas, electric savings, and water savings | Commercial | Dishwasher |  | New Construction/Natural Replacement | water heating | Energy Star Dishwasher | Stationary Single Tank Door – High Temperature | Non-Energy Star Dishwasher |  | unit |  | TRM Version 6.0 | 2021-12-16 | 981 | 0 | 4601 | 0 | 145828 | 0 | 1100 | 0 | 15 | Downstream | 0.2 | 1 | 1
COM-DW-WH-552-01 | Replaced | Updated in TRM Version 7.0; revised from TRM Version 5.0: natural gas, electric savings, and water savings | Commercial | Dishwasher |  | New Construction/Natural Replacement | water heating | Energy Star Dishwasher | Stationary Single Tank Door – Low Temperature | Non-Energy Star Dishwasher |  | unit |  | TRM Version 6.0 | 2021-12-16 | 2256 | 0 | 0 | 0 | 335406 | 0 | 0 | 0 | 15 | Downstream | 0.2 | 1 | 1
COM-DW-WH-549-01 | Replaced | Updated in TRM Version 7.0; revised from TRM Version 5.0: natural gas, electric savings, and water savings | Commercial | Dishwasher |  | New Construction/Natural Replacement | water heating | Energy Star Dishwasher | Undercounter – High Temperature | Non-Energy Star Dishwasher |  | unit |  | TRM Version 6.0 | 2021-12-16 | 151 | 0 | 1975 | 0 | 22460 | 0 | 171 | 0 | 10 | Downstream | 0.4 | 1 | 1
COM-DW-WH-550-01 | Replaced | Updated in TRM Version 7.0; revised from TRM Version 5.0: natural gas, electric savings, and water savings | Commercial | Dishwasher |  | New Construction/Natural Replacement | water heating | Energy Star Dishwasher | Undercounter – Low Temperature | Non-Energy Star Dishwasher |  | unit |  | TRM Version 6.0 | 2021-12-16 | 355 | 0 | 0 | 0 | 52733 | 0 | 71 | 0 | 10 | Downstream | 0.4 | 1 | 1
COM-CF-SH-494-01 | Current |  | Commercial | Condensing Furnace |  | New Construction | space heating | High Efficiency Condensing Furnace | >=97% AFUE | Condensing Furnace | 95% AFUE |  | kBtu/hr | TRM Version 5.0 | 2020-11-12 | 0 | 0.884 | 0 | 0 | 0 | 0 | 188 | 0 | 18 | Downstream | 0.175 | 1 | 1
COM-CF-SH-495-01 | Current |  | Commercial | Condensing Furnace |  | Natural Replacement | space heating | High Efficiency Condensing Furnace | >=97% AFUE | Condensing Furnace | 95% AFUE |  | kBtu/hr | TRM Version 5.0 | 2020-11-12 | 0 | 1.178 | 0 | 0 | 0 | 0 | 188 | 0 | 18 | Downstream | 0.175 | 1 | 1
RES-CF-SH-490-01 | Current |  | Residential | Condensing Furnace |  | New Construction | space heating | High Efficiency Condensing Furnace | >=97% AFUE | Condensing Furnace | 95% AFUE |  | kBtu/hr | TRM Version 5.0 | 2020-11-12 | 0 | 0.343 | 0 | 0 | 0 | 0 | 188 | 0 | 18 | Downstream | 0 | 1 | 1
RES-CF-SH-491-01 | Current |  | Residential | Condensing Furnace |  | Natural Replacement | space heating | High Efficiency Condensing Furnace | >=97% AFUE | Condensing Furnace | 95% AFUE |  | kBtu/hr | TRM Version 5.0 | 2020-11-12 | 0 | 0.446 | 0 | 0 | 0 | 0 | 188 | 0 | 18 | Downstream | 0 | 1 | 1
RES-SH-WH-567-01 | Current |  | Residential | Showerhead |  | Retrofit | water heating | Low-flow showerhead | 1.25 GPM (Per household) | Average Existing Stock | 2.5 GPM | unit |  | TRM Version 5.0 | 2020-11-12 | 28.2 | 0 | 0 | 0 | 13885 | 0 | actual cost |  | 10 | Downstream | 0.04 | 0.851 | 1
RES-SH-WH-568-01 | Current |  | Residential | Showerhead |  | Retrofit | water heating | Low-flow showerhead | 1.5 GPM (Per Household) | Average Existing Stock | 2.5 GPM | unit |  | TRM Version 5.0 | 2020-11-12 | 22.5 | 0 | 0 | 0 | 9546 | 0 | actual cost |  | 10 | Downstream | 0.04 | 0.851 | 1
RES-SH-WH-567-05 | Current |  | Residential | Showerhead |  | New Construction | water heating | Low-flow showerhead | 1.25 GPM (Per household) | Average Existing Stock | 2.0 GPM | unit |  | TRM Version 5.0 | 2020-11-12 | 16.9 | 0 | 0 | 0 | 9119 | 0 | actual cost |  | 10 | Downstream | 0.04 | 0.851 | 1
RES-SH-WH-568-05 | Current |  | Residential | Showerhead |  | New Construction | water heating | Low-flow showerhead | 1.5 GPM (Per Household) | Average Existing Stock | 2.0 GPM | unit |  | TRM Version 5.0 | 2020-11-12 | 11.3 | 0 | 0 | 0 | 4860 | 0 | actual cost |  | 10 | Downstream | 0.04 | 0.851 | 1
COM-DS-SH-560-01 | Current |  | Commercial | Dock Door Seals |  | Retrofit | space heating | Dock Door Seals | 10' x 10' | Dock door with deteriorated seals |  | unit |  | TRM Version 5.0 | 2020-11-12 | 1736 | 0 | 433 | 0 | 0 | 0 | 2968 | 0 | 10 | Downstream | 0.05 | 1 | 1
COM-DS-SH-564-01 | Current |  | Commercial | Dock Door Seals |  | Retrofit | space heating | Dock Door Seals | 10' x 10' | Dock door without seals |  | unit |  | TRM Version 5.0 | 2020-11-12 | 4501 | 0 | 1123 | 0 | 0 | 0 | 2615 | 0 | 10 | Downstream | 0.05 | 1 | 1
COM-CM-SH-497-01 | Current |  | Commercial | Condensing Make Up Air Unit | Commercial | New Construction/Natural Replacement | space heating | Condensing Make Up Air Unit (MUA) - Commercial | 2 Speed | Conventional MUA | 80% Thermal Efficiency |  | CFM | TRM Version 5.0 | 2020-11-12 | 0 | 1.22 | 0 | 1.24 | 0 | 0 | 870 | 1.01 | 20 | Downstream | 0.05 | 1 | 1
COM-CM-SH-500-01 | Current |  | Commercial | Condensing Make Up Air Unit | Multi-Residential and Long Term Care | New Construction/Natural Replacement | space heating | Condensing Make Up Air Unit (MUA) - Commercial | 2 Speed | Conventional MUA | 80% Thermal Efficiency |  | CFM | TRM Version 5.0 | 2020-11-12 | 0 | 2.45 | 0 | 1.61 | 0 | 0 | 870 | 1.01 | 20 | Downstream | 0.05 | 1 | 1
COM-DF-SH-545-01 | Current |  | Commercial | Destratification Fans |  | New Construction | space heating | HVLS (High Volume Low Speed) Destratification Fans | 20 ft fan diameter | No destratification fans |  | fan |  | TRM Version 5.0 | 2020-11-12 | 1472 | 0 | 0 | 0 | 0 | 0 | 7961 | 0 | 15 | Downstream | 0.1 | 1 | 1
COM-DF-SH-546-01 | Current |  | Commercial | Destratification Fans |  | Retrofit | space heating | HVLS (High Volume Low Speed) Destratification Fans | 20 ft fan diameter | No destratification fans |  | fan |  | TRM Version 5.0 | 2020-11-12 | 2029 | 0 | 0 | 0 | 0 | 0 | 7961 | 0 | 15 | Downstream | 0.1 | 1 | 1
COM-DF-SH-547-01 | Current |  | Commercial | Destratification Fans |  | New Construction | space heating | HVLS (High Volume Low Speed) Destratification Fans | 24 ft fan diameter | No destratification fans |  | fan |  | TRM Version 5.0 | 2020-11-12 | 2120 | 0 | 0 | 0 | 0 | 0 | 7961 | 0 | 15 | Downstream | 0.1 | 1 | 1
COM-DF-SH-548-01 | Current |  | Commercial | Destratification Fans |  | Retrofit | space heating | HVLS (High Volume Low Speed) Destratification Fans | 24 ft fan diameter | No destratification fans |  | fan |  | TRM Version 5.0 | 2020-11-12 | 2922 | 0 | 0 | 0 | 0 | 0 | 7961 | 0 | 15 | Downstream | 0.1 | 1 | 1
COM-DS-SH-559-01 | Current |  | Commercial | Dock Door Seals |  | Retrofit | space heating | Dock Door Seals | 8' x 10' | Dock door with deteriorated seals |  | unit |  | TRM Version 5.0 | 2020-11-12 | 2041 | 0 | 509 | 0 | 0 | 0 | 1617 | 0 | 10 | Downstream | 0.05 | 1 | 1
COM-DS-SH-563-01 | Current |  | Commercial | Dock Door Seals |  | Retrofit | space heating | Dock Door Seals | 8' x 10' | Dock door without seals |  | unit |  | TRM Version 5.0 | 2020-11-12 | 5087 | 0 | 1269 | 0 | 0 | 0 | 1455 | 0 | 10 | Downstream | 0.05 | 1 | 1
COM-DS-SH-557-01 | Current |  | Commercial | Dock Door Seals |  | Retrofit | space heating | Dock Door Seals | 8' x 8' | Dock door with deteriorated seals |  | unit |  | TRM Version 5.0 | 2020-11-12 | 1897 | 0 | 451 | 0 | 0 | 0 | 1425 | 0 | 10 | Downstream | 0.05 | 1 | 1
COM-DS-SH-561-01 | Current |  | Commercial | Dock Door Seals |  | Retrofit | space heating | Dock Door Seals | 8' x 8' | Dock door without seals |  | unit |  | TRM Version 5.0 | 2020-11-12 | 4853 | 0 | 1155 | 0 | 0 | 0 | 1263 | 0 | 10 | Downstream | 0.05 | 1 | 1
COM-DS-SH-558-01 | Current |  | Commercial | Dock Door Seals |  | Retrofit | space heating | Dock Door Seals | 8' x 9' | Dock door with deteriorated seals |  | unit |  | TRM Version 5.0 | 2020-11-12 | 1977 | 0 | 481 | 0 | 0 | 0 | 1580 | 0 | 10 | Downstream | 0.05 | 1 | 1
COM-DS-SH-562-01 | Current |  | Commercial | Dock Door Seals |  | Retrofit | space heating | Dock Door Seals | 8' x 9' | Dock door without seals |  | unit |  | TRM Version 5.0 | 2020-11-12 | 4988 | 0 | 1214 | 0 | 0 | 0 | 1417 | 0 | 10 | Downstream | 0.05 | 1 | 1
RES-AT-SH-320-01 | Current |  | Residential | Adaptive Thermostat |  | New Construction | space heating | Adaptive Thermostats | Adaptive Thermostat | Programmable Thermostat |  | unit |  | TRM Version 5.0 | 2020-11-12 | 105 | 0 | 206 | 0 | 0 | 0 | 200 | 0 | 15 | Downstream | 0.04 | 1 | 1
RES-AT-SH-323-01 | Current |  | Residential | Adaptive Thermostat |  | Retrofit | space heating | Adaptive Thermostats - Retail Purchase | Adaptive Thermostat | Blended value. Non Programmable and programmable Thermostat |  | unit |  | TRM Version 5.0 | 2020-11-12 | 185 | 0 | 176 | 0 | 0 | 0 | 300 | 0 | 15 | Downstream | 0.04 | 1 | 1
MRS-FA-WH-461-07 | Current |  | Commercial | Faucet Aerator | Multi-residential | Retrofit | water heating | Faucet Aerator | Bathroom, 1.0 GPM | Standard flow bathroom aerator (code compliant) | 2.2 GPM | unit |  | TRM Version 7.0 | 2022-11-30 | 6.65 | 0 | 0 | 0 | 2501 | 0 | 0.6 | 0 | 10 | Downstream | 0.1 | 1 | 1
RES-FA-WH-461-01 | Current |  | Residential | Faucet Aerator |  | Retrofit | water heating | Faucet Aerator | Bathroom, 1.0 GPM | Standard flow bathroom aerator (code compliant) | 2.2 GPM | unit |  | TRM Version 7.0 | 2022-11-30 | 6.65 | 0 | 0 | 0 | 2501 | 0 | 0.6 | 0 | 10 | Downstream | 0.33 | 0.6458 | 1
MRS-FA-WH-460-07 | Current |  | Commercial | Faucet Aerator | Multi-residential | Retrofit | water heating | Faucet Aerator | Bathroom, 1.5 GPM | Standard flow bathroom aerator (code compliant) | 2.2 GPM | unit |  | TRM Version 7.0 | 2022-11-30 | 3.88 | 0 | 0 | 0 | 1459 | 0 | 0.6 | 0 | 10 | Downstream | 0.1 | 1 | 1
RES-FA-WH-460-01 | Current |  | Residential | Faucet Aerator |  | Retrofit | water heating | Faucet Aerator | Bathroom, 1.5 GPM | Standard flow bathroom aerator (code compliant) | 2.2 GPM | unit |  | TRM Version 7.0 | 2022-11-30 | 3.88 | 0 | 0 | 0 | 1459 | 0 | 0.6 | 0 | 10 | Downstream | 0.33 | 0.6458 | 1
RES-TW-WH-576-01 | Current |  | Residential | Tankless Water Heater |  | New Construction/Natural Replacement | water heating | Tankless Water Heater | Condensing Tankless Water Heater, EF = 0.91 | Storage Tank Water Heater, EF=0.67 | EF=0.67 | unit |  | TRM Version 7.0 | 2022-11-30 | 130.7 | 0 | 0 | 0 | 0 | 0 | 2066 | 0 | 20 | Downstream | 0.02 | 1 | 1
COM-CM-SH-496-01 | Current |  | Commercial | Condensing Make Up Air Unit | Commercial | New Construction/Natural Replacement | space heating | Condensing Make Up Air Unit (MUA) - Commercial | Constant Speed | Conventional MUA | 80% Thermal Efficiency |  | CFM | TRM Version 5.0 | 2020-11-12 | 0 | 0.407 | 0 | 0 | 0 | 0 | 870 | 0.66 | 20 | Downstream | 0.05 | 1 | 1
COM-CM-SH-499-01 | Current |  | Commercial | Condensing Make Up Air Unit | Multi-Residential and Long Term Care | New Construction/Natural Replacement | space heating | Condensing Make Up Air Unit (MUA) - Commercial | Constant Speed | Conventional MUA | 80% Thermal Efficiency |  | CFM | TRM Version 5.0 | 2020-11-12 | 0 | 0.919 | 0 | 0 | 0 | 0 | 870 | 0.66 | 20 | Downstream | 0.05 | 1 | 1
RES-HP-SH-565-01 | Current |  | Residential | Heat Reflector Panels |  | Retrofit | space heating | Heat Reflector Panels | Heat reflector panel installed behind radiator | No heat reflector panel installed behind radiator |  | unit |  | TRM Version 5.0 | 2020-11-12 | 143.2 | 0 | 0 | 0 | 0 | 0 | actual cost |  | 25 | Downstream | 0.43 | 1 | 1
RES-TW-WH-575-01 | Current |  | Residential | Tankless Water Heater |  | New Construction/Natural Replacement | water heating | Tankless Water Heater | High Efficiency Non-Condensing Tankless Water Heater, EF = 0.82 | Storage Tank Water Heater, EF=0.67 | EF=0.67 | unit |  | TRM Version 7.0 | 2022-11-30 | 90.7 | 0 | 0 | 0 | 0 | 0 | 1667 | 0 | 20 | Downstream | 0.02 | 1 | 1
RES-SW-WH-574-01 | Current |  | Residential | Storage Water Heater |  | New Construction | water heating | High Efficiency Gas Storage Water Heaters | High efficiency storage tank water heater (Energy Factor of 0.80) | ENERGY STAR power vented storage tank water heater | Energy factor of 0.67 | unit |  | TRM Version 7.0 | 2022-11-30 | 44.1 | 0 | 0 | 0 | 0 | 0 | 545 | 0 | 16 | Downstream | 0.1 | 1 | 1
COM-HRV-SH-336-01 | Current |  | Commercial | Heat Recovery Ventialation | High Use | New Construction/Natural Replacement | space heating | High Efficient 65% Heat Recovery Ventilation High Use Group (Multi-Residential, Health Care, Nursing Homes) | HRV with Minimum 65% Sensible Heat Recovery Effectiveness at 32°F | HRV with Minimum 55% Sensible Heat Recovery Effectiveness as per Ontario Building Code 2017 |  |  | CFM | TRM Version 5.0 | 2020-11-12 | 0 | 0.7 | 0 | 0 | 0 | 0 | 0 | 1 | 14 | Downstream | 0.05 | 1 | 1
COM-HRV-SH-337-01 | Current |  | Commercial | Heat Recovery Ventialation | Low Use | New Construction/Natural Replacement | space heating | High Efficient 65% Heat Recovery Ventilation Low Use Group (Office, Warehouse, School) | HRV with Minimum 65% Sensible Heat Recovery Effectiveness at 32°F | HRV with Minimum 55% Sensible Heat Recovery Effectiveness as per Ontario Building Code 2017 |  |  | CFM | TRM Version 5.0 | 2020-11-12 | 0 | 0.25 | 0 | 0 | 0 | 0 | 0 | 1 | 14 | Downstream | 0.05 | 1 | 1
COM-HRV-SH-338-01 | Current |  | Commercial | Heat Recovery Ventialation | Medium Use | New Construction/Natural Replacement | space heating | High Efficient 65% Heat Recovery Ventilation Medium Use Group (Hotel, Restaurant, Retail) | HRV with Minimum 65% Sensible Heat Recovery Effectiveness at 32°F | HRV with Minimum 55% Sensible Heat Recovery Effectiveness as per Ontario Building Code 2017 |  |  | CFM | TRM Version 5.0 | 2020-11-12 | 0 | 0.39 | 0 | 0 | 0 | 0 | 0 | 1 | 14 | Downstream | 0.05 | 1 | 1
COM-HRV-SH-345-01 | Current |  | Commercial | Heat Recovery Ventialation | Multi-Family, Health Care and Nursing Homes | New Construction/Natural Replacement | space heating | High Efficient 65% Heat Recovery Ventilation High Use Group (Multi-Residential, Health Care, Nursing Homes) | HRV with Minimum 65% Sensible Heat Recovery Effectiveness at 32°F | HRV with Minimum 55% Sensible Heat Recovery Effectiveness as per Ontario Building Code 2017 |  |  | CFM | TRM Version 5.0 | 2020-11-12 | 0 | 0.7 | 0 | 0 | 0 | 0 | 0 | 1 | 14 | Downstream | 0.05 | 1 | 1
COM-HRV-SH-346-01 | Current |  | Commercial | Heat Recovery Ventialation | Hotels | New Construction/Natural Replacement | space heating | High Efficient 65% Heat Recovery Ventilation Medium Use Group (Hotel, Restaurant, Retail) | HRV with Minimum 65% Sensible Heat Recovery Effectiveness at 32°F | HRV with Minimum 55% Sensible Heat Recovery Effectiveness as per Ontario Building Code 2017 |  |  | CFM | TRM Version 5.0 | 2020-11-12 | 0 | 0.5 | 0 | 0 | 0 | 0 | 0 | 1 | 14 | Downstream | 0.05 | 1 | 1
COM-HRV-SH-347-01 | Current |  | Commercial | Heat Recovery Ventialation | Restaurant | New Construction/Natural Replacement | space heating | High Efficient 65% Heat Recovery Ventilation Medium Use Group (Hotel, Restaurant, Retail) | HRV with Minimum 65% Sensible Heat Recovery Effectiveness at 32°F | HRV with Minimum 55% Sensible Heat Recovery Effectiveness as per Ontario Building Code 2017 |  |  | CFM | TRM Version 5.0 | 2020-11-12 | 0 | 0.36 | 0 | 0 | 0 | 0 | 0 | 1 | 14 | Downstream | 0.05 | 1 | 1
COM-HRV-SH-348-01 | Current |  | Commercial | Heat Recovery Ventialation | Retail | New Construction/Natural Replacement | space heating | High Efficient 65% Heat Recovery Ventilation Medium Use Group (Hotel, Restaurant, Retail) | HRV with Minimum 65% Sensible Heat Recovery Effectiveness at 32°F | HRV with Minimum 55% Sensible Heat Recovery Effectiveness as per Ontario Building Code 2017 |  |  | CFM | TRM Version 5.0 | 2020-11-12 | 0 | 0.3 | 0 | 0 | 0 | 0 | 0 | 1 | 14 | Downstream | 0.05 | 1 | 1
COM-HRV-SH-349-01 | Current |  | Commercial | Heat Recovery Ventialation | Office | New Construction/Natural Replacement | space heating | High Efficient 65% Heat Recovery Ventilation Low Use Group (Office, Warehouse, School) | HRV with Minimum 65% Sensible Heat Recovery Effectiveness at 32°F | HRV with Minimum 55% Sensible Heat Recovery Effectiveness as per Ontario Building Code 2017 |  |  | CFM | TRM Version 5.0 | 2020-11-12 | 0 | 0.27 | 0 | 0 | 0 | 0 | 0 | 1 | 14 | Downstream | 0.05 | 1 | 1
COM-HRV-SH-350-01 | Current |  | Commercial | Heat Recovery Ventialation | Warehouse | New Construction/Natural Replacement | space heating | High Efficient 65% Heat Recovery Ventilation Low Use Group (Office, Warehouse, School) | HRV with Minimum 65% Sensible Heat Recovery Effectiveness at 32°F | HRV with Minimum 55% Sensible Heat Recovery Effectiveness as per Ontario Building Code 2017 |  |  | CFM | TRM Version 5.0 | 2020-11-12 | 0 | 0.25 | 0 | 0 | 0 | 0 | 0 | 1 | 14 | Downstream | 0.05 | 1 | 1
COM-HRV-SH-351-01 | Current |  | Commercial | Heat Recovery Ventialation | School | New Construction/Natural Replacement | space heating | High Efficient 65% Heat Recovery Ventilation Low Use Group (Office, Warehouse, School) | HRV with Minimum 65% Sensible Heat Recovery Effectiveness at 32°F | HRV with Minimum 55% Sensible Heat Recovery Effectiveness as per Ontario Building Code 2017 |  |  | CFM | TRM Version 5.0 | 2020-11-12 | 0 | 0.22 | 0 | 0 | 0 | 0 | 0 | 1 | 14 | Downstream | 0.05 | 1 | 1
COM-HRV-SH-339-01 | Current |  | Commercial | Heat Recovery Ventialation | High Use | New Construction/Natural Replacement | space heating | High Efficient 75% Heat Recovery Ventilation High Use Group (Multi-Residential, Health Care, Nursing Homes) | HRV with Minimum 75% Sensible Heat Recovery Effectiveness at 32°F | HRV with Minimum 55% Sensible Heat Recovery Effectiveness as per Ontario Building Code 2017 |  |  | CFM | TRM Version 5.0 | 2020-11-12 | 0 | 1.39 | 0 | 0 | 0 | 0 | 0 | 2 | 14 | Downstream | 0.05 | 1 | 1
COM-HRV-SH-340-01 | Current |  | Commercial | Heat Recovery Ventialation | Low Use | New Construction/Natural Replacement | space heating | High Efficient 75% Heat Recovery Ventilation Low Use Group (Office, Warehouse, School) | HRV with Minimum 75% Sensible Heat Recovery Effectiveness at 32°F | HRV with Minimum 55% Sensible Heat Recovery Effectiveness as per Ontario Building Code 2017 |  |  | CFM | TRM Version 5.0 | 2020-11-12 | 0 | 0.5 | 0 | 0 | 0 | 0 | 0 | 2 | 14 | Downstream | 0.05 | 1 | 1
COM-HRV-SH-341-01 | Current |  | Commercial | Heat Recovery Ventialation | Medium Use | New Construction/Natural Replacement | space heating | High Efficient 75% Heat Recovery Ventilation Medium Use Group (Hotel, Restaurant, Retail) | HRV with Minimum 75% Sensible Heat Recovery Effectiveness at 32°F | HRV with Minimum 55% Sensible Heat Recovery Effectiveness as per Ontario Building Code 2017 |  |  | CFM | TRM Version 5.0 | 2020-11-12 | 0 | 0.78 | 0 | 0 | 0 | 0 | 0 | 2 | 14 | Downstream | 0.05 | 1 | 1
COM-HRV-SH-352-01 | Current |  | Commercial | Heat Recovery Ventialation | Multi-Family, Health Care and Nursing Homes | New Construction/Natural Replacement | space heating | High Efficient 75% Heat Recovery Ventilation High Use Group (Multi-Residential, Health Care, Nursing Homes) | HRV with Minimum 75% Sensible Heat Recovery Effectiveness at 32°F | HRV with Minimum 55% Sensible Heat Recovery Effectiveness as per Ontario Building Code 2017 |  |  | CFM | TRM Version 5.0 | 2020-11-12 | 0 | 1.39 | 0 | 0 | 0 | 0 | 0 | 2 | 14 | Downstream | 0.05 | 1 | 1
COM-HRV-SH-353-01 | Current |  | Commercial | Heat Recovery Ventialation | Hotels | New Construction/Natural Replacement | space heating | High Efficient 75% Heat Recovery Ventilation Medium Use Group (Hotel, Restaurant, Retail) | HRV with Minimum 75% Sensible Heat Recovery Effectiveness at 32°F | HRV with Minimum 55% Sensible Heat Recovery Effectiveness as per Ontario Building Code 2017 |  |  | CFM | TRM Version 5.0 | 2020-11-12 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 2 | 14 | Downstream | 0.05 | 1 | 1
COM-HRV-SH-354-01 | Current |  | Commercial | Heat Recovery Ventialation | Restaurant | New Construction/Natural Replacement | space heating | High Efficient 75% Heat Recovery Ventilation Medium Use Group (Hotel, Restaurant, Retail) | HRV with Minimum 75% Sensible Heat Recovery Effectiveness at 32°F | HRV with Minimum 55% Sensible Heat Recovery Effectiveness as per Ontario Building Code 2017 |  |  | CFM | TRM Version 5.0 | 2020-11-12 | 0 | 0.72 | 0 | 0 | 0 | 0 | 0 | 2 | 14 | Downstream | 0.05 | 1 | 1
COM-HRV-SH-355-01 | Current |  | Commercial | Heat Recovery Ventialation | Retail | New Construction/Natural Replacement | space heating | High Efficient 75% Heat Recovery Ventilation Medium Use Group (Hotel, Restaurant, Retail) | HRV with Minimum 75% Sensible Heat Recovery Effectiveness at 32°F | HRV with Minimum 55% Sensible Heat Recovery Effectiveness as per Ontario Building Code 2017 |  |  | CFM | TRM Version 5.0 | 2020-11-12 | 0 | 0.61 | 0 | 0 | 0 | 0 | 0 | 2 | 14 | Downstream | 0.05 | 1 | 1
COM-HRV-SH-356-01 | Current |  | Commercial | Heat Recovery Ventialation | Office | New Construction/Natural Replacement | space heating | High Efficient 75% Heat Recovery Ventilation Low Use Group (Office, Warehouse, School) | HRV with Minimum 75% Sensible Heat Recovery Effectiveness at 32°F | HRV with Minimum 55% Sensible Heat Recovery Effectiveness as per Ontario Building Code 2017 |  |  | CFM | TRM Version 5.0 | 2020-11-12 | 0 | 0.53 | 0 | 0 | 0 | 0 | 0 | 2 | 14 | Downstream | 0.05 | 1 | 1
COM-HRV-SH-357-01 | Current |  | Commercial | Heat Recovery Ventialation | Warehouse | New Construction/Natural Replacement | space heating | High Efficient 75% Heat Recovery Ventilation Low Use Group (Office, Warehouse, School) | HRV with Minimum 75% Sensible Heat Recovery Effectiveness at 32°F | HRV with Minimum 55% Sensible Heat Recovery Effectiveness as per Ontario Building Code 2017 |  |  | CFM | TRM Version 5.0 | 2020-11-12 | 0 | 0.51 | 0 | 0 | 0 | 0 | 0 | 2 | 14 | Downstream | 0.05 | 1 | 1
COM-HRV-SH-358-01 | Current |  | Commercial | Heat Recovery Ventialation | School | New Construction/Natural Replacement | space heating | High Efficient 75% Heat Recovery Ventilation Low Use Group (Office, Warehouse, School) | HRV with Minimum 75% Sensible Heat Recovery Effectiveness at 32°F | HRV with Minimum 55% Sensible Heat Recovery Effectiveness as per Ontario Building Code 2017 |  |  | CFM | TRM Version 5.0 | 2020-11-12 | 0 | 0.45 | 0 | 0 | 0 | 0 | 0 | 2 | 14 | Downstream | 0.05 | 1 | 1
COM-HRV-SH-342-01 | Current |  | Commercial | Heat Recovery Ventialation | High Use | New Construction/Natural Replacement | space heating | High Efficient 85% Heat Recovery Ventilation High Use Group (Multi-Residential, Health Care, Nursing Homes) | HRV with Minimum 85% Sensible Heat Recovery Effectiveness at 32°F | HRV with Minimum 55% Sensible Heat Recovery Effectiveness as per Ontario Building Code 2017 |  |  | CFM | TRM Version 5.0 | 2020-11-12 | 0 | 2.09 | 0 | 0 | 0 | 0 | 0 | 3 | 14 | Downstream | 0.05 | 1 | 1
COM-HRV-SH-343-01 | Current |  | Commercial | Heat Recovery Ventialation | Low Use | New Construction/Natural Replacement | space heating | High Efficient 85% Heat Recovery Ventilation Low Use Group (Office, Warehouse, School) | HRV with Minimum 85% Sensible Heat Recovery Effectiveness at 32°F | HRV with Minimum 55% Sensible Heat Recovery Effectiveness as per Ontario Building Code 2017 |  |  | CFM | TRM Version 5.0 | 2020-11-12 | 0 | 0.74 | 0 | 0 | 0 | 0 | 0 | 3 | 14 | Downstream | 0.05 | 1 | 1
COM-HRV-SH-344-01 | Current |  | Commercial | Heat Recovery Ventialation | Medium Use | New Construction/Natural Replacement | space heating | High Efficient 85% Heat Recovery Ventilation Medium Use Group (Hotel, Restaurant, Retail) | HRV with Minimum 85% Sensible Heat Recovery Effectiveness at 32°F | HRV with Minimum 55% Sensible Heat Recovery Effectiveness as per Ontario Building Code 2017 |  |  | CFM | TRM Version 5.0 | 2020-11-12 | 0 | 1.16 | 0 | 0 | 0 | 0 | 0 | 3 | 14 | Downstream | 0.05 | 1 | 1
COM-HRV-SH-359-01 | Current |  | Commercial | Heat Recovery Ventialation | Multi-Family, Health Care and Nursing Homes | New Construction/Natural Replacement | space heating | High Efficient 85% Heat Recovery Ventilation High Use Group (Multi-Residential, Health Care, Nursing Homes) | HRV with Minimum 85% Sensible Heat Recovery Effectiveness at 32°F | HRV with Minimum 55% Sensible Heat Recovery Effectiveness as per Ontario Building Code 2017 |  |  | CFM | TRM Version 5.0 | 2020-11-12 | 0 | 2.09 | 0 | 0 | 0 | 0 | 0 | 3 | 14 | Downstream | 0.05 | 1 | 1
COM-HRV-SH-360-01 | Current |  | Commercial | Heat Recovery Ventialation | Hotels | New Construction/Natural Replacement | space heating | High Efficient 85% Heat Recovery Ventilation Medium Use Group (Hotel, Restaurant, Retail) | HRV with Minimum 85% Sensible Heat Recovery Effectiveness at 32°F | HRV with Minimum 55% Sensible Heat Recovery Effectiveness as per Ontario Building Code 2017 |  |  | CFM | TRM Version 5.0 | 2020-11-12 | 0 | 1.49 | 0 | 0 | 0 | 0 | 0 | 3 | 14 | Downstream | 0.05 | 1 | 1
COM-HRV-SH-361-01 | Current |  | Commercial | Heat Recovery Ventialation | Restaurant | New Construction/Natural Replacement | space heating | High Efficient 85% Heat Recovery Ventilation Medium Use Group (Hotel, Restaurant, Retail) | HRV with Minimum 85% Sensible Heat Recovery Effectiveness at 32°F | HRV with Minimum 55% Sensible Heat Recovery Effectiveness as per Ontario Building Code 2017 |  |  | CFM | TRM Version 5.0 | 2020-11-12 | 0 | 1.08 | 0 | 0 | 0 | 0 | 0 | 3 | 14 | Downstream | 0.05 | 1 | 1
COM-HRV-SH-362-01 | Current |  | Commercial | Heat Recovery Ventialation | Retail | New Construction/Natural Replacement | space heating | High Efficient 85% Heat Recovery Ventilation Medium Use Group (Hotel, Restaurant, Retail) | HRV with Minimum 85% Sensible Heat Recovery Effectiveness at 32°F | HRV with Minimum 55% Sensible Heat Recovery Effectiveness as per Ontario Building Code 2017 |  |  | CFM | TRM Version 5.0 | 2020-11-12 | 0 | 0.91 | 0 | 0 | 0 | 0 | 0 | 3 | 14 | Downstream | 0.05 | 1 | 1
COM-HRV-SH-363-01 | Current |  | Commercial | Heat Recovery Ventialation | Office | New Construction/Natural Replacement | space heating | High Efficient 85% Heat Recovery Ventilation Low Use Group (Office, Warehouse, School) | HRV with Minimum 85% Sensible Heat Recovery Effectiveness at 32°F | HRV with Minimum 55% Sensible Heat Recovery Effectiveness as per Ontario Building Code 2017 |  |  | CFM | TRM Version 5.0 | 2020-11-12 | 0 | 0.8 | 0 | 0 | 0 | 0 | 0 | 3 | 14 | Downstream | 0.05 | 1 | 1
COM-HRV-SH-364-01 | Current |  | Commercial | Heat Recovery Ventialation | Warehouse | New Construction/Natural Replacement | space heating | High Efficient 85% Heat Recovery Ventilation Low Use Group (Office, Warehouse, School) | HRV with Minimum 85% Sensible Heat Recovery Effectiveness at 32°F | HRV with Minimum 55% Sensible Heat Recovery Effectiveness as per Ontario Building Code 2017 |  |  | CFM | TRM Version 5.0 | 2020-11-12 | 0 | 0.76 | 0 | 0 | 0 | 0 | 0 | 3 | 14 | Downstream | 0.05 | 1 | 1
COM-HRV-SH-365-01 | Current |  | Commercial | Heat Recovery Ventialation | School | New Construction/Natural Replacement | space heating | High Efficient 85% Heat Recovery Ventilation Low Use Group (Office, Warehouse, School) | HRV with Minimum 85% Sensible Heat Recovery Effectiveness at 32°F | HRV with Minimum 55% Sensible Heat Recovery Effectiveness as per Ontario Building Code 2017 |  |  | CFM | TRM Version 5.0 | 2020-11-12 | 0 | 0.67 | 0 | 0 | 0 | 0 | 0 | 3 | 14 | Downstream | 0.05 | 1 | 1
MRS-FA-WH-462-07 | Current |  | Commercial | Faucet Aerator | Multi-residential | Retrofit | water heating | Faucet Aerator | Kitchen, 1.0 GPM | Standard flow kitchen aerator (code compliant) | 2.2 GPM | unit |  | TRM Version 7.0 | 2022-11-30 | 20.57 | 0 | 0 | 0 | 7742 | 0 | 1.14 | 0 | 10 | Downstream | 0.1 | 1 | 1
RES-FA-WH-462-01 | Current |  | Residential | Faucet Aerator |  | Retrofit | water heating | Faucet Aerator | Kitchen, 1.0 GPM | Standard flow kitchen aerator (code compliant) | 2.2 GPM | unit |  | TRM Version 7.0 | 2022-11-30 | 20.57 | 0 | 0 | 0 | 7742 | 0 | 1.14 | 0 | 10 | Downstream | 0.33 | 0.6768 | 1
MRS-FA-WH-463-07 | Current |  | Commercial | Faucet Aerator | Multi-residential | Retrofit | water heating | Faucet Aerator | Kitchen, 1.5 GPM | Standard flow kitchen aerator (code compliant) | 2.2 GPM | unit |  | TRM Version 7.0 | 2022-11-30 | 12 | 0 | 0 | 0 | 4516 | 0 | 1.14 | 0 | 10 | Downstream | 0.1 | 1 | 1
RES-FA-WH-463-01 | Current |  | Residential | Faucet Aerator |  | Retrofit | water heating | Faucet Aerator | Kitchen, 1.5 GPM | Standard flow kitchen aerator (code compliant) | 2.2 GPM | unit |  | TRM Version 7.0 | 2022-11-30 | 12 | 0 | 0 | 0 | 4516 | 0 | 1.14 | 0 | 10 | Downstream | 0.33 | 0.6768 | 1
COM-ERV-SH-380-01 | Current |  | Commercial | Energy Recovery Ventilation | High Use Group | New Construction/Natural Replacement | space heating | High Efficient 65% Energy Recovery Ventilation High Use Group (Multi-Residential, Health Care, Nursing Homes) | Minimum 65% Sensible Heat Recovery Effectiveness and 63% Total Energy Recovery Effectiveness at 32°F | Minimum 55% Energy Recovery Effectiveness as per Ontario Building Code 2017 |  |  | CFM | TRM Version 5.0 | 2020-11-12 | 0 | 0.85 | 0 | 0 | 0 | 0 | 0 | 1 | 14 | Downstream | 0.7 | 1 | 1
COM-ERV-SH-381-01 | Current |  | Commercial | Energy Recovery Ventilation | Medium Use Group | New Construction/Natural Replacement | space heating | High Efficient 65% Energy Recovery Ventilation Medium Use Group (Hotel, Restaurant, Retail) | Minimum 65% Sensible Heat Recovery Effectiveness and 63% Total Energy Recovery Effectiveness at 32°F | Minimum 55% Energy Recovery Effectiveness as per Ontario Building Code 2017 |  |  | CFM | TRM Version 5.0 | 2020-11-12 | 0 | 0.47 | 0 | 0 | 0 | 0 | 0 | 1 | 14 | Downstream | 0.7 | 1 | 1
COM-ERV-SH-382-01 | Current |  | Commercial | Energy Recovery Ventilation | Low Use Group | New Construction/Natural Replacement | space heating | High Efficient 65% Energy Recovery Ventilation Low Use Group (Office, Warehouse, School) | Minimum 65% Sensible Heat Recovery Effectiveness and 63% Total Energy Recovery Effectiveness at 32°F | Minimum 55% Energy Recovery Effectiveness as per Ontario Building Code 2017 |  |  | CFM | TRM Version 5.0 | 2020-11-12 | 0 | 0.3 | 0 | 0 | 0 | 0 | 0 | 1 | 14 | Downstream | 0.7 | 1 | 1
COM-ERV-SH-383-01 | Current |  | Commercial | Energy Recovery Ventilation | Multi-Residential, Health Care, Nursing Homes | New Construction/Natural Replacement | space heating | High Efficient 65% Energy Recovery Ventilation High Use Group (Multi-Residential, Health Care, Nursing Homes) | Minimum 65% Sensible Heat Recovery Effectiveness and 63% Total Energy Recovery Effectiveness at 32°F | Minimum 55% Energy Recovery Effectiveness as per Ontario Building Code 2017 |  |  | CFM | TRM Version 5.0 | 2020-11-12 | 0 | 0.85 | 0 | 0 | 0 | 0 | 0 | 1 | 14 | Downstream | 0.7 | 1 | 1
COM-ERV-SH-384-01 | Current |  | Commercial | Energy Recovery Ventilation | Hotel | New Construction/Natural Replacement | space heating | High Efficient 65% Energy Recovery Ventilation Medium Use Group (Hotel, Restaurant, Retail) | Minimum 65% Sensible Heat Recovery Effectiveness and 63% Total Energy Recovery Effectiveness at 32°F | Minimum 55% Energy Recovery Effectiveness as per Ontario Building Code 2017 |  |  | CFM | TRM Version 5.0 | 2020-11-12 | 0 | 0.61 | 0 | 0 | 0 | 0 | 0 | 1 | 14 | Downstream | 0.7 | 1 | 1
COM-ERV-SH-385-01 | Current |  | Commercial | Energy Recovery Ventilation | Restaurant | New Construction/Natural Replacement | space heating | High Efficient 65% Energy Recovery Ventilation Medium Use Group (Hotel, Restaurant, Retail) | Minimum 65% Sensible Heat Recovery Effectiveness and 63% Total Energy Recovery Effectiveness at 32°F | Minimum 55% Energy Recovery Effectiveness as per Ontario Building Code 2017 |  |  | CFM | TRM Version 5.0 | 2020-11-12 | 0 | 0.44 | 0 | 0 | 0 | 0 | 0 | 1 | 14 | Downstream | 0.7 | 1 | 1
COM-ERV-SH-386-01 | Current |  | Commercial | Energy Recovery Ventilation | Retail | New Construction/Natural Replacement | space heating | High Efficient 65% Energy Recovery Ventilation Medium Use Group (Hotel, Restaurant, Retail) | Minimum 65% Sensible Heat Recovery Effectiveness and 63% Total Energy Recovery Effectiveness at 32°F | Minimum 55% Energy Recovery Effectiveness as per Ontario Building Code 2017 |  |  | CFM | TRM Version 5.0 | 2020-11-12 | 0 | 0.37 | 0 | 0 | 0 | 0 | 0 | 1 | 14 | Downstream | 0.7 | 1 | 1
COM-ERV-SH-387-01 | Current |  | Commercial | Energy Recovery Ventilation | Office | New Construction/Natural Replacement | space heating | High Efficient 65% Energy Recovery Ventilation Low Use Group (Office, Warehouse, School) | Minimum 65% Sensible Heat Recovery Effectiveness and 63% Total Energy Recovery Effectiveness at 32°F | Minimum 55% Energy Recovery Effectiveness as per Ontario Building Code 2017 |  |  | CFM | TRM Version 5.0 | 2020-11-12 | 0 | 0.32 | 0 | 0 | 0 | 0 | 0 | 1 | 14 | Downstream | 0.7 | 1 | 1
COM-ERV-SH-388-01 | Current |  | Commercial | Energy Recovery Ventilation | Warehouse | New Construction/Natural Replacement | space heating | High Efficient 65% Energy Recovery Ventilation Low Use Group (Office, Warehouse, School) | Minimum 65% Sensible Heat Recovery Effectiveness and 63% Total Energy Recovery Effectiveness at 32°F | Minimum 55% Energy Recovery Effectiveness as per Ontario Building Code 2017 |  |  | CFM | TRM Version 5.0 | 2020-11-12 | 0 | 0.31 | 0 | 0 | 0 | 0 | 0 | 1 | 14 | Downstream | 0.7 | 1 | 1
COM-ERV-SH-389-01 | Current |  | Commercial | Energy Recovery Ventilation | School | New Construction/Natural Replacement | space heating | High Efficient 65% Energy Recovery Ventilation Low Use Group (Office, Warehouse, School) | Minimum 65% Sensible Heat Recovery Effectiveness and 63% Total Energy Recovery Effectiveness at 32°F | Minimum 55% Energy Recovery Effectiveness as per Ontario Building Code 2017 |  |  | CFM | TRM Version 5.0 | 2020-11-12 | 0 | 0.27 | 0 | 0 | 0 | 0 | 0 | 1 | 14 | Downstream | 0.7 | 1 | 1
COM-ERV-SH-380-05 | Current |  | Commercial | Energy Recovery Ventilation | High Use Group | New Construction/Natural Replacement | space heating | High Efficient 75% Energy Recovery Ventilation High Use Group (Multi-Residential, Health Care, Nursing Homes) | Minimum 75% Sensible Heat Recovery Effectiveness and 73% Total Energy Recovery Effectiveness at 32°F | Minimum 55% Energy Recovery Effectiveness as per Ontario Building Code 2017 |  |  | CFM | TRM Version 5.0 | 2020-11-12 | 0 | 1.7 | 0 | 0 | 0 | 0 | 0 | 2 | 14 | Downstream | 0.7 | 1 | 1
COM-ERV-SH-381-05 | Current |  | Commercial | Energy Recovery Ventilation | Medium Use Group | New Construction/Natural Replacement | space heating | High Efficient 75% Energy Recovery Ventilation Medium Use Group (Hotel, Restaurant, and Retail) | Minimum 75% Sensible Heat Recovery Effectiveness and 73% Total Energy Recovery Effectiveness at 32°F | Minimum 55% Energy Recovery Effectiveness as per Ontario Building Code 2017 |  |  | CFM | TRM Version 5.0 | 2020-11-12 | 0 | 0.95 | 0 | 0 | 0 | 0 | 0 | 2 | 14 | Downstream | 0.7 | 1 | 1
COM-ERV-SH-382-05 | Current |  | Commercial | Energy Recovery Ventilation | Low Use Group | New Construction/Natural Replacement | space heating | High Efficient 75% Energy Recovery Ventilation Low Use Group (Office, Warehouse, School) | Minimum 75% Sensible Heat Recovery Effectiveness and 73% Total Energy Recovery Effectiveness at 32°F | Minimum 55% Energy Recovery Effectiveness as per Ontario Building Code 2017 |  |  | CFM | TRM Version 5.0 | 2020-11-12 | 0 | 0.61 | 0 | 0 | 0 | 0 | 0 | 2 | 14 | Downstream | 0.7 | 1 | 1
COM-ERV-SH-383-05 | Current |  | Commercial | Energy Recovery Ventilation | Multi-Residential, Health Care, Nursing Homes | New Construction/Natural Replacement | space heating | High Efficient 75% Energy Recovery Ventilation High Use Group (Multi-Residential, Health Care, Nursing Homes) | Minimum 75% Sensible Heat Recovery Effectiveness and 73% Total Energy Recovery Effectiveness at 32°F | Minimum 55% Energy Recovery Effectiveness as per Ontario Building Code 2017 |  |  | CFM | TRM Version 5.0 | 2020-11-12 | 0 | 1.7 | 0 | 0 | 0 | 0 | 0 | 2 | 14 | Downstream | 0.7 | 1 | 1
COM-ERV-SH-384-05 | Current |  | Commercial | Energy Recovery Ventilation | Hotel | New Construction/Natural Replacement | space heating | High Efficient 75% Energy Recovery Ventilation Medium Use Group (Hotel, Restaurant, and Retail) | Minimum 75% Sensible Heat Recovery Effectiveness and 73% Total Energy Recovery Effectiveness at 32°F | Minimum 55% Energy Recovery Effectiveness as per Ontario Building Code 2017 |  |  | CFM | TRM Version 5.0 | 2020-11-12 | 0 | 1.22 | 0 | 0 | 0 | 0 | 0 | 2 | 14 | Downstream | 0.7 | 1 | 1
COM-ERV-SH-385-05 | Current |  | Commercial | Energy Recovery Ventilation | Restaurant | New Construction/Natural Replacement | space heating | High Efficient 75% Energy Recovery Ventilation Medium Use Group (Hotel, Restaurant, and Retail) | Minimum 75% Sensible Heat Recovery Effectiveness and 73% Total Energy Recovery Effectiveness at 32°F | Minimum 55% Energy Recovery Effectiveness as per Ontario Building Code 2017 |  |  | CFM | TRM Version 5.0 | 2020-11-12 | 0 | 0.88 | 0 | 0 | 0 | 0 | 0 | 2 | 14 | Downstream | 0.7 | 1 | 1
COM-ERV-SH-386-05 | Current |  | Commercial | Energy Recovery Ventilation | Retail | New Construction/Natural Replacement | space heating | High Efficient 75% Energy Recovery Ventilation Medium Use Group (Hotel, Restaurant, and Retail) | Minimum 75% Sensible Heat Recovery Effectiveness and 73% Total Energy Recovery Effectiveness at 32°F | Minimum 55% Energy Recovery Effectiveness as per Ontario Building Code 2017 |  |  | CFM | TRM Version 5.0 | 2020-11-12 | 0 | 0.74 | 0 | 0 | 0 | 0 | 0 | 2 | 14 | Downstream | 0.7 | 1 | 1
COM-ERV-SH-387-05 | Current |  | Commercial | Energy Recovery Ventilation | Office | New Construction/Natural Replacement | space heating | High Efficient 75% Energy Recovery Ventilation Low Use Group (Office, Warehouse, School) | Minimum 75% Sensible Heat Recovery Effectiveness and 73% Total Energy Recovery Effectiveness at 32°F | Minimum 55% Energy Recovery Effectiveness as per Ontario Building Code 2017 |  |  | CFM | TRM Version 5.0 | 2020-11-12 | 0 | 0.65 | 0 | 0 | 0 | 0 | 0 | 2 | 14 | Downstream | 0.7 | 1 | 1
COM-ERV-SH-388-05 | Current |  | Commercial | Energy Recovery Ventilation | Warehouse | New Construction/Natural Replacement | space heating | High Efficient 75% Energy Recovery Ventilation Low Use Group (Office, Warehouse, School) | Minimum 75% Sensible Heat Recovery Effectiveness and 73% Total Energy Recovery Effectiveness at 32°F | Minimum 55% Energy Recovery Effectiveness as per Ontario Building Code 2017 |  |  | CFM | TRM Version 5.0 | 2020-11-12 | 0 | 0.62 | 0 | 0 | 0 | 0 | 0 | 2 | 14 | Downstream | 0.7 | 1 | 1
COM-ERV-SH-389-05 | Current |  | Commercial | Energy Recovery Ventilation | School | New Construction/Natural Replacement | space heating | High Efficient 75% Energy Recovery Ventilation Low Use Group (Office, Warehouse, School) | Minimum 75% Sensible Heat Recovery Effectiveness and 73% Total Energy Recovery Effectiveness at 32°F | Minimum 55% Energy Recovery Effectiveness as per Ontario Building Code 2017 |  |  | CFM | TRM Version 5.0 | 2020-11-12 | 0 | 0.55 | 0 | 0 | 0 | 0 | 0 | 2 | 14 | Downstream | 0.7 | 1 | 1
COM-ERV-SH-390-01 | Current |  | Commercial | Energy Recovery Ventilation | High Use Group | New Construction/Natural Replacement | space heating | High Efficient 85% Energy Recovery Ventilation High Use Group (Multi-Residential, Health Care, Nursing Homes) | Minimum 85% Sensible Heat Recovery Effectiveness and 83% Total Energy Recovery Effectiveness at 32°F | Minimum 55% Energy Recovery Effectiveness as per Ontario Building Code 2017 |  |  | CFM | TRM Version 5.0 | 2020-11-12 | 0 | 2.56 | 0 | 0 | 0 | 0 | 0 | 3 | 14 | Downstream | 0.7 | 1 | 1
COM-ERV-SH-391-01 | Current |  | Commercial | Energy Recovery Ventilation | Medium Use Group | New Construction/Natural Replacement | space heating | High Efficient 85% Energy Recovery Ventilation Medium Use Group (Hotel, Restaurant, Retail) | Minimum 85% Sensible Heat Recovery Effectiveness and 83% Total Energy Recovery Effectiveness at 32°F | Minimum 55% Energy Recovery Effectiveness as per Ontario Building Code 2017 |  |  | CFM | TRM Version 5.0 | 2020-11-12 | 0 | 1.42 | 0 | 0 | 0 | 0 | 0 | 3 | 14 | Downstream | 0.7 | 1 | 1
COM-ERV-SH-392-01 | Current |  | Commercial | Energy Recovery Ventilation | Low Use Group | New Construction/Natural Replacement | space heating | High Efficient 85% Energy Recovery Ventilation Low Use Group (Office, Warehouse, School) | Minimum 85% Sensible Heat Recovery Effectiveness and 83% Total Energy Recovery Effectiveness at 32°F | Minimum 55% Energy Recovery Effectiveness as per Ontario Building Code 2017 |  |  | CFM | TRM Version 5.0 | 2020-11-12 | 0 | 0.91 | 0 | 0 | 0 | 0 | 0 | 3 | 14 | Downstream | 0.7 | 1 | 1
COM-ERV-SH-393-01 | Current |  | Commercial | Energy Recovery Ventilation | Multi-Residential, Health Care, Nursing Homes | New Construction/Natural Replacement | space heating | High Efficient 85% Energy Recovery Ventilation High Use Group (Multi-Residential, Health Care, Nursing Homes) | Minimum 85% Sensible Heat Recovery Effectiveness and 83% Total Energy Recovery Effectiveness at 32°F | Minimum 55% Energy Recovery Effectiveness as per Ontario Building Code 2017 |  |  | CFM | TRM Version 5.0 | 2020-11-12 | 0 | 2.56 | 0 | 0 | 0 | 0 | 0 | 3 | 14 | Downstream | 0.7 | 1 | 1
COM-ERV-SH-394-01 | Current |  | Commercial | Energy Recovery Ventilation | Hotel | New Construction/Natural Replacement | space heating | High Efficient 85% Energy Recovery Ventilation Medium Use Group (Hotel, Restaurant, Retail) | Minimum 85% Sensible Heat Recovery Effectiveness and 83% Total Energy Recovery Effectiveness at 32°F | Minimum 55% Energy Recovery Effectiveness as per Ontario Building Code 2017 |  |  | CFM | TRM Version 5.0 | 2020-11-12 | 0 | 1.83 | 0 | 0 | 0 | 0 | 0 | 3 | 14 | Downstream | 0.7 | 1 | 1
COM-ERV-SH-395-01 | Current |  | Commercial | Energy Recovery Ventilation | Restaurant | New Construction/Natural Replacement | space heating | High Efficient 85% Energy Recovery Ventilation Medium Use Group (Hotel, Restaurant, Retail) | Minimum 85% Sensible Heat Recovery Effectiveness and 83% Total Energy Recovery Effectiveness at 32°F | Minimum 55% Energy Recovery Effectiveness as per Ontario Building Code 2017 |  |  | CFM | TRM Version 5.0 | 2020-11-12 | 0 | 1.32 | 0 | 0 | 0 | 0 | 0 | 3 | 14 | Downstream | 0.7 | 1 | 1
COM-ERV-SH-396-01 | Current |  | Commercial | Energy Recovery Ventilation | Retail | New Construction/Natural Replacement | space heating | High Efficient 85% Energy Recovery Ventilation Medium Use Group (Hotel, Restaurant, Retail) | Minimum 85% Sensible Heat Recovery Effectiveness and 83% Total Energy Recovery Effectiveness at 32°F | Minimum 55% Energy Recovery Effectiveness as per Ontario Building Code 2017 |  |  | CFM | TRM Version 5.0 | 2020-11-12 | 0 | 1.11 | 0 | 0 | 0 | 0 | 0 | 3 | 14 | Downstream | 0.7 | 1 | 1
COM-ERV-SH-397-01 | Current |  | Commercial | Energy Recovery Ventilation | Office | New Construction/Natural Replacement | space heating | High Efficient 85% Energy Recovery Ventilation Low Use Group (Office, Warehouse, School) | Minimum 85% Sensible Heat Recovery Effectiveness and 83% Total Energy Recovery Effectiveness at 32°F | Minimum 55% Energy Recovery Effectiveness as per Ontario Building Code 2017 |  |  | CFM | TRM Version 5.0 | 2020-11-12 | 0 | 0.97 | 0 | 0 | 0 | 0 | 0 | 3 | 14 | Downstream | 0.7 | 1 | 1
COM-ERV-SH-398-01 | Current |  | Commercial | Energy Recovery Ventilation | Warehouse | New Construction/Natural Replacement | space heating | High Efficient 85% Energy Recovery Ventilation Low Use Group (Office, Warehouse, School) | Minimum 85% Sensible Heat Recovery Effectiveness and 83% Total Energy Recovery Effectiveness at 32°F | Minimum 55% Energy Recovery Effectiveness as per Ontario Building Code 2017 |  |  | CFM | TRM Version 5.0 | 2020-11-12 | 0 | 0.93 | 0 | 0 | 0 | 0 | 0 | 3 | 14 | Downstream | 0.7 | 1 | 1
COM-ERV-SH-399-01 | Current |  | Commercial | Energy Recovery Ventilation | School | New Construction/Natural Replacement | space heating | High Efficient 85% Energy Recovery Ventilation Low Use Group (Office, Warehouse, School) | Minimum 85% Sensible Heat Recovery Effectiveness and 83% Total Energy Recovery Effectiveness at 32°F | Minimum 55% Energy Recovery Effectiveness as per Ontario Building Code 2017 |  |  | CFM | TRM Version 5.0 | 2020-11-12 | 0 | 0.82 | 0 | 0 | 0 | 0 | 0 | 3 | 14 | Downstream | 0.7 | 1 | 1
COM-AC-SH-481-01 | Current |  | Commercial | Air Curtain |  | New Construction/Retrofit | space heating | Air Curtains | Pedestrian Doors 2 x (3' x 7') | Exterior doorway without vestibule or air curtain |  | unit |  | TRM Version 5.0 | 2020-11-12 | 1690 | 0 | 212 | 0 | 0 | 0 | 3150 | 0 | 15 | Downstream | 0.5 | 1 | 1
COM-AC-SH-487-01 | Current |  | Commercial | Air Curtain |  | New Construction/Retrofit | space heating | Air Curtains | Pedestrian Doors 2 x (3' x 7') | Exterior doorway with vestibule and no air curtain |  | unit |  | TRM Version 5.0 | 2020-11-12 | 1082 | 0 | 124 | 0 | 0 | 0 | 3150 | 0 | 15 | Downstream | 0.5 | 1 | 1
COM-AC-SH-483-01 | Current |  | Commercial | Air Curtain |  | New Construction/Retrofit | space heating | Air Curtains | Pedestrian Doors 2 x (6' x 8') | Exterior doorway without vestibule or air curtain |  | unit |  | TRM Version 5.0 | 2020-11-12 | 3774 | 0 | 431 | 0 | 0 | 0 | 3350 | 0 | 15 | Downstream | 0.5 | 1 | 1
COM-AC-SH-489-01 | Current |  | Commercial | Air Curtain |  | New Construction/Retrofit | space heating | Air Curtains | Pedestrian Doors 2 x (6' x 8') | Exterior doorway with vestibule and no air curtain |  | unit |  | TRM Version 5.0 | 2020-11-12 | 2416 | 0 | 232 | 0 | 0 | 0 | 3350 | 0 | 15 | Downstream | 0.5 | 1 | 1
COM-AC-SH-482-01 | Current |  | Commercial | Air Curtain |  | New Construction/Retrofit | space heating | Air Curtains | Pedestrian Doors 2 x (6' x 7') | Exterior doorway without vestibule or air curtain |  | unit |  | TRM Version 5.0 | 2020-11-12 | 3380 | 0 | 367 | 0 | 0 | 0 | 3350 | 0 | 15 | Downstream | 0.5 | 1 | 1
COM-AC-SH-488-01 | Current |  | Commercial | Air Curtain |  | New Construction/Retrofit | space heating | Air Curtains | Pedestrian Doors 2 x (6' x 7') | Exterior doorway with vestibule and no air curtain |  | unit |  | TRM Version 5.0 | 2020-11-12 | 2164 | 0 | 192 | 0 | 0 | 0 | 3350 | 0 | 15 | Downstream | 0.5 | 1 | 1
COM-AC-SH-478-01 | Current |  | Commercial | Air Curtain |  | New Construction/Retrofit | space heating | Air Curtains | Pedestrian Doors 3' x 7' | Exterior doorway without vestibule or air curtain |  | unit |  | TRM Version 5.0 | 2020-11-12 | 845 | 0 | 106 | 0 | 0 | 0 | 1645 | 0 | 15 | Downstream | 0.5 | 1 | 1
COM-AC-SH-484-01 | Current |  | Commercial | Air Curtain |  | New Construction/Retrofit | space heating | Air Curtains | Pedestrian Doors 3' x 7' | Exterior doorway with vestibule and no air curtain |  | unit |  | TRM Version 5.0 | 2020-11-12 | 541 | 0 | 62 | 0 | 0 | 0 | 1645 | 0 | 15 | Downstream | 0.5 | 1 | 1
COM-AC-SH-479-01 | Current |  | Commercial | Air Curtain |  | New Construction/Retrofit | space heating | Air Curtains | Pedestrian Doors 6' x 7' | Exterior doorway without vestibule or air curtain |  | unit |  | TRM Version 5.0 | 2020-11-12 | 1690 | 0 | 184 | 0 | 0 | 0 | 1745 | 0 | 15 | Downstream | 0.5 | 1 | 1
COM-AC-SH-485-01 | Current |  | Commercial | Air Curtain |  | New Construction/Retrofit | space heating | Air Curtains | Pedestrian Doors 6' x 7' | Exterior doorway with vestibule and no air curtain |  | unit |  | TRM Version 5.0 | 2020-11-12 | 1082 | 0 | 96 | 0 | 0 | 0 | 1745 | 0 | 15 | Downstream | 0.5 | 1 | 1
COM-AC-SH-480-01 | Current |  | Commercial | Air Curtain |  | New Construction/Retrofit | space heating | Air Curtains | Pedestrian Doors 6' x 8' | Exterior doorway without vestibule or air curtain |  | unit |  | TRM Version 5.0 | 2020-11-12 | 1887 | 0 | 215 | 0 | 0 | 0 | 1745 | 0 | 15 | Downstream | 0.5 | 1 | 1
COM-AC-SH-486-01 | Current |  | Commercial | Air Curtain |  | New Construction/Retrofit | space heating | Air Curtains | Pedestrian Doors 6' x 8' | Exterior doorway with vestibule and no air curtain |  | unit |  | TRM Version 5.0 | 2020-11-12 | 1208 | 0 | 116 | 0 | 0 | 0 | 1745 | 0 | 15 | Downstream | 0.5 | 1 | 1
RES-PT-SH-573-01 | Current |  | Residential | Programmable Thermostat |  | Retrofit | space heating | Programmable Thermostat | Programmable thermostat with at least two programming modes (weekday and weekend) | Non Programmable Thermostat |  | unit |  | TRM Version 5.0 | 2020-11-12 | 46 | 0 | 0 | 0 | 0 | 0 | 97 | 0 | 15 | Downstream | 0 | 1 | 1
RES-PW-WH-566-01 | Current |  | Residential | Pipe Wrap |  | Retrofit | water heating | Pipe Wrap | R 4.35 | No pipe wrap | R-0.435 | ft |  | TRM Version 7.0 | 2022-11-30 | 3.72 | 0 | 0 | 0 | 0 | 0 | 0.39 | 0 | 15 | Downstream | 0.02 | 0.939 | 1
COM-DCV-SH-527-01 | Current |  | Commercial | Demand Control Ventilation | Office | New Construction/Natural Replacement | space heating | Demand Control Ventilation with CO2 Sensor (Office) | Scheduled Ventilation (Occupied Periods) | New single-zone, constant volume ventilation system | Provides min outdoor air requirements as specificed in Table 6.2.2.1 of ASHRAE Standard 62.1-2013 [1] |  | sq ft | TRM Version 5.0 | 2020-11-12 | 0 | 0.112 | 0 | 0 | 0 | 0 | 750 | 0 | 15 | Downstream | 0.92 | 1 | 1.0414
COM-DCV-SH-528-01 | Current |  | Commercial | Demand Control Ventilation | Office | Retrofit | space heating | Demand Control Ventilation with CO2 Sensor (Office) | Scheduled Ventilation (Occupied Periods) | New single-zone, constant volume ventilation system | Provides min outdoor air requirements as specificed in Table 6.2.2.1 of ASHRAE Standard 62.1-2013 [1] |  | sq ft | TRM Version 5.0 | 2020-11-12 | 0 | 0.112 | 0 | 0 | 0 | 0 | 1050 | 0 | 15 | Downstream | 0.92 | 1 | 1.0414
COM-DCV-SH-529-01 | Current |  | Commercial | Demand Control Ventilation | Retail | New Construction/Natural Replacement | space heating | Demand Control Ventilation with CO2 Sensor (Retail) | Scheduled Ventilation (Occupied Periods) | New single-zone, constant volume ventilation system | Provides min outdoor air requirements as specificed in Table 6.2.2.1 of ASHRAE Standard 62.1-2013 [1] |  | sq ft | TRM Version 5.0 | 2020-11-12 | 0 | 0.392 | 0 | 0 | 0 | 0 | 750 | 0 | 15 | Downstream | 0.92 | 1 | 1.0414
COM-DCV-SH-530-01 | Current |  | Commercial | Demand Control Ventilation | Retail | Retrofit | space heating | Demand Control Ventilation with CO2 Sensor (Retail) | Scheduled Ventilation (Occupied Periods) | New single-zone, constant volume ventilation system | Provides min outdoor air requirements as specificed in Table 6.2.2.1 of ASHRAE Standard 62.1-2013 [1] |  | sq ft | TRM Version 5.0 | 2020-11-12 | 0 | 0.392 | 0 | 0 | 0 | 0 | 1050 | 0 | 15 | Downstream | 0.92 | 1 | 1.0414
COM-DCV-SH-531-01 | Current |  | Commercial | Demand Control Ventilation | Cinemas and Performing Arts | Retrofit | space heating | Demand Control Ventilation with CO2 Sensor (Cinemas and Performing Arts) | Scheduled Ventilation (Occupied Periods) | Existing single-zone, constant volume ventilation system | Provides min outdoor air requirements as specificed in Table 6.2.2.1 of ASHRAE Standard 62.1-2013 [1] |  | sq ft | TRM Version 5.0 | 2020-11-12 | 0 | 1.69 | 0 | 0 | 0 | 0 | 1050 | 0 | 15 | Downstream | 0.92 | 1 | 1.0414
COM-DCV-SH-532-01 | Current |  | Commercial | Demand Control Ventilation | Cinemas and Performing Arts | New Construction/Natural Replacement | space heating | Demand Control Ventilation with CO2 Sensor (Cinemas and Performing Arts) | Scheduled Ventilation (Occupied Periods) | Existing single-zone, constant volume ventilation system | Provides min outdoor air requirements as specificed in Table 6.2.2.1 of ASHRAE Standard 62.1-2013 [1] |  | sq ft | TRM Version 5.0 | 2020-11-12 | 0 | 1.69 | 0 | 0 | 0 | 0 | 750 | 0 | 15 | Downstream | 0.92 | 1 | 1.0414
COM-DCV-SH-533-01 | Current |  | Commercial | Demand Control Ventilation | Community Center Meeting Space | Retrofit | space heating | Demand Control Ventilation with CO2 Sensor (Community Center Meeting Space) | Scheduled Ventilation (Occupied Periods) | Existing single-zone, constant volume ventilation system | Provides min outdoor air requirements as specificed in Table 6.2.2.1 of ASHRAE Standard 62.1-2013 [1] |  | sq ft | TRM Version 5.0 | 2020-11-12 | 0 | 0.441 | 0 | 0 | 0 | 0 | 1050 | 0 | 15 | Downstream | 0.92 | 1 | 1.0414
COM-DCV-SH-534-01 | Current |  | Commercial | Demand Control Ventilation | Community Center Meeting Space | New Construction/Natural Replacement | space heating | Demand Control Ventilation with CO2 Sensor (Community Center Meeting Space) | Scheduled Ventilation (Occupied Periods) | Existing single-zone, constant volume ventilation system | Provides min outdoor air requirements as specificed in Table 6.2.2.1 of ASHRAE Standard 62.1-2013 [1] |  | sq ft | TRM Version 5.0 | 2020-11-12 | 0 | 0.441 | 0 | 0 | 0 | 0 | 750 | 0 | 15 | Downstream | 0.92 | 1 | 1.0414
COM-DCV-SH-535-01 | Current |  | Commercial | Demand Control Ventilation | Exercise Center/Sports Arena | Retrofit | space heating | Demand Control Ventilation with CO2 Sensor (Exercise Center/Sports Arena) | Scheduled Ventilation (Occupied Periods) | Existing single-zone, constant volume ventilation system | Provides min outdoor air requirements as specificed in Table 6.2.2.1 of ASHRAE Standard 62.1-2013 [1] |  | sq ft | TRM Version 5.0 | 2020-11-12 | 0 | 0.435 | 0 | 0 | 0 | 0 | 1050 | 0 | 15 | Downstream | 0.92 | 1 | 1.0414
COM-DCV-SH-536-01 | Current |  | Commercial | Demand Control Ventilation | Exercise Center/Sports Arena | New Construction/Natural Replacement | space heating | Demand Control Ventilation with CO2 Sensor (Exercise Center/Sports Arena) | Scheduled Ventilation (Occupied Periods) | Existing single-zone, constant volume ventilation system | Provides min outdoor air requirements as specificed in Table 6.2.2.1 of ASHRAE Standard 62.1-2013 [1] |  | sq ft | TRM Version 5.0 | 2020-11-12 | 0 | 0.435 | 0 | 0 | 0 | 0 | 750 | 0 | 15 | Downstream | 0.92 | 1 | 1.0414
COM-DCV-SH-537-01 | Current |  | Commercial | Demand Control Ventilation | Hotel Conference Rooms | Retrofit | space heating | Demand Control Ventilation with CO2 Sensor (Hotel Conference Rooms) | Scheduled Ventilation (Occupied Periods) | Existing single-zone, constant volume ventilation system | Provides min outdoor air requirements as specificed in Table 6.2.2.1 of ASHRAE Standard 62.1-2013 [1] |  | sq ft | TRM Version 5.0 | 2020-11-12 | 0 | 1.043 | 0 | 0 | 0 | 0 | 1050 | 0 | 15 | Downstream | 0.92 | 1 | 1.0414
COM-DCV-SH-538-01 | Current |  | Commercial | Demand Control Ventilation | Hotel Conference Rooms | New Construction/Natural Replacement | space heating | Demand Control Ventilation with CO2 Sensor (Hotel Conference Rooms) | Scheduled Ventilation (Occupied Periods) | Existing single-zone, constant volume ventilation system | Provides min outdoor air requirements as specificed in Table 6.2.2.1 of ASHRAE Standard 62.1-2013 [1] |  | sq ft | TRM Version 5.0 | 2020-11-12 | 0 | 1.043 | 0 | 0 | 0 | 0 | 750 | 0 | 15 | Downstream | 0.92 | 1 | 1.0414
COM-DCV-SH-539-01 | Current |  | Commercial | Demand Control Ventilation | Post-Secondary School Classroom | Retrofit | space heating | Demand Control Ventilation with CO2 Sensor (Post-Secondary School Classroom) | Scheduled Ventilation (Occupied Periods) | Existing single-zone, constant volume ventilation system | Provides min outdoor air requirements as specificed in Table 6.2.2.1 of ASHRAE Standard 62.1-2013 [1] |  | sq ft | TRM Version 5.0 | 2020-11-12 | 0 | 0.601 | 0 | 0 | 0 | 0 | 1050 | 0 | 15 | Downstream | 0.92 | 1 | 1.0414
COM-DCV-SH-540-01 | Current |  | Commercial | Demand Control Ventilation | Post-Secondary School Classroom | New Construction/Natural Replacement | space heating | Demand Control Ventilation with CO2 Sensor (Post-Secondary School Classroom) | Scheduled Ventilation (Occupied Periods) | Existing single-zone, constant volume ventilation system | Provides min outdoor air requirements as specificed in Table 6.2.2.1 of ASHRAE Standard 62.1-2013 [1] |  | sq ft | TRM Version 5.0 | 2020-11-12 | 0 | 0.601 | 0 | 0 | 0 | 0 | 750 | 0 | 15 | Downstream | 0.92 | 1 | 1.0414
COM-DCV-SH-541-01 | Current |  | Commercial | Demand Control Ventilation | Primary/Secondary School Gymnasium | Retrofit | space heating | Demand Control Ventilation with CO2 Sensor (Primary/Secondary School Gymnasium) | Scheduled Ventilation (Occupied Periods) | Existing single-zone, constant volume ventilation system | Provides min outdoor air requirements as specificed in Table 6.2.2.1 of ASHRAE Standard 62.1-2013 [1] |  | sq ft | TRM Version 5.0 | 2020-11-12 | 0 | 1.484 | 0 | 0 | 0 | 0 | 1050 | 0 | 15 | Downstream | 0.92 | 1 | 1.0414
COM-DCV-SH-542-01 | Current |  | Commercial | Demand Control Ventilation | Primary/Secondary School Gymnasium | New Construction/Natural Replacement | space heating | Demand Control Ventilation with CO2 Sensor (Primary/Secondary School Gymnasium) | Scheduled Ventilation (Occupied Periods) | Existing single-zone, constant volume ventilation system | Provides min outdoor air requirements as specificed in Table 6.2.2.1 of ASHRAE Standard 62.1-2013 [1] |  | sq ft | TRM Version 5.0 | 2020-11-12 | 0 | 1.484 | 0 | 0 | 0 | 0 | 750 | 0 | 15 | Downstream | 0.92 | 1 | 1.0414
COM-DCV-SH-543-01 | Current |  | Commercial | Demand Control Ventilation | Senior/Nursing/Long-Term Care Facility (Common Areas) | Retrofit | space heating | Demand Control Ventilation with CO2 Sensor (Senior/Nursing/Long-Term Care Facility (Common Areas)) | Scheduled Ventilation (Occupied Periods) | Existing single-zone, constant volume ventilation system | Provides min outdoor air requirements as specificed in Table 6.2.2.1 of ASHRAE Standard 62.1-2013 [1] |  | sq ft | TRM Version 5.0 | 2020-11-12 | 0 | 0.636 | 0 | 0 | 0 | 0 | 1050 | 0 | 15 | Downstream | 0.92 | 1 | 1.0414
COM-DCV-SH-544-01 | Current |  | Commercial | Demand Control Ventilation | Senior/Nursing/Long-Term Care Facility (Common Areas) | New Construction/Natural Replacement | space heating | Demand Control Ventilation with CO2 Sensor (Senior/Nursing/Long-Term Care Facility (Common Areas)) | Scheduled Ventilation (Occupied Periods) | Existing single-zone, constant volume ventilation system | Provides min outdoor air requirements as specificed in Table 6.2.2.1 of ASHRAE Standard 62.1-2013 [1] |  | sq ft | TRM Version 5.0 | 2020-11-12 | 0 | 0.636 | 0 | 0 | 0 | 0 | 750 | 0 | 15 | Downstream | 0.92 | 1 | 1.0414
COM-AC-SH-471-01 | Current |  | Commercial | Air Curtain |  | New Construction/Retrofit | space heating | Air Curtains | Shipping and Receiving Doors "Dock-In" 10' x 10' | Exterior doorway without air curtain |  | unit |  | TRM Version 5.0 | 2020-11-12 | 5517 | 0 | -2838 | 0 | 0 | 0 | 6345 | 0 | 15 | Downstream | 0.5 | 1 | 1
COM-AC-SH-470-01 | Current |  | Commercial | Air Curtain |  | New Construction/Retrofit | space heating | Air Curtains | Shipping and Receiving Doors "Dock-In" 8' x 10' | Exterior doorway without air curtain |  | unit |  | TRM Version 5.0 | 2020-11-12 | 4941 | 0 | -1576 | 0 | 0 | 0 | 5663 | 0 | 15 | Downstream | 0.5 | 1 | 1
COM-AC-SH-468-01 | Current |  | Commercial | Air Curtain |  | New Construction/Retrofit | space heating | Air Curtains | Shipping and Receiving Doors "Dock-In" 8' x 8' | Exterior doorway without air curtain |  | unit |  | TRM Version 5.0 | 2020-11-12 | 4713 | 0 | -1688 | 0 | 0 | 0 | 5663 | 0 | 15 | Downstream | 0.5 | 1 | 1
COM-AC-SH-469-01 | Current |  | Commercial | Air Curtain |  | New Construction/Retrofit | space heating | Air Curtains | Shipping and Receiving Doors "Dock-In" 8' x 9' | Exterior doorway without air curtain |  | unit |  | TRM Version 5.0 | 2020-11-12 | 4845 | 0 | -1630 | 0 | 0 | 0 | 5663 | 0 | 15 | Downstream | 0.5 | 1 | 1
COM-AC-SH-472-01 | Current |  | Commercial | Air Curtain |  | New Construction/Retrofit | space heating | Air Curtains | Shipping and Receiving Doors "Drive-In" 10' x 10' | Exterior doorway without air curtain |  | unit |  | TRM Version 5.0 | 2020-11-12 | 4844 | 0 | 540 | 0 | 0 | 0 | 6345 | 0 | 15 | Downstream | 0.5 | 1 | 1
COM-AC-SH-473-01 | Current |  | Commercial | Air Curtain |  | New Construction/Retrofit | space heating | Air Curtains | Shipping and Receiving Doors "Drive-In" 12' x 12' | Exterior doorway without air curtain |  | unit |  | TRM Version 5.0 | 2020-11-12 | 5753 | 0 | 843 | 0 | 0 | 0 | 11158 | 0 | 15 | Downstream | 0.5 | 1 | 1
COM-AC-SH-474-01 | Current |  | Commercial | Air Curtain |  | New Construction/Retrofit | space heating | Air Curtains | Shipping and Receiving Doors "Drive-In" 14' x 14' | Exterior doorway without air curtain |  | unit |  | TRM Version 5.0 | 2020-11-12 | 6504 | 0 | 772 | 0 | 0 | 0 | 14159 | 0 | 15 | Downstream | 0.5 | 1 | 1
COM-AC-SH-475-01 | Current |  | Commercial | Air Curtain |  | New Construction/Retrofit | space heating | Air Curtains | Shipping and Receiving Doors "Drive-In" 16' x 16' | Exterior doorway without air curtain |  | unit |  | TRM Version 5.0 | 2020-11-12 | 7081 | 0 | 987 | 0 | 0 | 0 | 22226 | 0 | 15 | Downstream | 0.5 | 1 | 1
COM-AC-SH-476-01 | Current |  | Commercial | Air Curtain |  | New Construction/Retrofit | space heating | Air Curtains | Shipping and Receiving Doors "Drive-In" 18' x 18' | Exterior doorway without air curtain |  | unit |  | TRM Version 5.0 | 2020-11-12 | 7459 | 0 | 488 | 0 | 0 | 0 | 24699 | 0 | 15 | Downstream | 0.5 | 1 | 1
COM-AC-SH-477-01 | Current |  | Commercial | Air Curtain |  | New Construction/Retrofit | space heating | Air Curtains | Shipping and Receiving Doors "Drive-In" 20' x 20' | Exterior doorway without air curtain |  | unit |  | TRM Version 5.0 | 2020-11-12 | 7605 | 0 | 596 | 0 | 0 | 0 | 45256 | 0 | 15 | Downstream | 0.5 | 1 | 1
COM-ERV-SH-300-01 | Current |  | Commercial | Energy Recovery Ventilation | High Use Group | New Construction/Retrofit | space heating | High Efficient 55% Energy Recovery Ventilation High Use Group (Multi-Residential, Health Care, Nursing Homes) | Ventilation with ERV Integrated | Ventilation without ERV |  |  | CFM | TRM Version 5.0 | 2020-11-12 | 0 | 4.52 | 0 | 0 | 0 | 0 | 0 | 4.86 | 14 | Downstream | 0.7 | 1 | 1
COM-ERV-SH-302-01 | Current |  | Commercial | Energy Recovery Ventilation | Medium Use Group | New Construction/Retrofit | space heating | High Efficient 55% Energy Recovery Ventilation Medium Use Group (Hotel, Restaurant, Retail) | Ventilation with ERV Integrated | Ventilation without ERV |  |  | CFM | TRM Version 5.0 | 2020-11-12 | 0 | 2.51 | 0 | 0 | 0 | 0 | 0 | 4.86 | 14 | Downstream | 0.7 | 1 | 1
COM-ERV-SH-304-01 | Current |  | Commercial | Energy Recovery Ventilation | Low Use Group | New Construction/Retrofit | space heating | High Efficient 55% Energy Recovery Ventilation Low Use Group (Office, Warehouse, School) | Ventilation with ERV Integrated | Ventilation without ERV |  |  | CFM | TRM Version 5.0 | 2020-11-12 | 0 | 1.6 | 0 | 0 | 0 | 0 | 0 | 4.86 | 14 | Downstream | 0.7 | 1 | 1
COM-ERV-SH-306-01 | Current |  | Commercial | Energy Recovery Ventilation | Multi-Residential, Health Care, Nursing Homes | New Construction/Retrofit | space heating | High Efficient 55% Energy Recovery Ventilation High Use Group (Multi-Residential, Health Care, Nursing Homes) | Ventilation with ERV Integrated | Ventilation without ERV |  |  | CFM | TRM Version 5.0 | 2020-11-12 | 0 | 4.52 | 0 | 0 | 0 | 0 | 0 | 4.86 | 14 | Downstream | 0.7 | 1 | 1
COM-ERV-SH-308-01 | Current |  | Commercial | Energy Recovery Ventilation | Hotel | New Construction/Retrofit | space heating | High Efficient 55% Energy Recovery Ventilation Medium Use Group (Hotel, Restaurant, Retail) | Ventilation with ERV Integrated | Ventilation without ERV |  |  | CFM | TRM Version 5.0 | 2020-11-12 | 0 | 3.23 | 0 | 0 | 0 | 0 | 0 | 4.86 | 14 | Downstream | 0.7 | 1 | 1
COM-ERV-SH-310-01 | Current |  | Commercial | Energy Recovery Ventilation | Restaurant | New Construction/Retrofit | space heating | High Efficient 55% Energy Recovery Ventilation Medium Use Group (Hotel, Restaurant, Retail) | Ventilation with ERV Integrated | Ventilation without ERV |  |  | CFM | TRM Version 5.0 | 2020-11-12 | 0 | 2.34 | 0 | 0 | 0 | 0 | 0 | 4.86 | 14 | Downstream | 0.7 | 1 | 1
COM-ERV-SH-312-01 | Current |  | Commercial | Energy Recovery Ventilation | Retail | New Construction/Retrofit | space heating | High Efficient 55% Energy Recovery Ventilation Medium Use Group (Hotel, Restaurant, Retail) | Ventilation with ERV Integrated | Ventilation without ERV |  |  | CFM | TRM Version 5.0 | 2020-11-12 | 0 | 1.96 | 0 | 0 | 0 | 0 | 0 | 4.86 | 14 | Downstream | 0.7 | 1 | 1
COM-ERV-SH-314-01 | Current |  | Commercial | Energy Recovery Ventilation | Office | New Construction/Retrofit | space heating | High Efficient 55% Energy Recovery Ventilation Low Use Group (Office, Warehouse, School) | Ventilation with ERV Integrated | Ventilation without ERV |  |  | CFM | TRM Version 5.0 | 2020-11-12 | 0 | 1.72 | 0 | 0 | 0 | 0 | 0 | 4.86 | 14 | Downstream | 0.7 | 1 | 1
COM-ERV-SH-316-01 | Current |  | Commercial | Energy Recovery Ventilation | Warehouse | New Construction/Retrofit | space heating | High Efficient 55% Energy Recovery Ventilation Low Use Group (Office, Warehouse, School) | Ventilation with ERV Integrated | Ventilation without ERV |  |  | CFM | TRM Version 5.0 | 2020-11-12 | 0 | 1.64 | 0 | 0 | 0 | 0 | 0 | 4.86 | 14 | Downstream | 0.7 | 1 | 1
COM-ERV-SH-318-01 | Current |  | Commercial | Energy Recovery Ventilation | School | New Construction/Retrofit | space heating | High Efficient 55% Energy Recovery Ventilation Low Use Group (Office, Warehouse, School) | Ventilation with ERV Integrated | Ventilation without ERV |  |  | CFM | TRM Version 5.0 | 2020-11-12 | 0 | 1.45 | 0 | 0 | 0 | 0 | 0 | 4.86 | 14 | Downstream | 0.7 | 1 | 1
COM-ERV-SH-320-01 | Current |  | Commercial | Energy Recovery Ventilation | High Use Group | New Construction/Retrofit | space heating | High Efficient 65% Energy Recovery Ventilation High Use Group (Multi-Residential, Health Care, Nursing Homes) | Ventilation with ERV Integrated | Ventilation without ERV |  |  | CFM | TRM Version 5.0 | 2020-11-12 | 0 | 5.37 | 0 | 0 | 0 | 0 | 0 | 5.86 | 14 | Downstream | 0.7 | 1 | 1
COM-ERV-SH-322-01 | Current |  | Commercial | Energy Recovery Ventilation | Medium Use Group | New Construction/Retrofit | space heating | High Efficient 65% Energy Recovery Ventilation Medium Use Group (Hotel, Restaurant, Retail) | Ventilation with ERV Integrated | Ventilation without ERV |  |  | CFM | TRM Version 5.0 | 2020-11-12 | 0 | 2.98 | 0 | 0 | 0 | 0 | 0 | 5.86 | 14 | Downstream | 0.7 | 1 | 1
COM-ERV-SH-324-01 | Current |  | Commercial | Energy Recovery Ventilation | Low Use Group | New Construction/Retrofit | space heating | High Efficient 65% Energy Recovery Ventilation Low Use Group (Office, Warehouse, School) | Ventilation with ERV Integrated | Ventilation without ERV |  |  | CFM | TRM Version 5.0 | 2020-11-12 | 0 | 1.91 | 0 | 0 | 0 | 0 | 0 | 5.86 | 14 | Downstream | 0.7 | 1 | 1
COM-ERV-SH-326-01 | Current |  | Commercial | Energy Recovery Ventilation | Multi-Residential, Health Care, Nursing Homes | New Construction/Retrofit | space heating | High Efficient 65% Energy Recovery Ventilation High Use Group (Multi-Residential, Health Care, Nursing Homes) | Ventilation with ERV Integrated | Ventilation without ERV |  |  | CFM | TRM Version 5.0 | 2020-11-12 | 0 | 5.37 | 0 | 0 | 0 | 0 | 0 | 5.86 | 14 | Downstream | 0.7 | 1 | 1
COM-ERV-SH-328-01 | Current |  | Commercial | Energy Recovery Ventilation | Hotel | New Construction/Retrofit | space heating | High Efficient 65% Energy Recovery Ventilation Medium Use Group (Hotel, Restaurant, Retail) | Ventilation with ERV Integrated | Ventilation without ERV |  |  | CFM | TRM Version 5.0 | 2020-11-12 | 0 | 3.84 | 0 | 0 | 0 | 0 | 0 | 5.86 | 14 | Downstream | 0.7 | 1 | 1
COM-ERV-SH-330-01 | Current |  | Commercial | Energy Recovery Ventilation | Restaurant | New Construction/Retrofit | space heating | High Efficient 65% Energy Recovery Ventilation Medium Use Group (Hotel, Restaurant, Retail) | Ventilation with ERV Integrated | Ventilation without ERV |  |  | CFM | TRM Version 5.0 | 2020-11-12 | 0 | 2.78 | 0 | 0 | 0 | 0 | 0 | 5.86 | 14 | Downstream | 0.7 | 1 | 1
COM-ERV-SH-332-01 | Current |  | Commercial | Energy Recovery Ventilation | Retail | New Construction/Retrofit | space heating | High Efficient 65% Energy Recovery Ventilation Medium Use Group (Hotel, Restaurant, Retail) | Ventilation with ERV Integrated | Ventilation without ERV |  |  | CFM | TRM Version 5.0 | 2020-11-12 | 0 | 2.33 | 0 | 0 | 0 | 0 | 0 | 5.86 | 14 | Downstream | 0.7 | 1 | 1
COM-ERV-SH-334-01 | Current |  | Commercial | Energy Recovery Ventilation | Office | New Construction/Retrofit | space heating | High Efficient 65% Energy Recovery Ventilation Low Use Group (Office, Warehouse, School) | Ventilation with ERV Integrated | Ventilation without ERV |  |  | CFM | TRM Version 5.0 | 2020-11-12 | 0 | 2.05 | 0 | 0 | 0 | 0 | 0 | 5.86 | 14 | Downstream | 0.7 | 1 | 1
COM-ERV-SH-336-01 | Current |  | Commercial | Energy Recovery Ventilation | Warehouse | New Construction/Retrofit | space heating | High Efficient 65% Energy Recovery Ventilation Low Use Group (Office, Warehouse, School) | Ventilation with ERV Integrated | Ventilation without ERV |  |  | CFM | TRM Version 5.0 | 2020-11-12 | 0 | 1.95 | 0 | 0 | 0 | 0 | 0 | 5.86 | 14 | Downstream | 0.7 | 1 | 1
COM-ERV-SH-338-01 | Current |  | Commercial | Energy Recovery Ventilation | School | New Construction/Retrofit | space heating | High Efficient 65% Energy Recovery Ventilation Low Use Group (Office, Warehouse, School) | Ventilation with ERV Integrated | Ventilation without ERV |  |  | CFM | TRM Version 5.0 | 2020-11-12 | 0 | 1.73 | 0 | 0 | 0 | 0 | 0 | 5.86 | 14 | Downstream | 0.7 | 1 | 1
COM-ERV-SH-340-01 | Current |  | Commercial | Energy Recovery Ventilation | High Use Group | New Construction/Retrofit | space heating | High Efficient 75% Energy Recovery Ventilation High Use Group (Multi-Residential, Health Care, Nursing Homes) | Ventilation with ERV Integrated | Ventilation without ERV |  |  | CFM | TRM Version 5.0 | 2020-11-12 | 0 | 6.22 | 0 | 0 | 0 | 0 | 0 | 6.86 | 14 | Downstream | 0.7 | 1 | 1
COM-ERV-SH-342-01 | Current |  | Commercial | Energy Recovery Ventilation | Medium Use Group | New Construction/Retrofit | space heating | High Efficient 75% Energy Recovery Ventilation Medium Use Group (Hotel, Restaurant, and Retail) | Ventilation with ERV Integrated | Ventilation without ERV |  |  | CFM | TRM Version 5.0 | 2020-11-12 | 0 | 3.45 | 0 | 0 | 0 | 0 | 0 | 6.86 | 14 | Downstream | 0.7 | 1 | 1
COM-ERV-SH-344-01 | Current |  | Commercial | Energy Recovery Ventilation | Low Use Group | New Construction/Retrofit | space heating | High Efficient 75% Energy Recovery Ventilation Low Use Group (Office, Warehouse, School) | Ventilation with ERV Integrated | Ventilation without ERV |  |  | CFM | TRM Version 5.0 | 2020-11-12 | 0 | 2.21 | 0 | 0 | 0 | 0 | 0 | 6.86 | 14 | Downstream | 0.7 | 1 | 1
COM-ERV-SH-346-01 | Current |  | Commercial | Energy Recovery Ventilation | Multi-Residential, Health Care, Nursing Homes | New Construction/Retrofit | space heating | High Efficient 75% Energy Recovery Ventilation High Use Group (Multi-Residential, Health Care, Nursing Homes) | Ventilation with ERV Integrated | Ventilation without ERV |  |  | CFM | TRM Version 5.0 | 2020-11-12 | 0 | 6.22 | 0 | 0 | 0 | 0 | 0 | 6.86 | 14 | Downstream | 0.7 | 1 | 1
COM-ERV-SH-348-01 | Current |  | Commercial | Energy Recovery Ventilation | Hotel | New Construction/Retrofit | space heating | High Efficient 75% Energy Recovery Ventilation Medium Use Group (Hotel, Restaurant, and Retail) | Ventilation with ERV Integrated | Ventilation without ERV |  |  | CFM | TRM Version 5.0 | 2020-11-12 | 0 | 4.44 | 0 | 0 | 0 | 0 | 0 | 6.86 | 14 | Downstream | 0.7 | 1 | 1
COM-ERV-SH-350-01 | Current |  | Commercial | Energy Recovery Ventilation | Restaurant | New Construction/Retrofit | space heating | High Efficient 75% Energy Recovery Ventilation Medium Use Group (Hotel, Restaurant, and Retail) | Ventilation with ERV Integrated | Ventilation without ERV |  |  | CFM | TRM Version 5.0 | 2020-11-12 | 0 | 3.22 | 0 | 0 | 0 | 0 | 0 | 6.86 | 14 | Downstream | 0.7 | 1 | 1
COM-ERV-SH-352-01 | Current |  | Commercial | Energy Recovery Ventilation | Retail | New Construction/Retrofit | space heating | High Efficient 75% Energy Recovery Ventilation Medium Use Group (Hotel, Restaurant, and Retail) | Ventilation with ERV Integrated | Ventilation without ERV |  |  | CFM | TRM Version 5.0 | 2020-11-12 | 0 | 2.7 | 0 | 0 | 0 | 0 | 0 | 6.86 | 14 | Downstream | 0.7 | 1 | 1
COM-ERV-SH-354-01 | Current |  | Commercial | Energy Recovery Ventilation | Office | New Construction/Retrofit | space heating | High Efficient 75% Energy Recovery Ventilation Low Use Group (Office, Warehouse, School) | Ventilation with ERV Integrated | Ventilation without ERV |  |  | CFM | TRM Version 5.0 | 2020-11-12 | 0 | 2.37 | 0 | 0 | 0 | 0 | 0 | 6.86 | 14 | Downstream | 0.7 | 1 | 1
COM-ERV-SH-356-01 | Current |  | Commercial | Energy Recovery Ventilation | Warehouse | New Construction/Retrofit | space heating | High Efficient 75% Energy Recovery Ventilation Low Use Group (Office, Warehouse, School) | Ventilation with ERV Integrated | Ventilation without ERV |  |  | CFM | TRM Version 5.0 | 2020-11-12 | 0 | 2.26 | 0 | 0 | 0 | 0 | 0 | 6.86 | 14 | Downstream | 0.7 | 1 | 1
COM-ERV-SH-358-01 | Current |  | Commercial | Energy Recovery Ventilation | School | New Construction/Retrofit | space heating | High Efficient 75% Energy Recovery Ventilation Low Use Group (Office, Warehouse, School) | Ventilation with ERV Integrated | Ventilation without ERV |  |  | CFM | TRM Version 5.0 | 2020-11-12 | 0 | 2 | 0 | 0 | 0 | 0 | 0 | 6.86 | 14 | Downstream | 0.7 | 1 | 1
COM-ERV-SH-360-01 | Current |  | Commercial | Energy Recovery Ventilation | High Use Group | New Construction/Retrofit | space heating | High Efficient 85% Energy Recovery Ventilation High Use Group (Multi-Residential, Health Care, Nursing Homes) | Ventilation with ERV Integrated | Ventilation without ERV |  |  | CFM | TRM Version 5.0 | 2020-11-12 | 0 | 7.07 | 0 | 0 | 0 | 0 | 0 | 7.86 | 14 | Downstream | 0.7 | 1 | 1
COM-ERV-SH-362-01 | Current |  | Commercial | Energy Recovery Ventilation | Medium Use Group | New Construction/Retrofit | space heating | High Efficient 85% Energy Recovery Ventilation Medium Use Group (Hotel, Restaurant, Retail) | Ventilation with ERV Integrated | Ventilation without ERV |  |  | CFM | TRM Version 5.0 | 2020-11-12 | 0 | 3.93 | 0 | 0 | 0 | 0 | 0 | 7.86 | 14 | Downstream | 0.7 | 1 | 1
COM-ERV-SH-364-01 | Current |  | Commercial | Energy Recovery Ventilation | Low Use Group | New Construction/Retrofit | space heating | High Efficient 85% Energy Recovery Ventilation Low Use Group (Office, Warehouse, School) | Ventilation with ERV Integrated | Ventilation without ERV |  |  | CFM | TRM Version 5.0 | 2020-11-12 | 0 | 2.51 | 0 | 0 | 0 | 0 | 0 | 7.86 | 14 | Downstream | 0.7 | 1 | 1
COM-ERV-SH-366-01 | Current |  | Commercial | Energy Recovery Ventilation | Multi-Residential, Health Care, Nursing Homes | New Construction/Retrofit | space heating | High Efficient 85% Energy Recovery Ventilation High Use Group (Multi-Residential, Health Care, Nursing Homes) | Ventilation with ERV Integrated | Ventilation without ERV |  |  | CFM | TRM Version 5.0 | 2020-11-12 | 0 | 7.07 | 0 | 0 | 0 | 0 | 0 | 7.86 | 14 | Downstream | 0.7 | 1 | 1
COM-ERV-SH-368-01 | Current |  | Commercial | Energy Recovery Ventilation | Hotel | New Construction/Retrofit | space heating | High Efficient 85% Energy Recovery Ventilation Medium Use Group (Hotel, Restaurant, Retail) | Ventilation with ERV Integrated | Ventilation without ERV |  |  | CFM | TRM Version 5.0 | 2020-11-12 | 0 | 5.05 | 0 | 0 | 0 | 0 | 0 | 7.86 | 14 | Downstream | 0.7 | 1 | 1
COM-ERV-SH-370-01 | Current |  | Commercial | Energy Recovery Ventilation | Restaurant | New Construction/Retrofit | space heating | High Efficient 85% Energy Recovery Ventilation Medium Use Group (Hotel, Restaurant, Retail) | Ventilation with ERV Integrated | Ventilation without ERV |  |  | CFM | TRM Version 5.0 | 2020-11-12 | 0 | 3.66 | 0 | 0 | 0 | 0 | 0 | 7.86 | 14 | Downstream | 0.7 | 1 | 1
COM-ERV-SH-372-01 | Current |  | Commercial | Energy Recovery Ventilation | Retail | New Construction/Retrofit | space heating | High Efficient 85% Energy Recovery Ventilation Medium Use Group (Hotel, Restaurant, Retail) | Ventilation with ERV Integrated | Ventilation without ERV |  |  | CFM | TRM Version 5.0 | 2020-11-12 | 0 | 3.07 | 0 | 0 | 0 | 0 | 0 | 7.86 | 14 | Downstream | 0.7 | 1 | 1
COM-ERV-SH-374-01 | Current |  | Commercial | Energy Recovery Ventilation | Office | New Construction/Retrofit | space heating | High Efficient 85% Energy Recovery Ventilation Low Use Group (Office, Warehouse, School) | Ventilation with ERV Integrated | Ventilation without ERV |  |  | CFM | TRM Version 5.0 | 2020-11-12 | 0 | 2.69 | 0 | 0 | 0 | 0 | 0 | 7.86 | 14 | Downstream | 0.7 | 1 | 1
COM-ERV-SH-376-01 | Current |  | Commercial | Energy Recovery Ventilation | Warehouse | New Construction/Retrofit | space heating | High Efficient 85% Energy Recovery Ventilation Low Use Group (Office, Warehouse, School) | Ventilation with ERV Integrated | Ventilation without ERV |  |  | CFM | TRM Version 5.0 | 2020-11-12 | 0 | 2.57 | 0 | 0 | 0 | 0 | 0 | 7.86 | 14 | Downstream | 0.7 | 1 | 1
COM-ERV-SH-378-01 | Current |  | Commercial | Energy Recovery Ventilation | School | New Construction/Retrofit | space heating | High Efficient 85% Energy Recovery Ventilation Low Use Group (Office, Warehouse, School) | Ventilation with ERV Integrated | Ventilation without ERV |  |  | CFM | TRM Version 5.0 | 2020-11-12 | 0 | 2.27 | 0 | 0 | 0 | 0 | 0 | 7.86 | 14 | Downstream | 0.7 | 1 | 1
COM-ERV-SH-301-01 | Current |  | Commercial | Energy Recovery Ventilation | High Use Group | New Construction/Retrofit | space heating | High Efficient 55% Energy Recovery Ventilation High Use Group (Multi-Residential, Health Care, Nursing Homes) | Ventilation with ERV Standalone | Ventilation without ERV |  |  | CFM | TRM Version 5.0 | 2020-11-12 | 0 | 4.52 | 0 | -4.39 | 0 | 0 | 0 | 7.8 | 14 | Downstream | 0.7 | 1 | 1
COM-ERV-SH-303-01 | Current |  | Commercial | Energy Recovery Ventilation | Medium Use Group | New Construction/Retrofit | space heating | High Efficient 55% Energy Recovery Ventilation Medium Use Group (Hotel, Restaurant, Retail) | Ventilation with ERV Standalone | Ventilation without ERV |  |  | CFM | TRM Version 5.0 | 2020-11-12 | 0 | 2.51 | 0 | -2.44 | 0 | 0 | 0 | 7.8 | 14 | Downstream | 0.7 | 1 | 1
COM-ERV-SH-305-01 | Current |  | Commercial | Energy Recovery Ventilation | Low Use Group | New Construction/Retrofit | space heating | High Efficient 55% Energy Recovery Ventilation Low Use Group (Office, Warehouse, School) | Ventilation with ERV Standalone | Ventilation without ERV |  |  | CFM | TRM Version 5.0 | 2020-11-12 | 0 | 1.6 | 0 | -1.56 | 0 | 0 | 0 | 7.8 | 14 | Downstream | 0.7 | 1 | 1
COM-ERV-SH-307-01 | Current |  | Commercial | Energy Recovery Ventilation | Multi-Residential, Health Care, Nursing Homes | New Construction/Retrofit | space heating | High Efficient 55% Energy Recovery Ventilation High Use Group (Multi-Residential, Health Care, Nursing Homes) | Ventilation with ERV Standalone | Ventilation without ERV |  |  | CFM | TRM Version 5.0 | 2020-11-12 | 0 | 4.52 | 0 | -4.39 | 0 | 0 | 0 | 7.8 | 14 | Downstream | 0.7 | 1 | 1
COM-ERV-SH-309-01 | Current |  | Commercial | Energy Recovery Ventilation | Hotel | New Construction/Retrofit | space heating | High Efficient 55% Energy Recovery Ventilation Medium Use Group (Hotel, Restaurant, Retail) | Ventilation with ERV Standalone | Ventilation without ERV |  |  | CFM | TRM Version 5.0 | 2020-11-12 | 0 | 3.23 | 0 | -3.14 | 0 | 0 | 0 | 7.8 | 14 | Downstream | 0.7 | 1 | 1
COM-ERV-SH-311-01 | Current |  | Commercial | Energy Recovery Ventilation | Restaurant | New Construction/Retrofit | space heating | High Efficient 55% Energy Recovery Ventilation Medium Use Group (Hotel, Restaurant, Retail) | Ventilation with ERV Standalone | Ventilation without ERV |  |  | CFM | TRM Version 5.0 | 2020-11-12 | 0 | 2.34 | 0 | -2.28 | 0 | 0 | 0 | 7.8 | 14 | Downstream | 0.7 | 1 | 1
COM-ERV-SH-313-01 | Current |  | Commercial | Energy Recovery Ventilation | Retail | New Construction/Retrofit | space heating | High Efficient 55% Energy Recovery Ventilation Medium Use Group (Hotel, Restaurant, Retail) | Ventilation with ERV Standalone | Ventilation without ERV |  |  | CFM | TRM Version 5.0 | 2020-11-12 | 0 | 1.96 | 0 | -1.91 | 0 | 0 | 0 | 7.8 | 14 | Downstream | 0.7 | 1 | 1
COM-ERV-SH-315-01 | Current |  | Commercial | Energy Recovery Ventilation | Office | New Construction/Retrofit | space heating | High Efficient 55% Energy Recovery Ventilation Low Use Group (Office, Warehouse, School) | Ventilation with ERV Standalone | Ventilation without ERV |  |  | CFM | TRM Version 5.0 | 2020-11-12 | 0 | 1.72 | 0 | -1.67 | 0 | 0 | 0 | 7.8 | 14 | Downstream | 0.7 | 1 | 1
COM-ERV-SH-317-01 | Current |  | Commercial | Energy Recovery Ventilation | Warehouse | New Construction/Retrofit | space heating | High Efficient 55% Energy Recovery Ventilation Low Use Group (Office, Warehouse, School) | Ventilation with ERV Standalone | Ventilation without ERV |  |  | CFM | TRM Version 5.0 | 2020-11-12 | 0 | 1.64 | 0 | -1.6 | 0 | 0 | 0 | 7.8 | 14 | Downstream | 0.7 | 1 | 1
COM-ERV-SH-319-01 | Current |  | Commercial | Energy Recovery Ventilation | School | New Construction/Retrofit | space heating | High Efficient 55% Energy Recovery Ventilation Low Use Group (Office, Warehouse, School) | Ventilation with ERV Standalone | Ventilation without ERV |  |  | CFM | TRM Version 5.0 | 2020-11-12 | 0 | 1.45 | 0 | -1.41 | 0 | 0 | 0 | 7.8 | 14 | Downstream | 0.7 | 1 | 1
COM-ERV-SH-321-01 | Current |  | Commercial | Energy Recovery Ventilation | High Use Group | New Construction/Retrofit | space heating | High Efficient 65% Energy Recovery Ventilation High Use Group (Multi-Residential, Health Care, Nursing Homes) | Ventilation with ERV Standalone | Ventilation without ERV |  |  | CFM | TRM Version 5.0 | 2020-11-12 | 0 | 5.37 | 0 | -4.39 | 0 | 0 | 0 | 8.8 | 14 | Downstream | 0.7 | 1 | 1
COM-ERV-SH-323-01 | Current |  | Commercial | Energy Recovery Ventilation | Medium Use Group | New Construction/Retrofit | space heating | High Efficient 65% Energy Recovery Ventilation Medium Use Group (Hotel, Restaurant, Retail) | Ventilation with ERV Standalone | Ventilation without ERV |  |  | CFM | TRM Version 5.0 | 2020-11-12 | 0 | 2.98 | 0 | -2.44 | 0 | 0 | 0 | 8.8 | 14 | Downstream | 0.7 | 1 | 1
COM-ERV-SH-325-01 | Current |  | Commercial | Energy Recovery Ventilation | Low Use Group | New Construction/Retrofit | space heating | High Efficient 65% Energy Recovery Ventilation Low Use Group (Office, Warehouse, School) | Ventilation with ERV Standalone | Ventilation without ERV |  |  | CFM | TRM Version 5.0 | 2020-11-12 | 0 | 1.91 | 0 | -1.56 | 0 | 0 | 0 | 8.8 | 14 | Downstream | 0.7 | 1 | 1
COM-ERV-SH-327-01 | Current |  | Commercial | Energy Recovery Ventilation | Multi-Residential, Health Care, Nursing Homes | New Construction/Retrofit | space heating | High Efficient 65% Energy Recovery Ventilation High Use Group (Multi-Residential, Health Care, Nursing Homes) | Ventilation with ERV Standalone | Ventilation without ERV |  |  | CFM | TRM Version 5.0 | 2020-11-12 | 0 | 5.37 | 0 | -4.39 | 0 | 0 | 0 | 8.8 | 14 | Downstream | 0.7 | 1 | 1
COM-ERV-SH-329-01 | Current |  | Commercial | Energy Recovery Ventilation | Hotel | New Construction/Retrofit | space heating | High Efficient 65% Energy Recovery Ventilation Medium Use Group (Hotel, Restaurant, Retail) | Ventilation with ERV Standalone | Ventilation without ERV |  |  | CFM | TRM Version 5.0 | 2020-11-12 | 0 | 3.84 | 0 | -3.14 | 0 | 0 | 0 | 8.8 | 14 | Downstream | 0.7 | 1 | 1
COM-ERV-SH-331-01 | Current |  | Commercial | Energy Recovery Ventilation | Restaurant | New Construction/Retrofit | space heating | High Efficient 65% Energy Recovery Ventilation Medium Use Group (Hotel, Restaurant, Retail) | Ventilation with ERV Standalone | Ventilation without ERV |  |  | CFM | TRM Version 5.0 | 2020-11-12 | 0 | 2.78 | 0 | -2.28 | 0 | 0 | 0 | 8.8 | 14 | Downstream | 0.7 | 1 | 1
COM-ERV-SH-333-01 | Current |  | Commercial | Energy Recovery Ventilation | Retail | New Construction/Retrofit | space heating | High Efficient 65% Energy Recovery Ventilation Medium Use Group (Hotel, Restaurant, Retail) | Ventilation with ERV Standalone | Ventilation without ERV |  |  | CFM | TRM Version 5.0 | 2020-11-12 | 0 | 2.33 | 0 | -1.91 | 0 | 0 | 0 | 8.8 | 14 | Downstream | 0.7 | 1 | 1
COM-ERV-SH-335-01 | Current |  | Commercial | Energy Recovery Ventilation | Office | New Construction/Retrofit | space heating | High Efficient 65% Energy Recovery Ventilation Low Use Group (Office, Warehouse, School) | Ventilation with ERV Standalone | Ventilation without ERV |  |  | CFM | TRM Version 5.0 | 2020-11-12 | 0 | 2.05 | 0 | -1.67 | 0 | 0 | 0 | 8.8 | 14 | Downstream | 0.7 | 1 | 1
COM-ERV-SH-337-01 | Current |  | Commercial | Energy Recovery Ventilation | Warehouse | New Construction/Retrofit | space heating | High Efficient 65% Energy Recovery Ventilation Low Use Group (Office, Warehouse, School) | Ventilation with ERV Standalone | Ventilation without ERV |  |  | CFM | TRM Version 5.0 | 2020-11-12 | 0 | 1.95 | 0 | -1.6 | 0 | 0 | 0 | 8.8 | 14 | Downstream | 0.7 | 1 | 1
COM-ERV-SH-339-01 | Current |  | Commercial | Energy Recovery Ventilation | School | New Construction/Retrofit | space heating | High Efficient 65% Energy Recovery Ventilation Low Use Group (Office, Warehouse, School) | Ventilation with ERV Standalone | Ventilation without ERV |  |  | CFM | TRM Version 5.0 | 2020-11-12 | 0 | 1.73 | 0 | -1.41 | 0 | 0 | 0 | 8.8 | 14 | Downstream | 0.7 | 1 | 1
COM-ERV-SH-341-01 | Current |  | Commercial | Energy Recovery Ventilation | High Use Group | New Construction/Retrofit | space heating | High Efficient 75% Energy Recovery Ventilation High Use Group (Multi-Residential, Health Care, Nursing Homes) | Ventilation with ERV Standalone | Ventilation without ERV |  |  | CFM | TRM Version 5.0 | 2020-11-12 | 0 | 6.22 | 0 | -4.39 | 0 | 0 | 0 | 9.8 | 14 | Downstream | 0.7 | 1 | 1
COM-ERV-SH-343-01 | Current |  | Commercial | Energy Recovery Ventilation | Medium Use Group | New Construction/Retrofit | space heating | High Efficient 75% Energy Recovery Ventilation Medium Use Group (Hotel, Restaurant, and Retail) | Ventilation with ERV Standalone | Ventilation without ERV |  |  | CFM | TRM Version 5.0 | 2020-11-12 | 0 | 3.45 | 0 | -2.44 | 0 | 0 | 0 | 9.8 | 14 | Downstream | 0.7 | 1 | 1
COM-ERV-SH-345-01 | Current |  | Commercial | Energy Recovery Ventilation | Low Use Group | New Construction/Retrofit | space heating | High Efficient 75% Energy Recovery Ventilation Low Use Group (Office, Warehouse, School) | Ventilation with ERV Standalone | Ventilation without ERV |  |  | CFM | TRM Version 5.0 | 2020-11-12 | 0 | 2.21 | 0 | -1.56 | 0 | 0 | 0 | 9.8 | 14 | Downstream | 0.7 | 1 | 1
COM-ERV-SH-347-01 | Current |  | Commercial | Energy Recovery Ventilation | Multi-Residential, Health Care, Nursing Homes | New Construction/Retrofit | space heating | High Efficient 75% Energy Recovery Ventilation High Use Group (Multi-Residential, Health Care, Nursing Homes) | Ventilation with ERV Standalone | Ventilation without ERV |  |  | CFM | TRM Version 5.0 | 2020-11-12 | 0 | 6.22 | 0 | -4.39 | 0 | 0 | 0 | 9.8 | 14 | Downstream | 0.7 | 1 | 1
COM-ERV-SH-349-01 | Current |  | Commercial | Energy Recovery Ventilation | Hotel | New Construction/Retrofit | space heating | High Efficient 75% Energy Recovery Ventilation Medium Use Group (Hotel, Restaurant, and Retail) | Ventilation with ERV Standalone | Ventilation without ERV |  |  | CFM | TRM Version 5.0 | 2020-11-12 | 0 | 4.44 | 0 | -3.14 | 0 | 0 | 0 | 9.8 | 14 | Downstream | 0.7 | 1 | 1
COM-ERV-SH-351-01 | Current |  | Commercial | Energy Recovery Ventilation | Restaurant | New Construction/Retrofit | space heating | High Efficient 75% Energy Recovery Ventilation Medium Use Group (Hotel, Restaurant, and Retail) | Ventilation with ERV Standalone | Ventilation without ERV |  |  | CFM | TRM Version 5.0 | 2020-11-12 | 0 | 3.22 | 0 | -2.28 | 0 | 0 | 0 | 9.8 | 14 | Downstream | 0.7 | 1 | 1
COM-ERV-SH-353-01 | Current |  | Commercial | Energy Recovery Ventilation | Retail | New Construction/Retrofit | space heating | High Efficient 75% Energy Recovery Ventilation Medium Use Group (Hotel, Restaurant, and Retail) | Ventilation with ERV Standalone | Ventilation without ERV |  |  | CFM | TRM Version 5.0 | 2020-11-12 | 0 | 2.7 | 0 | -1.91 | 0 | 0 | 0 | 9.8 | 14 | Downstream | 0.7 | 1 | 1
COM-ERV-SH-355-01 | Current |  | Commercial | Energy Recovery Ventilation | Office | New Construction/Retrofit | space heating | High Efficient 75% Energy Recovery Ventilation Low Use Group (Office, Warehouse, School) | Ventilation with ERV Standalone | Ventilation without ERV |  |  | CFM | TRM Version 5.0 | 2020-11-12 | 0 | 2.37 | 0 | -1.67 | 0 | 0 | 0 | 9.8 | 14 | Downstream | 0.7 | 1 | 1
COM-ERV-SH-357-01 | Current |  | Commercial | Energy Recovery Ventilation | Warehouse | New Construction/Retrofit | space heating | High Efficient 75% Energy Recovery Ventilation Low Use Group (Office, Warehouse, School) | Ventilation with ERV Standalone | Ventilation without ERV |  |  | CFM | TRM Version 5.0 | 2020-11-12 | 0 | 2.26 | 0 | -1.6 | 0 | 0 | 0 | 9.8 | 14 | Downstream | 0.7 | 1 | 1
COM-ERV-SH-359-01 | Current |  | Commercial | Energy Recovery Ventilation | School | New Construction/Retrofit | space heating | High Efficient 75% Energy Recovery Ventilation Low Use Group (Office, Warehouse, School) | Ventilation with ERV Standalone | Ventilation without ERV |  |  | CFM | TRM Version 5.0 | 2020-11-12 | 0 | 2 | 0 | -1.41 | 0 | 0 | 0 | 9.8 | 14 | Downstream | 0.7 | 1 | 1
COM-ERV-SH-361-01 | Current |  | Commercial | Energy Recovery Ventilation | High Use Group | New Construction/Retrofit | space heating | High Efficient 85% Energy Recovery Ventilation High Use Group (Multi-Residential, Health Care, Nursing Homes) | Ventilation with ERV Standalone | Ventilation without ERV |  |  | CFM | TRM Version 5.0 | 2020-11-12 | 0 | 7.07 | 0 | -4.39 | 0 | 0 | 0 | 10.8 | 14 | Downstream | 0.7 | 1 | 1
COM-ERV-SH-363-01 | Current |  | Commercial | Energy Recovery Ventilation | Medium Use Group | New Construction/Retrofit | space heating | High Efficient 85% Energy Recovery Ventilation Medium Use Group (Hotel, Restaurant, Retail) | Ventilation with ERV Standalone | Ventilation without ERV |  |  | CFM | TRM Version 5.0 | 2020-11-12 | 0 | 3.93 | 0 | -2.44 | 0 | 0 | 0 | 10.8 | 14 | Downstream | 0.7 | 1 | 1
COM-ERV-SH-365-01 | Current |  | Commercial | Energy Recovery Ventilation | Low Use Group | New Construction/Retrofit | space heating | High Efficient 85% Energy Recovery Ventilation Low Use Group (Office, Warehouse, School) | Ventilation with ERV Standalone | Ventilation without ERV |  |  | CFM | TRM Version 5.0 | 2020-11-12 | 0 | 2.51 | 0 | -1.56 | 0 | 0 | 0 | 10.8 | 14 | Downstream | 0.7 | 1 | 1
COM-ERV-SH-367-01 | Current |  | Commercial | Energy Recovery Ventilation | Multi-Residential, Health Care, Nursing Homes | New Construction/Retrofit | space heating | High Efficient 85% Energy Recovery Ventilation High Use Group (Multi-Residential, Health Care, Nursing Homes) | Ventilation with ERV Standalone | Ventilation without ERV |  |  | CFM | TRM Version 5.0 | 2020-11-12 | 0 | 7.07 | 0 | -4.39 | 0 | 0 | 0 | 10.8 | 14 | Downstream | 0.7 | 1 | 1
COM-ERV-SH-369-01 | Current |  | Commercial | Energy Recovery Ventilation | Hotel | New Construction/Retrofit | space heating | High Efficient 85% Energy Recovery Ventilation Medium Use Group (Hotel, Restaurant, Retail) | Ventilation with ERV Standalone | Ventilation without ERV |  |  | CFM | TRM Version 5.0 | 2020-11-12 | 0 | 5.05 | 0 | -3.14 | 0 | 0 | 0 | 10.8 | 14 | Downstream | 0.7 | 1 | 1
COM-ERV-SH-371-01 | Current |  | Commercial | Energy Recovery Ventilation | Restaurant | New Construction/Retrofit | space heating | High Efficient 85% Energy Recovery Ventilation Medium Use Group (Hotel, Restaurant, Retail) | Ventilation with ERV Standalone | Ventilation without ERV |  |  | CFM | TRM Version 5.0 | 2020-11-12 | 0 | 3.66 | 0 | -2.28 | 0 | 0 | 0 | 10.8 | 14 | Downstream | 0.7 | 1 | 1
COM-ERV-SH-373-01 | Current |  | Commercial | Energy Recovery Ventilation | Retail | New Construction/Retrofit | space heating | High Efficient 85% Energy Recovery Ventilation Medium Use Group (Hotel, Restaurant, Retail) | Ventilation with ERV Standalone | Ventilation without ERV |  |  | CFM | TRM Version 5.0 | 2020-11-12 | 0 | 3.07 | 0 | -1.91 | 0 | 0 | 0 | 10.8 | 14 | Downstream | 0.7 | 1 | 1
COM-ERV-SH-375-01 | Current |  | Commercial | Energy Recovery Ventilation | Office | New Construction/Retrofit | space heating | High Efficient 85% Energy Recovery Ventilation Low Use Group (Office, Warehouse, School) | Ventilation with ERV Standalone | Ventilation without ERV |  |  | CFM | TRM Version 5.0 | 2020-11-12 | 0 | 2.69 | 0 | -1.67 | 0 | 0 | 0 | 10.8 | 14 | Downstream | 0.7 | 1 | 1
COM-ERV-SH-377-01 | Current |  | Commercial | Energy Recovery Ventilation | Warehouse | New Construction/Retrofit | space heating | High Efficient 85% Energy Recovery Ventilation Low Use Group (Office, Warehouse, School) | Ventilation with ERV Standalone | Ventilation without ERV |  |  | CFM | TRM Version 5.0 | 2020-11-12 | 0 | 2.57 | 0 | -1.6 | 0 | 0 | 0 | 10.8 | 14 | Downstream | 0.7 | 1 | 1
COM-ERV-SH-379-01 | Current |  | Commercial | Energy Recovery Ventilation | School | New Construction/Retrofit | space heating | High Efficient 85% Energy Recovery Ventilation Low Use Group (Office, Warehouse, School) | Ventilation with ERV Standalone | Ventilation without ERV |  |  | CFM | TRM Version 5.0 | 2020-11-12 | 0 | 2.27 | 0 | -1.41 | 0 | 0 | 0 | 10.8 | 14 | Downstream | 0.7 | 1 | 1
COM-HRV-SH-366-01 | Current |  | Commercial | Heat Recovery Ventialation | High Use | New Construction/Retrofit | space heating | High Efficient 55% Heat Recovery Ventilation High Use Group (Multi-Residential, Health Care, Nursing Homes) | Ventilation with HRV Integrated | Ventilation without HRV |  |  | CFM | TRM Version 5.0 | 2020-11-12 | 0 | 3.84 | 0 | 0 | 0 | 0 | 0 | 5.35 | 14 | Downstream | 0.05 | 1 | 1
COM-HRV-SH-368-01 | Current |  | Commercial | Heat Recovery Ventialation | Low Use | New Construction/Retrofit | space heating | High Efficient 55% Heat Recovery Ventilation Low Use Group (Office, Warehouse, School) | Ventilation with HRV Integrated | Ventilation without HRV |  |  | CFM | TRM Version 5.0 | 2020-11-12 | 0 | 1.36 | 0 | 0 | 0 | 0 | 0 | 5.35 | 14 | Downstream | 0.05 | 1 | 1
COM-HRV-SH-370-01 | Current |  | Commercial | Heat Recovery Ventialation | Medium Use | New Construction/Retrofit | space heating | High Efficient 55% Heat Recovery Ventilation Medium Use Group (Hotel, Restaurant, Retail) | Ventilation with HRV Integrated | Ventilation without HRV |  |  | CFM | TRM Version 5.0 | 2020-11-12 | 0 | 2.13 | 0 | 0 | 0 | 0 | 0 | 5.35 | 14 | Downstream | 0.05 | 1 | 1
COM-HRV-SH-372-01 | Current |  | Commercial | Heat Recovery Ventialation | High Use | New Construction/Retrofit | space heating | High Efficient 65% Heat Recovery Ventilation High Use Group (Multi-Residential, Health Care, Nursing Homes) | Ventilation with HRV Integrated | Ventilation without HRV |  |  | CFM | TRM Version 5.0 | 2020-11-12 | 0 | 4.54 | 0 | 0 | 0 | 0 | 0 | 6.35 | 14 | Downstream | 0.05 | 1 | 1
COM-HRV-SH-374-01 | Current |  | Commercial | Heat Recovery Ventialation | Low Use | New Construction/Retrofit | space heating | High Efficient 65% Heat Recovery Ventilation Low Use Group (Office, Warehouse, School) | Ventilation with HRV Integrated | Ventilation without HRV |  |  | CFM | TRM Version 5.0 | 2020-11-12 | 0 | 1.61 | 0 | 0 | 0 | 0 | 0 | 6.35 | 14 | Downstream | 0.05 | 1 | 1
COM-HRV-SH-376-01 | Current |  | Commercial | Heat Recovery Ventialation | Medium Use | New Construction/Retrofit | space heating | High Efficient 65% Heat Recovery Ventilation Medium Use Group (Hotel, Restaurant, Retail) | Ventilation with HRV Integrated | Ventilation without HRV |  |  | CFM | TRM Version 5.0 | 2020-11-12 | 0 | 2.52 | 0 | 0 | 0 | 0 | 0 | 6.35 | 14 | Downstream | 0.05 | 1 | 1
COM-HRV-SH-378-01 | Current |  | Commercial | Heat Recovery Ventialation | High Use | New Construction/Retrofit | space heating | High Efficient 75% Heat Recovery Ventilation High Use Group (Multi-Residential, Health Care, Nursing Homes) | Ventilation with HRV Integrated | Ventilation without HRV |  |  | CFM | TRM Version 5.0 | 2020-11-12 | 0 | 5.24 | 0 | 0 | 0 | 0 | 0 | 7.35 | 14 | Downstream | 0.05 | 1 | 1
COM-HRV-SH-380-01 | Current |  | Commercial | Heat Recovery Ventialation | Low Use | New Construction/Retrofit | space heating | High Efficient 75% Heat Recovery Ventilation Low Use Group (Office, Warehouse, School) | Ventilation with HRV Integrated | Ventilation without HRV |  |  | CFM | TRM Version 5.0 | 2020-11-12 | 0 | 1.86 | 0 | 0 | 0 | 0 | 0 | 7.35 | 14 | Downstream | 0.05 | 1 | 1
COM-HRV-SH-382-01 | Current |  | Commercial | Heat Recovery Ventialation | Medium Use | New Construction/Retrofit | space heating | High Efficient 75% Heat Recovery Ventilation Medium Use Group (Hotel, Restaurant, Retail) | Ventilation with HRV Integrated | Ventilation without HRV |  |  | CFM | TRM Version 5.0 | 2020-11-12 | 0 | 2.91 | 0 | 0 | 0 | 0 | 0 | 7.35 | 14 | Downstream | 0.05 | 1 | 1
COM-HRV-SH-384-01 | Current |  | Commercial | Heat Recovery Ventialation | High Use | New Construction/Retrofit | space heating | High Efficient 85% Heat Recovery Ventilation High Use Group (Multi-Residential, Health Care, Nursing Homes) | Ventilation with HRV Integrated | Ventilation without HRV |  |  | CFM | TRM Version 5.0 | 2020-11-12 | 0 | 5.93 | 0 | 0 | 0 | 0 | 0 | 8.35 | 14 | Downstream | 0.05 | 1 | 1
COM-HRV-SH-386-01 | Current |  | Commercial | Heat Recovery Ventialation | Low Use | New Construction/Retrofit | space heating | High Efficient 85% Heat Recovery Ventilation Low Use Group (Office, Warehouse, School) | Ventilation with HRV Integrated | Ventilation without HRV |  |  | CFM | TRM Version 5.0 | 2020-11-12 | 0 | 2.11 | 0 | 0 | 0 | 0 | 0 | 8.35 | 14 | Downstream | 0.05 | 1 | 1
COM-HRV-SH-388-01 | Current |  | Commercial | Heat Recovery Ventialation | Medium Use | New Construction/Retrofit | space heating | High Efficient 85% Heat Recovery Ventilation Medium Use Group (Hotel, Restaurant, Retail) | Ventilation with HRV Integrated | Ventilation without HRV |  |  | CFM | TRM Version 5.0 | 2020-11-12 | 0 | 3.3 | 0 | 0 | 0 | 0 | 0 | 8.35 | 14 | Downstream | 0.05 | 1 | 1
COM-HRV-SH-390-01 | Current |  | Commercial | Heat Recovery Ventialation | Multi-Family, Health Care and Nursing Homes | New Construction/Retrofit | space heating | High Efficient 55% Heat Recovery Ventilation High Use Group (Multi-Residential, Health Care, Nursing Homes) | Ventilation with HRV Integrated | Ventilation without HRV |  |  | CFM | TRM Version 5.0 | 2020-11-12 | 0 | 3.84 | 0 | 0 | 0 | 0 | 0 | 5.35 | 14 | Downstream | 0.05 | 1 | 1
COM-HRV-SH-392-01 | Current |  | Commercial | Heat Recovery Ventialation | Hotels | New Construction/Retrofit | space heating | High Efficient 55% Heat Recovery Ventilation Medium Use Group (Hotel, Restaurant, Retail) | Ventilation with HRV Integrated | Ventilation without HRV |  |  | CFM | TRM Version 5.0 | 2020-11-12 | 0 | 2.74 | 0 | 0 | 0 | 0 | 0 | 5.35 | 14 | Downstream | 0.05 | 1 | 1
COM-HRV-SH-394-01 | Current |  | Commercial | Heat Recovery Ventialation | Restaurant | New Construction/Retrofit | space heating | High Efficient 55% Heat Recovery Ventilation Medium Use Group (Hotel, Restaurant, Retail) | Ventilation with HRV Integrated | Ventilation without HRV |  |  | CFM | TRM Version 5.0 | 2020-11-12 | 0 | 1.99 | 0 | 0 | 0 | 0 | 0 | 5.35 | 14 | Downstream | 0.05 | 1 | 1
COM-HRV-SH-396-01 | Current |  | Commercial | Heat Recovery Ventialation | Retail | New Construction/Retrofit | space heating | High Efficient 55% Heat Recovery Ventilation Medium Use Group (Hotel, Restaurant, Retail) | Ventilation with HRV Integrated | Ventilation without HRV |  |  | CFM | TRM Version 5.0 | 2020-11-12 | 0 | 1.67 | 0 | 0 | 0 | 0 | 0 | 5.35 | 14 | Downstream | 0.05 | 1 | 1
COM-HRV-SH-398-01 | Current |  | Commercial | Heat Recovery Ventialation | Office | New Construction/Retrofit | space heating | High Efficient 55% Heat Recovery Ventilation Low Use Group (Office, Warehouse, School) | Ventilation with HRV Integrated | Ventilation without HRV |  |  | CFM | TRM Version 5.0 | 2020-11-12 | 0 | 1.46 | 0 | 0 | 0 | 0 | 0 | 5.35 | 14 | Downstream | 0.05 | 1 | 1
COM-HRV-SH-400-01 | Current |  | Commercial | Heat Recovery Ventialation | Warehouse | New Construction/Retrofit | space heating | High Efficient 55% Heat Recovery Ventilation Low Use Group (Office, Warehouse, School) | Ventilation with HRV Integrated | Ventilation without HRV |  |  | CFM | TRM Version 5.0 | 2020-11-12 | 0 | 1.39 | 0 | 0 | 0 | 0 | 0 | 5.35 | 14 | Downstream | 0.05 | 1 | 1
COM-HRV-SH-402-01 | Current |  | Commercial | Heat Recovery Ventialation | School | New Construction/Retrofit | space heating | High Efficient 55% Heat Recovery Ventilation Low Use Group (Office, Warehouse, School) | Ventilation with HRV Integrated | Ventilation without HRV |  |  | CFM | TRM Version 5.0 | 2020-11-12 | 0 | 1.23 | 0 | 0 | 0 | 0 | 0 | 5.35 | 14 | Downstream | 0.05 | 1 | 1
COM-HRV-SH-404-01 | Current |  | Commercial | Heat Recovery Ventialation | Multi-Family, Health Care and Nursing Homes | New Construction/Retrofit | space heating | High Efficient 65% Heat Recovery Ventilation High Use Group (Multi-Residential, Health Care, Nursing Homes) | Ventilation with HRV Integrated | Ventilation without HRV |  |  | CFM | TRM Version 5.0 | 2020-11-12 | 0 | 4.54 | 0 | 0 | 0 | 0 | 0 | 6.35 | 14 | Downstream | 0.05 | 1 | 1
COM-HRV-SH-406-01 | Current |  | Commercial | Heat Recovery Ventialation | Hotels | New Construction/Retrofit | space heating | High Efficient 65% Heat Recovery Ventilation Medium Use Group (Hotel, Restaurant, Retail) | Ventilation with HRV Integrated | Ventilation without HRV |  |  | CFM | TRM Version 5.0 | 2020-11-12 | 0 | 3.24 | 0 | 0 | 0 | 0 | 0 | 6.35 | 14 | Downstream | 0.05 | 1 | 1
COM-HRV-SH-408-01 | Current |  | Commercial | Heat Recovery Ventialation | Restaurant | New Construction/Retrofit | space heating | High Efficient 65% Heat Recovery Ventilation Medium Use Group (Hotel, Restaurant, Retail) | Ventilation with HRV Integrated | Ventilation without HRV |  |  | CFM | TRM Version 5.0 | 2020-11-12 | 0 | 2.35 | 0 | 0 | 0 | 0 | 0 | 6.35 | 14 | Downstream | 0.05 | 1 | 1
COM-HRV-SH-410-01 | Current |  | Commercial | Heat Recovery Ventialation | Retail | New Construction/Retrofit | space heating | High Efficient 65% Heat Recovery Ventilation Medium Use Group (Hotel, Restaurant, Retail) | Ventilation with HRV Integrated | Ventilation without HRV |  |  | CFM | TRM Version 5.0 | 2020-11-12 | 0 | 1.97 | 0 | 0 | 0 | 0 | 0 | 6.35 | 14 | Downstream | 0.05 | 1 | 1
COM-HRV-SH-412-01 | Current |  | Commercial | Heat Recovery Ventialation | Office | New Construction/Retrofit | space heating | High Efficient 65% Heat Recovery Ventilation Low Use Group (Office, Warehouse, School) | Ventilation with HRV Integrated | Ventilation without HRV |  |  | CFM | TRM Version 5.0 | 2020-11-12 | 0 | 1.73 | 0 | 0 | 0 | 0 | 0 | 6.35 | 14 | Downstream | 0.05 | 1 | 1
COM-HRV-SH-414-01 | Current |  | Commercial | Heat Recovery Ventialation | Warehouse | New Construction/Retrofit | space heating | High Efficient 65% Heat Recovery Ventilation Low Use Group (Office, Warehouse, School) | Ventilation with HRV Integrated | Ventilation without HRV |  |  | CFM | TRM Version 5.0 | 2020-11-12 | 0 | 1.65 | 0 | 0 | 0 | 0 | 0 | 6.35 | 14 | Downstream | 0.05 | 1 | 1
COM-HRV-SH-416-01 | Current |  | Commercial | Heat Recovery Ventialation | School | New Construction/Retrofit | space heating | High Efficient 65% Heat Recovery Ventilation Low Use Group (Office, Warehouse, School) | Ventilation with HRV Integrated | Ventilation without HRV |  |  | CFM | TRM Version 5.0 | 2020-11-12 | 0 | 1.46 | 0 | 0 | 0 | 0 | 0 | 6.35 | 14 | Downstream | 0.05 | 1 | 1
COM-HRV-SH-418-01 | Current |  | Commercial | Heat Recovery Ventialation | Multi-Family, Health Care and Nursing Homes | New Construction/Retrofit | space heating | High Efficient 75% Heat Recovery Ventilation High Use Group (Multi-Residential, Health Care, Nursing Homes) | Ventilation with HRV Integrated | Ventilation without HRV |  |  | CFM | TRM Version 5.0 | 2020-11-12 | 0 | 5.24 | 0 | 0 | 0 | 0 | 0 | 7.35 | 14 | Downstream | 0.05 | 1 | 1
COM-HRV-SH-420-01 | Current |  | Commercial | Heat Recovery Ventialation | Hotels | New Construction/Retrofit | space heating | High Efficient 75% Heat Recovery Ventilation Medium Use Group (Hotel, Restaurant, Retail) | Ventilation with HRV Integrated | Ventilation without HRV |  |  | CFM | TRM Version 5.0 | 2020-11-12 | 0 | 3.74 | 0 | 0 | 0 | 0 | 0 | 7.35 | 14 | Downstream | 0.05 | 1 | 1
COM-HRV-SH-422-01 | Current |  | Commercial | Heat Recovery Ventialation | Restaurant | New Construction/Retrofit | space heating | High Efficient 75% Heat Recovery Ventilation Medium Use Group (Hotel, Restaurant, Retail) | Ventilation with HRV Integrated | Ventilation without HRV |  |  | CFM | TRM Version 5.0 | 2020-11-12 | 0 | 2.71 | 0 | 0 | 0 | 0 | 0 | 7.35 | 14 | Downstream | 0.05 | 1 | 1
COM-HRV-SH-424-01 | Current |  | Commercial | Heat Recovery Ventialation | Retail | New Construction/Retrofit | space heating | High Efficient 75% Heat Recovery Ventilation Medium Use Group (Hotel, Restaurant, Retail) | Ventilation with HRV Integrated | Ventilation without HRV |  |  | CFM | TRM Version 5.0 | 2020-11-12 | 0 | 2.28 | 0 | 0 | 0 | 0 | 0 | 7.35 | 14 | Downstream | 0.05 | 1 | 1
COM-HRV-SH-426-01 | Current |  | Commercial | Heat Recovery Ventialation | Office | New Construction/Retrofit | space heating | High Efficient 75% Heat Recovery Ventilation Low Use Group (Office, Warehouse, School) | Ventilation with HRV Integrated | Ventilation without HRV |  |  | CFM | TRM Version 5.0 | 2020-11-12 | 0 | 1.99 | 0 | 0 | 0 | 0 | 0 | 7.35 | 14 | Downstream | 0.05 | 1 | 1
COM-HRV-SH-428-01 | Current |  | Commercial | Heat Recovery Ventialation | Warehouse | New Construction/Retrofit | space heating | High Efficient 75% Heat Recovery Ventilation Low Use Group (Office, Warehouse, School) | Ventilation with HRV Integrated | Ventilation without HRV |  |  | CFM | TRM Version 5.0 | 2020-11-12 | 0 | 1.9 | 0 | 0 | 0 | 0 | 0 | 7.35 | 14 | Downstream | 0.05 | 1 | 1
COM-HRV-SH-430-01 | Current |  | Commercial | Heat Recovery Ventialation | School | New Construction/Retrofit | space heating | High Efficient 75% Heat Recovery Ventilation Low Use Group (Office, Warehouse, School) | Ventilation with HRV Integrated | Ventilation without HRV |  |  | CFM | TRM Version 5.0 | 2020-11-12 | 0 | 1.68 | 0 | 0 | 0 | 0 | 0 | 7.35 | 14 | Downstream | 0.05 | 1 | 1
COM-HRV-SH-432-01 | Current |  | Commercial | Heat Recovery Ventialation | Multi-Family, Health Care and Nursing Homes | New Construction/Retrofit | space heating | High Efficient 85% Heat Recovery Ventilation High Use Group (Multi-Residential, Health Care, Nursing Homes) | Ventilation with HRV Integrated | Ventilation without HRV |  |  | CFM | TRM Version 5.0 | 2020-11-12 | 0 | 5.93 | 0 | 0 | 0 | 0 | 0 | 8.35 | 14 | Downstream | 0.05 | 1 | 1
COM-HRV-SH-434-01 | Current |  | Commercial | Heat Recovery Ventialation | Hotels | New Construction/Retrofit | space heating | High Efficient 85% Heat Recovery Ventilation Medium Use Group (Hotel, Restaurant, Retail) | Ventilation with HRV Integrated | Ventilation without HRV |  |  | CFM | TRM Version 5.0 | 2020-11-12 | 0 | 4.24 | 0 | 0 | 0 | 0 | 0 | 8.35 | 14 | Downstream | 0.05 | 1 | 1
COM-HRV-SH-436-01 | Current |  | Commercial | Heat Recovery Ventialation | Restaurant | New Construction/Retrofit | space heating | High Efficient 85% Heat Recovery Ventilation Medium Use Group (Hotel, Restaurant, Retail) | Ventilation with HRV Integrated | Ventilation without HRV |  |  | CFM | TRM Version 5.0 | 2020-11-12 | 0 | 3.07 | 0 | 0 | 0 | 0 | 0 | 8.35 | 14 | Downstream | 0.05 | 1 | 1
COM-HRV-SH-438-01 | Current |  | Commercial | Heat Recovery Ventialation | Retail | New Construction/Retrofit | space heating | High Efficient 85% Heat Recovery Ventilation Medium Use Group (Hotel, Restaurant, Retail) | Ventilation with HRV Integrated | Ventilation without HRV |  |  | CFM | TRM Version 5.0 | 2020-11-12 | 0 | 2.58 | 0 | 0 | 0 | 0 | 0 | 8.35 | 14 | Downstream | 0.05 | 1 | 1
COM-HRV-SH-440-01 | Current |  | Commercial | Heat Recovery Ventialation | Office | New Construction/Retrofit | space heating | High Efficient 85% Heat Recovery Ventilation Low Use Group (Office, Warehouse, School) | Ventilation with HRV Integrated | Ventilation without HRV |  |  | CFM | TRM Version 5.0 | 2020-11-12 | 0 | 2.26 | 0 | 0 | 0 | 0 | 0 | 8.35 | 14 | Downstream | 0.05 | 1 | 1
COM-HRV-SH-442-01 | Current |  | Commercial | Heat Recovery Ventialation | Warehouse | New Construction/Retrofit | space heating | High Efficient 85% Heat Recovery Ventilation Low Use Group (Office, Warehouse, School) | Ventilation with HRV Integrated | Ventilation without HRV |  |  | CFM | TRM Version 5.0 | 2020-11-12 | 0 | 2.15 | 0 | 0 | 0 | 0 | 0 | 8.35 | 14 | Downstream | 0.05 | 1 | 1
COM-HRV-SH-444-01 | Current |  | Commercial | Heat Recovery Ventialation | School | New Construction/Retrofit | space heating | High Efficient 85% Heat Recovery Ventilation Low Use Group (Office, Warehouse, School) | Ventilation with HRV Integrated | Ventilation without HRV |  |  | CFM | TRM Version 5.0 | 2020-11-12 | 0 | 1.91 | 0 | 0 | 0 | 0 | 0 | 8.35 | 14 | Downstream | 0.05 | 1 | 1
COM-HRV-SH-367-01 | Current |  | Commercial | Heat Recovery Ventialation | High Use | New Construction/Retrofit | space heating | High Efficient 55% Heat Recovery Ventilation High Use Group (Multi-Residential, Health Care, Nursing Homes) | Ventilation with HRV Standalone | Ventilation without HRV |  |  | CFM | TRM Version 5.0 | 2020-11-12 | 0 | 3.84 | 0 | -4.39 | 0 | 0 | 0 | 8.28 | 14 | Downstream | 0.05 | 1 | 1
COM-HRV-SH-369-01 | Current |  | Commercial | Heat Recovery Ventialation | Low Use | New Construction/Retrofit | space heating | High Efficient 55% Heat Recovery Ventilation Low Use Group (Office, Warehouse, School) | Ventilation with HRV Standalone | Ventilation without HRV |  |  | CFM | TRM Version 5.0 | 2020-11-12 | 0 | 1.36 | 0 | -1.56 | 0 | 0 | 0 | 8.28 | 14 | Downstream | 0.05 | 1 | 1
COM-HRV-SH-371-01 | Current |  | Commercial | Heat Recovery Ventialation | Medium Use | New Construction/Retrofit | space heating | High Efficient 55% Heat Recovery Ventilation Medium Use Group (Hotel, Restaurant, Retail) | Ventilation with HRV Standalone | Ventilation without HRV |  |  | CFM | TRM Version 5.0 | 2020-11-12 | 0 | 2.13 | 0 | -2.44 | 0 | 0 | 0 | 8.28 | 14 | Downstream | 0.05 | 1 | 1
COM-HRV-SH-373-01 | Current |  | Commercial | Heat Recovery Ventialation | High Use | New Construction/Retrofit | space heating | High Efficient 65% Heat Recovery Ventilation High Use Group (Multi-Residential, Health Care, Nursing Homes) | Ventilation with HRV Standalone | Ventilation without HRV |  |  | CFM | TRM Version 5.0 | 2020-11-12 | 0 | 4.54 | 0 | -4.39 | 0 | 0 | 0 | 9.28 | 14 | Downstream | 0.05 | 1 | 1
COM-HRV-SH-375-01 | Current |  | Commercial | Heat Recovery Ventialation | Low Use | New Construction/Retrofit | space heating | High Efficient 65% Heat Recovery Ventilation Low Use Group (Office, Warehouse, School) | Ventilation with HRV Standalone | Ventilation without HRV |  |  | CFM | TRM Version 5.0 | 2020-11-12 | 0 | 1.61 | 0 | -1.56 | 0 | 0 | 0 | 9.28 | 14 | Downstream | 0.05 | 1 | 1
COM-HRV-SH-377-01 | Current |  | Commercial | Heat Recovery Ventialation | Medium Use | New Construction/Retrofit | space heating | High Efficient 65% Heat Recovery Ventilation Medium Use Group (Hotel, Restaurant, Retail) | Ventilation with HRV Standalone | Ventilation without HRV |  |  | CFM | TRM Version 5.0 | 2020-11-12 | 0 | 2.52 | 0 | -2.44 | 0 | 0 | 0 | 9.28 | 14 | Downstream | 0.05 | 1 | 1
COM-HRV-SH-379-01 | Current |  | Commercial | Heat Recovery Ventialation | High Use | New Construction/Retrofit | space heating | High Efficient 75% Heat Recovery Ventilation High Use Group (Multi-Residential, Health Care, Nursing Homes) | Ventilation with HRV Standalone | Ventilation without HRV |  |  | CFM | TRM Version 5.0 | 2020-11-12 | 0 | 5.24 | 0 | -4.39 | 0 | 0 | 0 | 10.28 | 14 | Downstream | 0.05 | 1 | 1
COM-HRV-SH-381-01 | Current |  | Commercial | Heat Recovery Ventialation | Low Use | New Construction/Retrofit | space heating | High Efficient 75% Heat Recovery Ventilation Low Use Group (Office, Warehouse, School) | Ventilation with HRV Standalone | Ventilation without HRV |  |  | CFM | TRM Version 5.0 | 2020-11-12 | 0 | 1.86 | 0 | -1.56 | 0 | 0 | 0 | 10.28 | 14 | Downstream | 0.05 | 1 | 1
COM-HRV-SH-383-01 | Current |  | Commercial | Heat Recovery Ventialation | Medium Use | New Construction/Retrofit | space heating | High Efficient 75% Heat Recovery Ventilation Medium Use Group (Hotel, Restaurant, Retail) | Ventilation with HRV Standalone | Ventilation without HRV |  |  | CFM | TRM Version 5.0 | 2020-11-12 | 0 | 2.91 | 0 | -2.44 | 0 | 0 | 0 | 10.28 | 14 | Downstream | 0.05 | 1 | 1
COM-HRV-SH-385-01 | Current |  | Commercial | Heat Recovery Ventialation | High Use | New Construction/Retrofit | space heating | High Efficient 85% Heat Recovery Ventilation High Use Group (Multi-Residential, Health Care, Nursing Homes) | Ventilation with HRV Standalone | Ventilation without HRV |  |  | CFM | TRM Version 5.0 | 2020-11-12 | 0 | 5.93 | 0 | -4.39 | 0 | 0 | 0 | 11.28 | 14 | Downstream | 0.05 | 1 | 1
COM-HRV-SH-387-01 | Current |  | Commercial | Heat Recovery Ventialation | Low Use | New Construction/Retrofit | space heating | High Efficient 85% Heat Recovery Ventilation Low Use Group (Office, Warehouse, School) | Ventilation with HRV Standalone | Ventilation without HRV |  |  | CFM | TRM Version 5.0 | 2020-11-12 | 0 | 2.11 | 0 | -1.56 | 0 | 0 | 0 | 11.28 | 14 | Downstream | 0.05 | 1 | 1
COM-HRV-SH-389-01 | Current |  | Commercial | Heat Recovery Ventialation | Medium Use | New Construction/Retrofit | space heating | High Efficient 85% Heat Recovery Ventilation Medium Use Group (Hotel, Restaurant, Retail) | Ventilation with HRV Standalone | Ventilation without HRV |  |  | CFM | TRM Version 5.0 | 2020-11-12 | 0 | 3.3 | 0 | -2.44 | 0 | 0 | 0 | 11.28 | 14 | Downstream | 0.05 | 1 | 1
COM-HRV-SH-391-01 | Current |  | Commercial | Heat Recovery Ventialation | Multi-Family, Health Care and Nursing Homes | New Construction/Retrofit | space heating | High Efficient 55% Heat Recovery Ventilation High Use Group (Multi-Residential, Health Care, Nursing Homes) | Ventilation with HRV Standalone | Ventilation without HRV |  |  | CFM | TRM Version 5.0 | 2020-11-12 | 0 | 3.84 | 0 | -4.39 | 0 | 0 | 0 | 8.28 | 14 | Downstream | 0.05 | 1 | 1
COM-HRV-SH-393-01 | Current |  | Commercial | Heat Recovery Ventialation | Hotels | New Construction/Retrofit | space heating | High Efficient 55% Heat Recovery Ventilation Medium Use Group (Hotel, Restaurant, Retail) | Ventilation with HRV Standalone | Ventilation without HRV |  |  | CFM | TRM Version 5.0 | 2020-11-12 | 0 | 2.74 | 0 | -3.14 | 0 | 0 | 0 | 8.28 | 14 | Downstream | 0.05 | 1 | 1
COM-HRV-SH-395-01 | Current |  | Commercial | Heat Recovery Ventialation | Restaurant | New Construction/Retrofit | space heating | High Efficient 55% Heat Recovery Ventilation Medium Use Group (Hotel, Restaurant, Retail) | Ventilation with HRV Standalone | Ventilation without HRV |  |  | CFM | TRM Version 5.0 | 2020-11-12 | 0 | 1.99 | 0 | -2.28 | 0 | 0 | 0 | 8.28 | 14 | Downstream | 0.05 | 1 | 1
COM-HRV-SH-397-01 | Current |  | Commercial | Heat Recovery Ventialation | Retail | New Construction/Retrofit | space heating | High Efficient 55% Heat Recovery Ventilation Medium Use Group (Hotel, Restaurant, Retail) | Ventilation with HRV Standalone | Ventilation without HRV |  |  | CFM | TRM Version 5.0 | 2020-11-12 | 0 | 1.67 | 0 | -1.91 | 0 | 0 | 0 | 8.28 | 14 | Downstream | 0.05 | 1 | 1
COM-HRV-SH-399-01 | Current |  | Commercial | Heat Recovery Ventialation | Office | New Construction/Retrofit | space heating | High Efficient 55% Heat Recovery Ventilation Low Use Group (Office, Warehouse, School) | Ventilation with HRV Standalone | Ventilation without HRV |  |  | CFM | TRM Version 5.0 | 2020-11-12 | 0 | 1.46 | 0 | -1.67 | 0 | 0 | 0 | 8.28 | 14 | Downstream | 0.05 | 1 | 1
COM-HRV-SH-401-01 | Current |  | Commercial | Heat Recovery Ventialation | Warehouse | New Construction/Retrofit | space heating | High Efficient 55% Heat Recovery Ventilation Low Use Group (Office, Warehouse, School) | Ventilation with HRV Standalone | Ventilation without HRV |  |  | CFM | TRM Version 5.0 | 2020-11-12 | 0 | 1.39 | 0 | -1.6 | 0 | 0 | 0 | 8.28 | 14 | Downstream | 0.05 | 1 | 1
COM-HRV-SH-403-01 | Current |  | Commercial | Heat Recovery Ventialation | School | New Construction/Retrofit | space heating | High Efficient 55% Heat Recovery Ventilation Low Use Group (Office, Warehouse, School) | Ventilation with HRV Standalone | Ventilation without HRV |  |  | CFM | TRM Version 5.0 | 2020-11-12 | 0 | 1.23 | 0 | -1.41 | 0 | 0 | 0 | 8.28 | 14 | Downstream | 0.05 | 1 | 1
COM-HRV-SH-405-01 | Current |  | Commercial | Heat Recovery Ventialation | Multi-Family, Health Care and Nursing Homes | New Construction/Retrofit | space heating | High Efficient 65% Heat Recovery Ventilation High Use Group (Multi-Residential, Health Care, Nursing Homes) | Ventilation with HRV Standalone | Ventilation without HRV |  |  | CFM | TRM Version 5.0 | 2020-11-12 | 0 | 4.54 | 0 | -4.39 | 0 | 0 | 0 | 9.28 | 14 | Downstream | 0.05 | 1 | 1
COM-HRV-SH-407-01 | Current |  | Commercial | Heat Recovery Ventialation | Hotels | New Construction/Retrofit | space heating | High Efficient 65% Heat Recovery Ventilation Medium Use Group (Hotel, Restaurant, Retail) | Ventilation with HRV Standalone | Ventilation without HRV |  |  | CFM | TRM Version 5.0 | 2020-11-12 | 0 | 3.24 | 0 | -3.14 | 0 | 0 | 0 | 9.28 | 14 | Downstream | 0.05 | 1 | 1
COM-HRV-SH-409-01 | Current |  | Commercial | Heat Recovery Ventialation | Restaurant | New Construction/Retrofit | space heating | High Efficient 65% Heat Recovery Ventilation Medium Use Group (Hotel, Restaurant, Retail) | Ventilation with HRV Standalone | Ventilation without HRV |  |  | CFM | TRM Version 5.0 | 2020-11-12 | 0 | 2.35 | 0 | -2.28 | 0 | 0 | 0 | 9.28 | 14 | Downstream | 0.05 | 1 | 1
COM-HRV-SH-411-01 | Current |  | Commercial | Heat Recovery Ventialation | Retail | New Construction/Retrofit | space heating | High Efficient 65% Heat Recovery Ventilation Medium Use Group (Hotel, Restaurant, Retail) | Ventilation with HRV Standalone | Ventilation without HRV |  |  | CFM | TRM Version 5.0 | 2020-11-12 | 0 | 1.97 | 0 | -1.91 | 0 | 0 | 0 | 9.28 | 14 | Downstream | 0.05 | 1 | 1
COM-HRV-SH-413-01 | Current |  | Commercial | Heat Recovery Ventialation | Office | New Construction/Retrofit | space heating | High Efficient 65% Heat Recovery Ventilation Low Use Group (Office, Warehouse, School) | Ventilation with HRV Standalone | Ventilation without HRV |  |  | CFM | TRM Version 5.0 | 2020-11-12 | 0 | 1.73 | 0 | -1.67 | 0 | 0 | 0 | 9.28 | 14 | Downstream | 0.05 | 1 | 1
COM-HRV-SH-415-01 | Current |  | Commercial | Heat Recovery Ventialation | Warehouse | New Construction/Retrofit | space heating | High Efficient 65% Heat Recovery Ventilation Low Use Group (Office, Warehouse, School) | Ventilation with HRV Standalone | Ventilation without HRV |  |  | CFM | TRM Version 5.0 | 2020-11-12 | 0 | 1.65 | 0 | -1.6 | 0 | 0 | 0 | 9.28 | 14 | Downstream | 0.05 | 1 | 1
COM-HRV-SH-417-01 | Current |  | Commercial | Heat Recovery Ventialation | School | New Construction/Retrofit | space heating | High Efficient 65% Heat Recovery Ventilation Low Use Group (Office, Warehouse, School) | Ventilation with HRV Standalone | Ventilation without HRV |  |  | CFM | TRM Version 5.0 | 2020-11-12 | 0 | 1.46 | 0 | -1.41 | 0 | 0 | 0 | 9.28 | 14 | Downstream | 0.05 | 1 | 1
COM-HRV-SH-419-01 | Current |  | Commercial | Heat Recovery Ventialation | Multi-Family, Health Care and Nursing Homes | New Construction/Retrofit | space heating | High Efficient 75% Heat Recovery Ventilation High Use Group (Multi-Residential, Health Care, Nursing Homes) | Ventilation with HRV Standalone | Ventilation without HRV |  |  | CFM | TRM Version 5.0 | 2020-11-12 | 0 | 5.24 | 0 | -4.39 | 0 | 0 | 0 | 10.28 | 14 | Downstream | 0.05 | 1 | 1
COM-HRV-SH-421-01 | Current |  | Commercial | Heat Recovery Ventialation | Hotels | New Construction/Retrofit | space heating | High Efficient 75% Heat Recovery Ventilation Medium Use Group (Hotel, Restaurant, Retail) | Ventilation with HRV Standalone | Ventilation without HRV |  |  | CFM | TRM Version 5.0 | 2020-11-12 | 0 | 3.74 | 0 | -3.14 | 0 | 0 | 0 | 10.28 | 14 | Downstream | 0.05 | 1 | 1
COM-HRV-SH-423-01 | Current |  | Commercial | Heat Recovery Ventialation | Restaurant | New Construction/Retrofit | space heating | High Efficient 75% Heat Recovery Ventilation Medium Use Group (Hotel, Restaurant, Retail) | Ventilation with HRV Standalone | Ventilation without HRV |  |  | CFM | TRM Version 5.0 | 2020-11-12 | 0 | 2.71 | 0 | -2.28 | 0 | 0 | 0 | 10.28 | 14 | Downstream | 0.05 | 1 | 1
COM-HRV-SH-425-01 | Current |  | Commercial | Heat Recovery Ventialation | Retail | New Construction/Retrofit | space heating | High Efficient 75% Heat Recovery Ventilation Medium Use Group (Hotel, Restaurant, Retail) | Ventilation with HRV Standalone | Ventilation without HRV |  |  | CFM | TRM Version 5.0 | 2020-11-12 | 0 | 2.28 | 0 | -1.91 | 0 | 0 | 0 | 10.28 | 14 | Downstream | 0.05 | 1 | 1
COM-HRV-SH-427-01 | Current |  | Commercial | Heat Recovery Ventialation | Office | New Construction/Retrofit | space heating | High Efficient 75% Heat Recovery Ventilation Low Use Group (Office, Warehouse, School) | Ventilation with HRV Standalone | Ventilation without HRV |  |  | CFM | TRM Version 5.0 | 2020-11-12 | 0 | 1.99 | 0 | -1.67 | 0 | 0 | 0 | 10.28 | 14 | Downstream | 0.05 | 1 | 1
COM-HRV-SH-429-01 | Current |  | Commercial | Heat Recovery Ventialation | Warehouse | New Construction/Retrofit | space heating | High Efficient 75% Heat Recovery Ventilation Low Use Group (Office, Warehouse, School) | Ventilation with HRV Standalone | Ventilation without HRV |  |  | CFM | TRM Version 5.0 | 2020-11-12 | 0 | 1.9 | 0 | -1.6 | 0 | 0 | 0 | 10.28 | 14 | Downstream | 0.05 | 1 | 1
COM-HRV-SH-431-01 | Current |  | Commercial | Heat Recovery Ventialation | School | New Construction/Retrofit | space heating | High Efficient 75% Heat Recovery Ventilation Low Use Group (Office, Warehouse, School) | Ventilation with HRV Standalone | Ventilation without HRV |  |  | CFM | TRM Version 5.0 | 2020-11-12 | 0 | 1.68 | 0 | -1.41 | 0 | 0 | 0 | 10.28 | 14 | Downstream | 0.05 | 1 | 1
COM-HRV-SH-433-01 | Current |  | Commercial | Heat Recovery Ventialation | Multi-Family, Health Care and Nursing Homes | New Construction/Retrofit | space heating | High Efficient 85% Heat Recovery Ventilation High Use Group (Multi-Residential, Health Care, Nursing Homes) | Ventilation with HRV Standalone | Ventilation without HRV |  |  | CFM | TRM Version 5.0 | 2020-11-12 | 0 | 5.93 | 0 | -4.39 | 0 | 0 | 0 | 11.28 | 14 | Downstream | 0.05 | 1 | 1
COM-HRV-SH-435-01 | Current |  | Commercial | Heat Recovery Ventialation | Hotels | New Construction/Retrofit | space heating | High Efficient 85% Heat Recovery Ventilation Medium Use Group (Hotel, Restaurant, Retail) | Ventilation with HRV Standalone | Ventilation without HRV |  |  | CFM | TRM Version 5.0 | 2020-11-12 | 0 | 4.24 | 0 | -3.14 | 0 | 0 | 0 | 11.28 | 14 | Downstream | 0.05 | 1 | 1
COM-HRV-SH-437-01 | Current |  | Commercial | Heat Recovery Ventialation | Restaurant | New Construction/Retrofit | space heating | High Efficient 85% Heat Recovery Ventilation Medium Use Group (Hotel, Restaurant, Retail) | Ventilation with HRV Standalone | Ventilation without HRV |  |  | CFM | TRM Version 5.0 | 2020-11-12 | 0 | 3.07 | 0 | -2.28 | 0 | 0 | 0 | 11.28 | 14 | Downstream | 0.05 | 1 | 1
COM-HRV-SH-439-01 | Current |  | Commercial | Heat Recovery Ventialation | Retail | New Construction/Retrofit | space heating | High Efficient 85% Heat Recovery Ventilation Medium Use Group (Hotel, Restaurant, Retail) | Ventilation with HRV Standalone | Ventilation without HRV |  |  | CFM | TRM Version 5.0 | 2020-11-12 | 0 | 2.58 | 0 | -1.91 | 0 | 0 | 0 | 11.28 | 14 | Downstream | 0.05 | 1 | 1
COM-HRV-SH-441-01 | Current |  | Commercial | Heat Recovery Ventialation | Office | New Construction/Retrofit | space heating | High Efficient 85% Heat Recovery Ventilation Low Use Group (Office, Warehouse, School) | Ventilation with HRV Standalone | Ventilation without HRV |  |  | CFM | TRM Version 5.0 | 2020-11-12 | 0 | 2.26 | 0 | -1.67 | 0 | 0 | 0 | 11.28 | 14 | Downstream | 0.05 | 1 | 1
COM-HRV-SH-443-01 | Current |  | Commercial | Heat Recovery Ventialation | Warehouse | New Construction/Retrofit | space heating | High Efficient 85% Heat Recovery Ventilation Low Use Group (Office, Warehouse, School) | Ventilation with HRV Standalone | Ventilation without HRV |  |  | CFM | TRM Version 5.0 | 2020-11-12 | 0 | 2.15 | 0 | -1.6 | 0 | 0 | 0 | 11.28 | 14 | Downstream | 0.05 | 1 | 1
COM-HRV-SH-445-01 | Current |  | Commercial | Heat Recovery Ventialation | School | New Construction/Retrofit | space heating | High Efficient 85% Heat Recovery Ventilation Low Use Group (Office, Warehouse, School) | Ventilation with HRV Standalone | Ventilation without HRV |  |  | CFM | TRM Version 5.0 | 2020-11-12 | 0 | 1.91 | 0 | -1.41 | 0 | 0 | 0 | 11.28 | 14 | Downstream | 0.05 | 1 | 1
COM-CM-SH-498-01 | Current |  | Commercial | Condensing Make Up Air Unit | Commercial | New Construction/Natural Replacement | space heating | Condensing Make Up Air Unit (MUA) - Commercial | VFD | Conventional MUA | 80% Thermal Efficiency |  | CFM | TRM Version 5.0 | 2020-11-12 | 0 | 2.03 | 0 | 2.04 | 0 | 0 | 870 | 1.02 | 20 | Downstream | 0.05 | 1 | 1
COM-CM-SH-501-01 | Current |  | Commercial | Condensing Make Up Air Unit | Multi-Residential and Long Term Care | New Construction/Natural Replacement | space heating | Condensing Make Up Air Unit (MUA) - Commercial | VFD | Conventional MUA | 80% Thermal Efficiency |  | CFM | TRM Version 5.0 | 2020-11-12 | 0 | 3 | 0 | 2.3 | 0 | 0 | 870 | 1.02 | 20 | Downstream | 0.05 | 1 | 1
MRS-SH-WH-569-01 | Current |  | Commercial | Showerhead | Multi-residential | New Construction | water heating | Low-flow showerhead | 1.25 GPM |  | 2.0 GPM | unit |  | TRM Version 6.0 | 2021-12-16 | 23.2 | 0 | 0 | 0 | 7775 | 0 | actual cost |  | 10 | Downstream | 0.1 | 0.8576 | 1
MRS-SH-WH-571-01 | Current |  | Commercial | Showerhead | Multi-residential | Retrofit | water heating | Low-flow showerhead | 1.25 GPM | Average existing stock | 2.5 GPM | unit |  | TRM Version 6.0 | 2021-12-16 | 38.7 | 0 | 0 | 0 | 11734 | 0 | actual cost |  | 10 | Downstream | 0.1 | 0.8576 | 1
MRS-SH-WH-570-01 | Current |  | Commercial | Showerhead | Multi-residential | New Construction | water heating | Low-flow showerhead | 1.50 GPM |  | 2.0 GPM | unit |  | TRM Version 6.0 | 2021-12-16 | 15.5 | 0 | 0 | 0 | 4107 | 0 | actual cost |  | 10 | Downstream | 0.1 | 0.8576 | 1
MRS-SH-WH-572-01 | Current |  | Commercial | Showerhead | Multi-residential | Retrofit | water heating | Low-flow showerhead | 1.50 GPM | Average existing stock | 2.5 GPM | unit |  | TRM Version 6.0 | 2021-12-16 | 31 | 0 | 0 | 0 | 8068 | 0 | actual cost |  | 10 | Downstream | 0.1 | 0.8576 | 1
COM-CMB-FS-621-01 | Current |  | Commercial | Combination Oven |  | New Construction/Natural Replacement | food service | Energy Star Combination Oven | Energy Star Rated Combiniation Oven, 15-28 pan | Conventional combination oven |  | unit |  | TRM Version 6.0 | 2021-12-16 | 1295 | 0 | 4747 | 0 | 51684 | 0 | 5007 | 0 | 12 | Downstream | 0.2 | 1 | 1
COM-CMB-FS-622-01 | Current |  | Commercial | Combination Oven |  | New Construction/Natural Replacement | food service | Energy Star Combination Oven | Energy Star Rated Combiniation Oven, 29+ pan | Conventional combination oven |  | unit |  | TRM Version 6.0 | 2021-12-16 | 1048 | 0 | 485 | 0 | 599459 | 0 | 8507 | 0 | 12 | Downstream | 0.2 | 1 | 1
COM-CMB-FS-623-01 | Current |  | Commercial | Combination Oven |  | New Construction/Natural Replacement | food service | Energy Star Combination Oven | Energy Star Rated Combiniation Oven, average | Conventional combination oven |  | unit |  | TRM Version 6.0 | 2021-12-16 | 1186 | 0 | 2088 | 0 | 145120 | 0 | 4440 | 0 | 12 | Downstream | 0.2 | 1 | 1
COM-CO-FS-520-01 | Current |  | Commercial | Convection Ovens |  | New Construction/Natural Replacement | food service | Energy Star Convection Ovens | Energy Star Rated Convection Oven (Full Size) | Conventional Convection Oven (Full Size) |  | unit |  | TRM Version 6.0 | 2021-12-16 | 954 | 0 | 44.2 | 0 | 0 | 0 | 1200 | 0 | 12 | Downstream | 0.2 | 1 | 1
COM-RO-FS-651-01 | Current |  | Commercial | Rack Oven |  | New Construction/Natural Replacement | food service | ENERGY STAR Rack Oven | Energy Star Rated Rack Oven, Double | Conventiona rack oven |  | unit |  | TRM Version 6.0 | 2021-12-16 | 1187 | 0 | 1858 | 0 | 0 | 0 | 2591 | 0 | 12 | Downstream | 0.2 | 1 | 1
COM-RO-FS-650-01 | Current |  | Commercial | Rack Oven |  | New Construction/Natural Replacement | food service | ENERGY STAR Rack Oven | Energy Star Rated Rack Oven, Single | Conventiona rack oven |  | unit |  | TRM Version 6.0 | 2021-12-16 | 915 | 0 | 826 | 0 | 0 | 0 | 1544 | 0 | 12 | Downstream | 0.2 | 1 | 1
COM-OL-WH-329-01 | Current |  | Commercial | Ozone Laundry |  | New Construction/Retrofit | water heating | Commercial Ozone Laundry Treatment | Ozone Treatment Tunnel Washer <= 120 lbs | Commercial laundry with no ozone treatment system |  |  | lbs/yr | TRM Version 7.0 | 2022-11-30 | 0 | 0.0295 | 0 | 0.0015 | 0 | 1.29 | 71429 | 0 | 15 | Downstream | 0.08 | 1 | 1
COM-OL-WH-331-01 | Current |  | Commercial | Ozone Laundry |  | New Construction/Retrofit | water heating | Commercial Ozone Laundry Treatment | Ozone Treatment Tunnel Washer=> 500 lbs | Commercial laundry with no ozone treatment system |  |  | lbs/yr | TRM Version 7.0 | 2022-11-30 | 0 | 0.0295 | 0 | 0.0015 | 0 | 1.29 | 228571 | 0 | 15 | Downstream | 0.08 | 1 | 1
COM-OL-WH-330-01 | Current |  | Commercial | Ozone Laundry |  | New Construction/Retrofit | water heating | Commercial Ozone Laundry Treatment | Ozone Treatment Tunnel Washer 121 lbs to 499 lbs | Commercial laundry with no ozone treatment system |  |  | lbs/yr | TRM Version 7.0 | 2022-11-30 | 0 | 0.0295 | 0 | 0.0015 | 0 | 1.29 | 150000 | 0 | 15 | Downstream | 0.08 | 1 | 1
COM-OL-WH-326-01 | Current |  | Commercial | Ozone Laundry |  | New Construction/Retrofit | water heating | Commercial Ozone Laundry Treatment | Ozone Treatment Washer extractor =< 60 lbs | Commercial laundry with no ozone treatment system |  |  | lbs/yr | TRM Version 7.0 | 2022-11-30 | 0 | 0.0376 | 0 | 0.00211 | 0 | 2.1 | 15714 | 0 | 15 | Downstream | 0.08 | 1 | 1
COM-OL-WH-327-01 | Current |  | Commercial | Ozone Laundry |  | New Construction/Retrofit | water heating | Commercial Ozone Laundry Treatment | Ozone Treatment Washer extractor 61 lbs to 499 lbs | Commercial laundry with no ozone treatment system |  |  | lbs/yr | TRM Version 7.0 | 2022-11-30 | 0 | 0.0376 | 0 | 0.00211 | 0 | 2.1 | 35714 | 0 | 15 | Downstream | 0.08 | 1 | 1
COM-OL-WH-328-01 | Current |  | Commercial | Ozone Laundry |  | New Construction/Retrofit | water heating | Commercial Ozone Laundry Treatment | Ozone Treatment Washer extractor=> 500 lbs | Commercial laundry with no ozone treatment system |  |  | lbs/yr | TRM Version 7.0 | 2022-11-30 | 0 | 0.0376 | 0 | 0.00211 | 0 | 2.1 | 44286 | 0 | 15 | Downstream | 0.08 | 1 | 1
COM-CMB-FS-620-01 | Current |  | Commercial | Combination Oven |  | New Construction/Natural Replacement | food service | Energy Star Combination Oven | Energy Star Rated Combination Oven, 6-14 pan | Conventional combination oven |  | unit |  | TRM Version 6.0 | 2021-12-16 | 1104 | 0 | 72 | 0 | 209664 | 0 | 3941 | 0 | 12 | Downstream | 0.2 | 1 | 1
COM-GR-FS-800-02 | Current |  | Commercial | Griddles |  | New Construction/Natural Replacement | food service | Energy Star Griddle | ENERGY STAR Certified Griddle | Non-ENERGY STAR Griddle |  |  | ft | TRM Version 7.0 | 2022-11-30 | 0 | 439 | 0 | 0 | 0 | 0 | 0 | 1096 | 12 | Downstream | 0.2 | 1 | 1
COM-GR-FS-801-02 | Current |  | Commercial | Griddles |  | New Construction/Natural Replacement | food service | Energy Star Griddle | ENERGY STAR Certified Griddle | Non-ENERGY STAR Griddle |  | unit |  | TRM Version 7.0 | 2022-11-30 | 1974 | 0 | 0 | 0 | 0 | 0 | 4581 | 0 | 12 | Downstream | 0.2 | 1 | 1
COM-FR-FS-325-01 | Current | Split measure into two Vat sizes | Commercial | Fryer |  | New Construction/Natural Replacement | food service | Energy Star Fryer, Standard Vat | Energy Star Rated Fryer | Non-Energy Star rated Fryer |  | unit |  | TRM Version 7.0 | 2022-11-30 | 1466 | 0 | 0 | 0 | 0 | 0 | 2657 | 0 | 12 | Downstream | 0.2 | 1 | 1
COM-FR-FS-326-01 | Current | Split measure into two Vat sizes | Commercial | Fryer |  | New Construction/Natural Replacement | food service | Energy Star Fryer, Large Vat | Energy Star Rated Fryer | Non-Energy Star rated Fryer |  | unit |  | TRM Version 7.0 | 2022-11-30 | 1709 | 0 | 0 | 0 | 0 | 0 | 3113 | 0 | 12 | Downstream | 0.2 | 1 | 1
COM-SC-FS-325-01 | Current |  | Commercial | Steam Cookers |  | New Construction/Natural Replacement | food service | Energy Star Steam Cookers | Energy Star Rated Steam Cooker | Boiler-based steam cooker |  | unit |  | TRM Version 7.0 | 2022-11-30 | 8461 | 0 | 0 | 0 | 1109458 | 0 | 3045 | 0 | 12 | Downstream | 0.2 | 1 | 1
COM-CNB-FS-810-02 | Current | New measure in TRM V7.0 | Commercial | Conveyor Broiler |  | New Construction/Natural Replacement | food service | Energy-Efficient Conveyor Broiler, <22" width | high-efficiency conveyor broiler with a catalyst and an idle input rate less than the rates listed below or a dual stage or modulating gas valve with a capability of throttling the input rate below the idle rates <40,000 Btu/h | Conventional Conveyor Broiler |  | unit |  | TRM Version 7.0 | 2022-11-30 | 1954 | 0 | 2443 | 0 | 0 | 0 | 3154 | 0 | 12 | Downstream | 0.2 | 1 | 1
COM-CNB-FS-811-02 | Current | New measure in TRM V7.0 | Commercial | Conveyor Broiler |  | New Construction/Natural Replacement | food service | Energy-Efficient Conveyor Broiler, 22" - 26" width | high-efficiency conveyor broiler with a catalyst and an idle input rate less than the rates listed below or a dual stage or modulating gas valve with a capability of throttling the input rate below the idle rates <60,000 Btu/h | Conventional Conveyor Broiler |  | unit |  | TRM Version 7.0 | 2022-11-30 | 3070 | 0 | 3839 | 0 | 0 | 0 | 3933 | 0 | 12 | Downstream | 0.2 | 1 | 1
COM-CNB-FS-812-02 | Current | New measure in TRM V7.0 | Commercial | Conveyor Broiler |  | New Construction/Natural Replacement | food service | Energy-Efficient Conveyor Broiler, > 26" width | high-efficiency conveyor broiler with a catalyst and an idle input rate less than the rates listed below or a dual stage or modulating gas valve with a capability of throttling the input rate below the idle rates <70,000 Btu/h | Conventional Conveyor Broiler |  | unit |  | TRM Version 7.0 | 2022-11-30 | 3768 | 0 | 4712 | 0 | 0 | 0 | 4586 | 0 | 12 | Downstream | 0.2 | 1 | 1
COM-CNO-FS-806-02 | Current | New measure in TRM V7.0 | Commercial | Conveyor Oven |  | New Construction/Natural Replacement | food service | Energy-Efficient Conveyor Oven, large ≥ 1520 sq in | Large Conveyor Oven Chamber Area ≥ 1520 sq in, 45% cooking efficiency | Conventional Conveyor Oven |  | unit |  | TRM Version 7.0 | 2022-11-30 | 1519 | 0 | 2601 | 0 | 0 | 0 | 1994 | 0 | 12 | Downstream | 0.2 | 1 | 1
COM-UB-FS-332-01 | Current |  | Commercial | Under-Fired Broilers |  | New Construction/Natural Replacement | food service | High Efficiency Under-Fired Broilers - 3 foot | low idle energy rate (≤22,000 Btu/hr per linear foot) | Conventional Efficiency Under-Fired Broiler | conventional underfired broiler | unit |  | TRM Version 7.0 | 2022-11-30 | 2636 | 0 | 0 | 0 | 0 | 0 | 1868 | 0 | 12 | Downstream | 0.2 | 1 | 1
COM-UB-FS-333-01 | Current |  | Commercial | Under-Fired Broilers |  | New Construction/Natural Replacement | food service | High Efficiency Under-Fired Broilers - 4 foot | low idle energy rate (≤22,000 Btu/hr per linear foot) | Conventional Efficiency Under-Fired Broiler | conventional underfired broiler | unit |  | TRM Version 7.0 | 2022-11-30 | 3515 | 0 | 0 | 0 | 0 | 0 | 2948 | 0 | 12 | Downstream | 0.2 | 1 | 1
COM-UB-FS-334-01 | Current |  | Commercial | Under-Fired Broilers |  | New Construction/Natural Replacement | food service | High Efficiency Under-Fired Broilers - 5 foot | low idle energy rate (≤22,000 Btu/hr per linear foot) | Conventional Efficiency Under-Fired Broiler | conventional underfired broiler | unit |  | TRM Version 7.0 | 2022-11-30 | 4393 | 0 | 0 | 0 | 0 | 0 | 3820 | 0 | 12 | Downstream | 0.2 | 1 | 1
COM-UB-FS-335-01 | Current |  | Commercial | Under-Fired Broilers |  | New Construction/Natural Replacement | food service | High Efficiency Under-Fired Broilers - 6 foot | low idle energy rate (≤22,000 Btu/hr per linear foot) | Conventional Efficiency Under-Fired Broiler | conventional underfired broiler | unit |  | TRM Version 7.0 | 2022-11-30 | 5272 | 0 | 0 | 0 | 0 | 0 | 4134 | 0 | 12 | Downstream | 0.2 | 1 | 1
COM-UB-FS-336-01 | Current |  | Commercial | Under-Fired Broilers |  | New Construction/Natural Replacement | food service | High Efficiency Under-Fired Broilers - 2 foot | low idle energy rate (≤22,000 Btu/hr per linear foot) | Conventional Efficiency Under-Fired Broiler | conventional underfired broiler | unit |  | TRM Version 7.0 | 2022-11-30 | 1757 | 0 | 0 | 0 | 0 | 0 | 1264 | 0 | 12 | Downstream | 0.2 | 1 | 1
COM-DW-WH-555-01 | Current | revised from TRM Version 5.0: natural gas, electric savings, and water savings | Commercial | Dishwasher |  | New Construction/Natural Replacement | water heating | Energy Star Dishwasher | Multi Tank Conveyor - High Temperature | Non-Energy Star Dishwasher |  | unit |  | TRM Version 7.0 | 2022-11-30 | 2970 | 0 | 14386 | 0 | 437533 | 0 | 1216 | 0 | 20 | Downstream | 0.27 | 1 | 1
COM-DW-WH-556-01 | Current | revised from TRM Version 5.0: natural gas, electric savings, and water savings | Commercial | Dishwasher |  | New Construction/Natural Replacement | water heating | Energy Star Dishwasher | Multi Tank Conveyor - Low Temperature | Non-Energy Star Dishwasher |  | unit |  | TRM Version 7.0 | 2022-11-30 | 3447 | 0 | 3375 | 0 | 507851 | 0 | 1216 | 0 | 20 | Downstream | 0.27 | 1 | 1
COM-DW-WH-553-01 | Current | revised from TRM Version 5.0: natural gas, electric savings, and water savings | Commercial | Dishwasher |  | New Construction/Natural Replacement | water heating | Energy Star Dishwasher | Single Tank Conveyor – High Temperature | Non-Energy Star Dishwasher |  | unit |  | TRM Version 7.0 | 2022-11-30 | 1167 | 0 | 7599 | 0 | 171888 | 0 | 2570 | 0 | 20 | Downstream | 0.27 | 1 | 1
COM-DW-WH-554-01 | Current | revised from TRM Version 5.0: natural gas, electric savings, and water savings | Commercial | Dishwasher |  | New Construction/Natural Replacement | water heating | Energy Star Dishwasher | Single Tank Conveyor - Low Temperature | Non-Energy Star Dishwasher |  | unit |  | TRM Version 7.0 | 2022-11-30 | 2546 | 0 | 3474 | 0 | 375028 | 0 | 0 | 0 | 20 | Downstream | 0.27 | 1 | 1
COM-CNO-FS-805-02 | Current | New measure in TRM V7.0 | Commercial | Conveyor Oven |  | New Construction/Natural Replacement | food service | Energy-Efficient Conveyor Oven, small < 1520 sq in | Small Conveyor Oven Chamber Area <1520 sq in, 37% cooking efficiency | Conventional Conveyor Oven |  | unit |  | TRM Version 7.0 | 2022-11-30 | 562 | 0 | 619 | 0 | 0 | 0 | 859 | 0 | 12 | Downstream | 0.2 | 1 | 1
COM-DW-WH-551-01 | Current | revised from TRM Version 5.0: natural gas, electric savings, and water savings | Commercial | Dishwasher |  | New Construction/Natural Replacement | water heating | Energy Star Dishwasher | Stationary Single Tank Door – High Temperature | Non-Energy Star Dishwasher |  | unit |  | TRM Version 7.0 | 2022-11-30 | 1262 | 0 | 6032 | 0 | 185951 | 0 | 1247 | 0 | 15 | Downstream | 0.2 | 1 | 1
COM-DW-WH-552-01 | Current | revised from TRM Version 5.0: natural gas, electric savings, and water savings | Commercial | Dishwasher |  | New Construction/Natural Replacement | water heating | Energy Star Dishwasher | Stationary Single Tank Door – Low Temperature | Non-Energy Star Dishwasher |  | unit |  | TRM Version 7.0 | 2022-11-30 | 2846 | 0 | 946 | 0 | 419302 | 0 | 830 | 0 | 15 | Downstream | 0.2 | 1 | 1
COM-DW-WH-549-01 | Current | revised from TRM Version 5.0: natural gas, electric savings, and water savings | Commercial | Dishwasher |  | New Construction/Natural Replacement | water heating | Energy Star Dishwasher | Undercounter – High Temperature | Non-Energy Star Dishwasher |  | unit |  | TRM Version 7.0 | 2022-11-30 | 285 | 0 | 2767 | 0 | 41995 | 0 | 2538 | 0 | 10 | Downstream | 0.4 | 1 | 1
COM-DW-WH-550-01 | Current | revised from TRM Version 5.0: natural gas, electric savings, and water savings | Commercial | Dishwasher |  | New Construction/Natural Replacement | water heating | Energy Star Dishwasher | Undercounter – Low Temperature | Non-Energy Star Dishwasher |  | unit |  | TRM Version 7.0 | 2022-11-30 | 438 | 0 | 1405 | 0 | 64458 | 0 | 293 | 0 | 10 | Downstream | 0.4 | 1 | 1
COM-DK-SH-524-01 | Current | Updated savings values | Commercial | Demand Control Kitchen Ventilation |  | New Construction/Natural Replacement | space heating | Demand Control Kitchen Ventilation | 0 - 5,000 CFM | Constant Volume Kitchen Ventilation |  | unit |  | TRM Version 8.0 | 2024-04-30 | 4307 | 0 | 15865 | 0 | 0 | 0 | 5490 | 0 | 15 | Downstream | 0.38 | 1 | 1
COM-DK-SH-526-01 | Current | Updated savings values | Commercial | Demand Control Kitchen Ventilation |  | New Construction/Natural Replacement | space heating | Demand Control Kitchen Ventilation | 10,001 - 15,000 CFM | Constant Volume Kitchen Ventilation |  | unit |  | TRM Version 8.0 | 2024-04-30 | 17947 | 0 | 29586 | 0 | 0 | 0 | 22875 | 0 | 15 | Downstream | 0.38 | 1 | 1
COM-DK-SH-525-01 | Current | Updated savings values | Commercial | Demand Control Kitchen Ventilation |  | New Construction/Natural Replacement | space heating | Demand Control Kitchen Ventilation | 5,001 - 10,000 CFM | Constant Volume Kitchen Ventilation |  | unit |  | TRM Version 8.0 | 2024-04-30 | 10768 | 0 | 22364 | 0 | 0 | 0 | 13725 | 0 | 15 | Downstream | 0.38 | 1 | 1
COM-CU-SH-515-01 | Current | Updated size descriptions in eTRM to match TRM, entered energy savings that appear to be new from last TRM | Commercial | Condensing Unit Heater |  | Natural Replacement | space heating | Condensing Unit Heater | 125-225 kBtu/hr 90% Thermal Efficiency, 89% Annual Efficiency | Non-Condensing Unit Heater | 80% Thermal Efficiency, 78% Annual Efficiency |  | kBtu/hr input capacity | TRM Version 8.0 | 2024-04-30 | 0 | 6.52 | -438 | 0 | 0 | 0 | 0 | 16.07 | 18 | Downstream | 0 | 1 | 1
COM-CU-SH-516-01 | Current | Entered energy savings that appear to be new from last TRM | Commercial | Condensing Unit Heater |  | Natural Replacement | space heating | Condensing Unit Heater | 225-300 kBtu/hr 90% Thermal Efficiency, 89% Annual Efficiency | Non-Condensing Unit Heater | 80% Thermal Efficiency, 78% Annual Efficiency |  | kBtu/hr input capacity | TRM Version 8.0 | 2024-04-30 | 0 | 6.52 | -451 | 0 | 0 | 0 | 0 | 16.07 | 18 | Downstream | 0 | 1 | 1
COM-CU-SH-514-01 | Current | Updated size descriptions in eTRM to match TRM, entered energy savings that appear to be new from last TRM | Commercial | Condensing Unit Heater |  | Natural Replacement | space heating | Condensing Unit Heater | 30-125 kBtu/hr - 90% Thermal Efficiency, 89% Annual Efficiency | Non-Condensing Unit Heater | 80% Thermal Efficiency, 78% Annual Efficiency |  | kBtu/hr input capacity | TRM Version 8.0 | 2024-04-30 | 0 | 6.52 | -244 | 0 | 0 | 0 | 0 | 16.07 | 18 | Downstream | 0 | 1 | 1
COM-CU-SH-518-01 | Current | Updated size descriptions in eTRM to match TRM, entered energy savings that appear to be new from last TRM | Commercial | Condensing Unit Heater |  | New Construction | space heating | Condensing Unit Heater | 125-225 kBtu/hr 90% Thermal Efficiency, 89% Annual Efficiency | Non-Condensing Unit Heater | 80% Thermal Efficiency, 78% Annual Efficiency |  | kBtu/hr input capacity | TRM Version 8.0 | 2024-04-30 | 0 | 4.62 | -310 | 0 | 0 | 0 | 0 | 16.07 | 18 | Downstream | 0 | 1 | 1
COM-CU-SH-519-01 | Current | Entered energy savings that appear to be new from last TRM | Commercial | Condensing Unit Heater |  | New Construction | space heating | Condensing Unit Heater | 225-300 kBtu/hr 90% Thermal Efficiency, 89% Annual Efficiency | Non-Condensing Unit Heater | 80% Thermal Efficiency, 78% Annual Efficiency |  | kBtu/hr input capacity | TRM Version 8.0 | 2024-04-30 | 0 | 4.62 | -320 | 0 | 0 | 0 | 0 | 16.07 | 18 | Downstream | 0 | 1 | 1
COM-CU-SH-517-01 | Current | Updated size descriptions in eTRM to match TRM, entered energy savings that appear to be new from last TRM | Commercial | Condensing Unit Heater |  | New Construction | space heating | Condensing Unit Heater | 30-125 kBtu/hr - 90% Thermal Efficiency, 89% Annual Efficiency | Non-Condensing Unit Heater | 80% Thermal Efficiency, 78% Annual Efficiency |  | kBtu/hr input capacity | TRM Version 8.0 | 2024-04-30 | 0 | 4.62 | -173 | 0 | 0 | 0 | 0 | 16.07 | 18 | Downstream | 0 | 1 | 1
COM-CT-WH-533-00 | Current | Updated size descriptions in eTRM to match TRM. Split New Construction and Natural Replacement to effectively represent baseline. Updated technology descriptions. Updated energy savings. | Commercial | Condensing Tankless Water Heater | High Utilization | Natural Replacement | water heating | Condensing Tankless Water Heater - High Utilization | <200 kBtu/hr UEF >= 0.90 Stand-by Loss = negligible | Non-Condensing Storage Water Heater | Storage Water Heater 75 kBtu/hr. and greater Uniform Energy Factor (UEF)=0.6597-0.00024Vs | unit | kBtu/hr input capacity | TRM Version 8.0 | 2024-04-30 | 212 | 4.349 | 0 | 0 | 0 | 0 | 3030 | 0 | 20 | Downstream | 0.02 | 1 | 1
COM-CT-WH-533-01 | Current | Split New Construction and Natural Replacement to effectively represent baseline. Updated technology descriptions. Updated energy savings. | Commercial | Condensing Tankless Water Heater | High Utilization | Natural Replacement | water heating | Condensing Tankless Water Heater - High Utilization | >=200 kBtu/hr Thermal efficiency >= 94% Stand-by Loss = negligible | Non-Condensing Storage Water Heater | Storage Water Heater 75 kBtu/hr. and greater Thermal efficiency = 80% Stand-by Loss Q/800 +110√V0 Btu/hr | unit | kBtu/hr input capacity | TRM Version 8.0 | 2024-04-30 | 351 | 1.954 | 0 | 0 | 0 | 0 | 3030 | 0 | 20 | Downstream | 0.02 | 1 | 1
COM-CT-WH-533-02 | Current | Updated size descriptions in eTRM to match TRM. Split New Construction and Natural Replacement to effectively represent baseline. Updated technology descriptions. Updated energy savings. | Commercial | Condensing Tankless Water Heater | High Utilization | Natural Replacement | water heating | Condensing Tankless Water Heater - High Utilization | <200 kBtu/hr UEF >= 0.95 Stand-by Loss = negligible | Non-Condensing Storage Water Heater | Storage Water Heater 75 kBtu/hr. and greater Uniform Energy Factor (UEF)=0.6597-0.00024Vs | unit | kBtu/hr input capacity | TRM Version 8.0 | 2024-04-30 | 212 | 5.211 | 0 | 0 | 0 | 0 | 3030 | 0 | 20 | Downstream | 0.02 | 1 | 1
COM-CT-WH-533-03 | Current | Split New Construction and Natural Replacement to effectively represent baseline. Updated technology descriptions. Updated energy savings. | Commercial | Condensing Tankless Water Heater | High Utilization | Natural Replacement | water heating | Condensing Tankless Water Heater - High Utilization | >=200 kBtu/hr Thermal efficiency >= 96% Stand-by Loss = negligible | Non-Condensing Storage Water Heater | Storage Water Heater 75 kBtu/hr. and greater Thermal efficiency = 80% Stand-by Loss Q/800 +110√V0 Btu/hr | unit | kBtu/hr input capacity | TRM Version 8.0 | 2024-04-30 | 521 | 2.233 | 0 | 0 | 0 | 0 | 3030 | 0 | 20 | Downstream | 0.02 | 1 | 1
COM-CT-WH-533-04 | Current | Split New Construction and Natural Replacement to effectively represent baseline. Updated technology descriptions. Updated energy savings. | Commercial | Condensing Tankless Water Heater | High Utilization | Natural Replacement | water heating | Condensing Tankless Water Heater - High Utilization | >=200 kBtu/hr Thermal efficiency >= 98% Stand-by Loss = negligible | Non-Condensing Storage Water Heater | Storage Water Heater 75 kBtu/hr. and greater Thermal efficiency = 80% Stand-by Loss Q/800 +110√V0 Btu/hr | unit | kBtu/hr input capacity | TRM Version 8.0 | 2024-04-30 | 867 | 2.512 | 0 | 0 | 0 | 0 | 3030 | 0 | 20 | Downstream | 0.02 | 1 | 1
COM-CT-WH-534-00 | Current | Updated size descriptions in eTRM to match TRM. Split New Construction and Natural Replacement to effectively represent baseline. Updated technology descriptions. Updated energy savings. | Commercial | Condensing Tankless Water Heater | High Utilization | New Construction | water heating | Condensing Tankless Water Heater - High Utilization | <200 kBtu/hr UEF >= 0.95 Stand-by Loss = negligible | Non-Condensing Storage Water Heater | Storage Water Heater 75 kBtu/hr. and greater Uniform Energy Factor (UEF)=0.8107-0.00021Vs | unit | kBtu/hr input capacity | TRM Version 8.0 | 2024-04-30 | 178 | 2.09 | 0 | 0 | 0 | 0 | 1030 | 0 | 20 | Downstream | 0.02 | 1 | 1
COM-CT-WH-534-01 | Current | Split New Construction and Natural Replacement to effectively represent baseline. Updated technology descriptions. Updated energy savings. | Commercial | Condensing Tankless Water Heater | High Utilization | New Construction | water heating | Condensing Tankless Water Heater - High Utilization | >=200 kBtu/hr Thermal efficiency >= 96% Stand-by Loss = negligible | Non-Condensing Storage Water Heater | Storage Water Heater 75 kBtu/hr. and greater Thermal efficiency = 90% Stand-by Loss 0.84(Q/800 +110√V0)Btu/hr | unit | kBtu/hr input capacity | TRM Version 8.0 | 2024-04-30 | 295 | 0.744 | 0 | 0 | 0 | 0 | 1030 | 0 | 20 | Downstream | 0.02 | 1 | 1
COM-CT-WH-534-02 | Current | Split New Construction and Natural Replacement to effectively represent baseline. Updated technology descriptions. Updated energy savings. | Commercial | Condensing Tankless Water Heater | High Utilization | New Construction | water heating | Condensing Tankless Water Heater - High Utilization | >=1000 < 2500 kBtu/hr Thermal efficiency >= 98% Stand-by Loss = negligible | Non-Condensing Storage Water Heater | Storage Water Heater 75 kBtu/hr. and greater Thermal efficiency = 80% Stand-by Loss Q/800 +110√V0 Btu/hr | unit | kBtu/hr input capacity | TRM Version 8.0 | 2024-04-30 | 438 | 0.992 | 0 | 0 | 0 | 0 | 1030 | 0 | 20 | Downstream | 0.02 | 1 | 1
COM-CT-WH-534-03 | Current | Split New Construction and Natural Replacement to effectively represent baseline. Updated technology descriptions. Updated energy savings. | Commercial | Condensing Tankless Water Heater | High Utilization | New Construction | water heating | Condensing Tankless Water Heater - High Utilization | >=2500 kBtu/hr Thermal efficiency >= 98% Stand-by Loss = negligible | Non-Condensing Storage Water Heater | Storage Water Heater 75 kBtu/hr. and greater Thermal efficiency = 80% Stand-by Loss Q/800 +110√V0 Btu/hr | unit | kBtu/hr input capacity | TRM Version 8.0 | 2024-04-30 | 728 | 0.992 | 0 | 0 | 0 | 0 | 1030 | 0 | 20 | Downstream | 0.02 | 1 | 1
COM-CT-WH-535-00 | Current | Updated size descriptions in eTRM to match TRM. Split New Construction and Natural Replacement to effectively represent baseline. Updated technology descriptions. Updated energy savings. | Commercial | Condensing Tankless Water Heater | Low Utilization | Natural Replacement | water heating | Condensing Tankless Water Heater - Low Utilization | <200 kBtu/hr UEF >= 0.90 Stand-by Loss = negligible | Non-Condensing Storage Water Heater | Storage Water Heater 75 kBtu/hr. and greater Uniform Energy Factor (UEF)=0.6597-0.00024Vs | unit | kBtu/hr input capacity | TRM Version 8.0 | 2024-04-30 | 212 | 1.918 | 0 | 0 | 0 | 0 | 3030 | 0 | 20 | Downstream | 0.02 | 1 | 1
COM-CT-WH-535-01 | Current | Split New Construction and Natural Replacement to effectively represent baseline. Updated technology descriptions. Updated energy savings. | Commercial | Condensing Tankless Water Heater | Low Utilization | Natural Replacement | water heating | Condensing Tankless Water Heater - Low Utilization | >=200 kBtu/hr Thermal efficiency >= 94% Stand-by Loss = negligible | Non-Condensing Storage Water Heater | Storage Water Heater 75 kBtu/hr. and greater Thermal efficiency = 80% Stand-by Loss Q/800 +110√V0 Btu/hr | unit | kBtu/hr input capacity | TRM Version 8.0 | 2024-04-30 | 351 | 0.862 | 0 | 0 | 0 | 0 | 3030 | 0 | 20 | Downstream | 0.02 | 1 | 1
COM-CT-WH-535-02 | Current | Updated size descriptions in eTRM to match TRM. Split New Construction and Natural Replacement to effectively represent baseline. Updated technology descriptions. Updated energy savings. | Commercial | Condensing Tankless Water Heater | Low Utilization | Natural Replacement | water heating | Condensing Tankless Water Heater - Low Utilization | <200 kBtu/hr UEF >= 0.95 Stand-by Loss = negligible | Non-Condensing Storage Water Heater | Storage Water Heater 75 kBtu/hr. and greater Uniform Energy Factor (UEF)=0.6597-0.00024Vs | unit | kBtu/hr input capacity | TRM Version 8.0 | 2024-04-30 | 212 | 2.299 | 0 | 0 | 0 | 0 | 3030 | 0 | 20 | Downstream | 0.02 | 1 | 1
COM-CT-WH-535-03 | Current | Split New Construction and Natural Replacement to effectively represent baseline. Updated technology descriptions. Updated energy savings. | Commercial | Condensing Tankless Water Heater | Low Utilization | Natural Replacement | water heating | Condensing Tankless Water Heater - Low Utilization | >=200 kBtu/hr Thermal efficiency >= 96% Stand-by Loss = negligible | Non-Condensing Storage Water Heater | Storage Water Heater 75 kBtu/hr. and greater Thermal efficiency = 80% Stand-by Loss Q/800 +110√V0 Btu/hr | unit | kBtu/hr input capacity | TRM Version 8.0 | 2024-04-30 | 521 | 0.985 | 0 | 0 | 0 | 0 | 3030 | 0 | 20 | Downstream | 0.02 | 1 | 1
COM-CT-WH-535-04 | Current | Split New Construction and Natural Replacement to effectively represent baseline. Updated technology descriptions. Updated energy savings. | Commercial | Condensing Tankless Water Heater | Low Utilization | Natural Replacement | water heating | Condensing Tankless Water Heater - Low Utilization | >=200 kBtu/hr Thermal efficiency >= 98% Stand-by Loss = negligible | Non-Condensing Storage Water Heater | Storage Water Heater 75 kBtu/hr. and greater Thermal efficiency = 80% Stand-by Loss Q/800 +110√V0 Btu/hr | unit | kBtu/hr input capacity | TRM Version 8.0 | 2024-04-30 | 867 | 1.108 | 0 | 0 | 0 | 0 | 3030 | 0 | 20 | Downstream | 0.02 | 1 | 1
COM-CT-WH-536-00 | Current | Updated size descriptions in eTRM to match TRM. Split New Construction and Natural Replacement to effectively represent baseline. Updated technology descriptions. Updated energy savings. | Commercial | Condensing Tankless Water Heater | Low Utilization | New Construction | water heating | Condensing Tankless Water Heater - Low Utilization | <200 kBtu/hr UEF >= 0.95 Stand-by Loss = negligible | Non-Condensing Storage Water Heater | Storage Water Heater 75 kBtu/hr. and greater Uniform Energy Factor (UEF)=0.8107-0.00021Vs | unit | kBtu/hr input capacity | TRM Version 8.0 | 2024-04-30 | 178 | 0.922 | 0 | 0 | 0 | 0 | 1030 | 0 | 20 | Downstream | 0.02 | 1 | 1
COM-CT-WH-536-01 | Current | Split New Construction and Natural Replacement to effectively represent baseline. Updated technology descriptions. Updated energy savings. | Commercial | Condensing Tankless Water Heater | Low Utilization | New Construction | water heating | Condensing Tankless Water Heater - Low Utilization | >=200 kBtu/hr Thermal efficiency >= 96% Stand-by Loss = negligible | Non-Condensing Storage Water Heater | Storage Water Heater 75 kBtu/hr. and greater Thermal efficiency = 90% Stand-by Loss 0.84(Q/800 +110√V0)Btu/hr | unit | kBtu/hr input capacity | TRM Version 8.0 | 2024-04-30 | 295 | 0.328 | 0 | 0 | 0 | 0 | 1030 | 0 | 20 | Downstream | 0.02 | 1 | 1
COM-CT-WH-536-02 | Current | Split New Construction and Natural Replacement to effectively represent baseline. Updated technology descriptions. Updated energy savings. | Commercial | Condensing Tankless Water Heater | Low Utilization | New Construction | water heating | Condensing Tankless Water Heater - Low Utilization | >=1000 < 2500 kBtu/hr Thermal efficiency >= 98% Stand-by Loss = negligible | Non-Condensing Storage Water Heater | Storage Water Heater 75 kBtu/hr. and greater Thermal efficiency = 80% Stand-by Loss Q/800 +110√V0 Btu/hr | unit | kBtu/hr input capacity | TRM Version 8.0 | 2024-04-30 | 438 | 0.438 | 0 | 0 | 0 | 0 | 1030 | 0 | 20 | Downstream | 0.02 | 1 | 1
COM-CT-WH-536-03 | Current | Split New Construction and Natural Replacement to effectively represent baseline. Updated technology descriptions. Updated energy savings. | Commercial | Condensing Tankless Water Heater | Low Utilization | New Construction | water heating | Condensing Tankless Water Heater - Low Utilization | >=2500 kBtu/hr Thermal efficiency >= 98% Stand-by Loss = negligible | Non-Condensing Storage Water Heater | Storage Water Heater 75 kBtu/hr. and greater Thermal efficiency = 80% Stand-by Loss Q/800 +110√V0 Btu/hr | unit | kBtu/hr input capacity | TRM Version 8.0 | 2024-04-30 | 728 | 0.438 | 0 | 0 | 0 | 0 | 1030 | 0 | 20 | Downstream | 0.02 | 1 | 1
COM-CT-WH-537-00 | Current | Updated size descriptions in eTRM to match TRM. Split New Construction and Natural Replacement to effectively represent baseline. Updated technology descriptions. Updated energy savings. | Commercial | Condensing Tankless Water Heater | Medium Utilization | Natural Replacement | water heating | Condensing Tankless Water Heater - Medium Utilization | <200 kBtu/hr UEF >= 0.90 Stand-by Loss = negligible | Non-Condensing Storage Water Heater | Storage Water Heater 75 kBtu/hr. and greater Uniform Energy Factor (UEF)=0.6597-0.00024Vs | unit | kBtu/hr input capacity | TRM Version 8.0 | 2024-04-30 | 212 | 3.128 | 0 | 0 | 0 | 0 | 3030 | 0 | 20 | Downstream | 0.02 | 1 | 1
COM-CT-WH-537-01 | Current | Split New Construction and Natural Replacement to effectively represent baseline. Updated technology descriptions. Updated energy savings. | Commercial | Condensing Tankless Water Heater | Medium Utilization | Natural Replacement | water heating | Condensing Tankless Water Heater - Medium Utilization | >=200 kBtu/hr Thermal efficiency >= 94% Stand-by Loss = negligible | Non-Condensing Storage Water Heater | Storage Water Heater 75 kBtu/hr. and greater Thermal efficiency = 80% Stand-by Loss Q/800 +110√V0 Btu/hr | unit | kBtu/hr input capacity | TRM Version 8.0 | 2024-04-30 | 351 | 1.405 | 0 | 0 | 0 | 0 | 3030 | 0 | 20 | Downstream | 0.02 | 1 | 1
COM-CT-WH-537-02 | Current | Updated size descriptions in eTRM to match TRM. Split New Construction and Natural Replacement to effectively represent baseline. Updated technology descriptions. Updated energy savings. | Commercial | Condensing Tankless Water Heater | Medium Utilization | Natural Replacement | water heating | Condensing Tankless Water Heater - Medium Utilization | <200 kBtu/hr UEF >= 0.95 Stand-by Loss = negligible | Non-Condensing Storage Water Heater | Storage Water Heater 75 kBtu/hr. and greater Uniform Energy Factor (UEF)=0.6597-0.00024Vs | unit | kBtu/hr input capacity | TRM Version 8.0 | 2024-04-30 | 212 | 3.748 | 0 | 0 | 0 | 0 | 3030 | 0 | 20 | Downstream | 0.02 | 1 | 1
COM-DK-SH-521-09 | Replaced | Updated in TRM V8.0 | Commercial | Demand Control Kitchen Ventilation |  | Retrofit - LUG Rate Zone | space heating | Demand Control Kitchen Ventilation | 0 - 5,000 CFM | Constant Volume Kitchen Ventilation |  | unit |  | TRM Version 5.0 | 2020-11-12 | 4207 | 0 | 4940 | 0 | 0 | 0 | 4766 | 0 | 15 | Downstream | 0.05 | 1 | 1
COM-DK-SH-524-09 | Replaced | Updated in TRM V8.0 | Commercial | Demand Control Kitchen Ventilation |  | New Construction/Natural Replacement - LUG Rate Zone | space heating | Demand Control Kitchen Ventilation | 0 - 5,000 CFM | Constant Volume Kitchen Ventilation |  | unit |  | TRM Version 5.0 | 2020-11-12 | 4207 | 0 | 4940 | 0 | 0 | 0 | 2383 | 0 | 15 | Downstream | 0.05 | 1 | 1
MRS-SH-WH-569-03 | Replaced | Updated in TRM Version 6.0 | Commercial | Showerhead | Multi-residential | New Construction - LUG | water heating | Low-flow showerhead | 1.25 GPM |  | 2.0 GPM | unit |  | TRM Version 5.0 | 2020-11-12 | 23 | 0 | 0 | 0 | 8020 | 0 | actual cost |  | 10 | Downstream | 0.1 | 0.88 | 1
MRS-SH-WH-571-03 | Replaced | Updated in TRM Version 6.0 | Commercial | Showerhead | Multi-residential | Retrofit - LUG | water heating | Low-flow showerhead | 1.25 GPM | Average existing stock | 2.5 GPM | unit |  | TRM Version 5.0 | 2020-11-12 | 38.2 | 0 | 0 | 0 | 12105 | 0 | actual cost |  | 10 | Downstream | 0.1 | 0.88 | 1
MRS-SH-WH-570-03 | Replaced | Updated in TRM Version 6.0 | Commercial | Showerhead | Multi-residential | New Construction - LUG | water heating | Low-flow showerhead | 1.50 GPM |  | 2.0 GPM | unit |  | TRM Version 5.0 | 2020-11-12 | 15.3 | 0 | 0 | 0 | 4237 | 0 | actual cost |  | 10 | Downstream | 0.1 | 0.88 | 1
MRS-SH-WH-572-03 | Replaced | Updated in TRM Version 6.0 | Commercial | Showerhead | Multi-residential | Retrofit - LUG | water heating | Low-flow showerhead | 1.50 GPM | Average existing stock | 2.5 GPM | unit |  | TRM Version 5.0 | 2020-11-12 | 30.6 | 0 | 0 | 0 | 8322 | 0 | actual cost |  | 10 | Downstream | 0.1 | 0.88 | 1
COM-DK-SH-523-09 | Replaced | Updated in TRM V8.0 | Commercial | Demand Control Kitchen Ventilation |  | Retrofit - LUG Rate Zone | space heating | Demand Control Kitchen Ventilation | 10,001 - 15,000 CFM | Constant Volume Kitchen Ventilation |  | unit |  | TRM Version 5.0 | 2020-11-12 | 17529 | 0 | 28929 | 0 | 0 | 0 | 19859 | 0 | 15 | Downstream | 0.05 | 1 | 1
COM-DK-SH-526-09 | Replaced | Updated in TRM V8.0 | Commercial | Demand Control Kitchen Ventilation |  | New Construction/Natural Replacement - LUG Rate Zone | space heating | Demand Control Kitchen Ventilation | 10,001 - 15,000 CFM | Constant Volume Kitchen Ventilation |  | unit |  | TRM Version 5.0 | 2020-11-12 | 17529 | 0 | 28929 | 0 | 0 | 0 | 9929 | 0 | 15 | Downstream | 0.05 | 1 | 1
COM-DK-SH-522-09 | Replaced | Updated in TRM V8.0 | Commercial | Demand Control Kitchen Ventilation |  | Retrofit - LUG Rate Zone | space heating | Demand Control Kitchen Ventilation | 5,001 - 10,000 CFM | Constant Volume Kitchen Ventilation |  | unit |  | TRM Version 5.0 | 2020-11-12 | 10517 | 0 | 16294 | 0 | 0 | 0 | 11915 | 0 | 15 | Downstream | 0.05 | 1 | 1
COM-DK-SH-525-09 | Replaced | Updated in TRM V8.0 | Commercial | Demand Control Kitchen Ventilation |  | New Construction/Natural Replacement - LUG Rate Zone | space heating | Demand Control Kitchen Ventilation | 5,001 - 10,000 CFM | Constant Volume Kitchen Ventilation |  | unit |  | TRM Version 5.0 | 2020-11-12 | 10517 | 0 | 16294 | 0 | 0 | 0 | 5958 | 0 | 15 | Downstream | 0.05 | 1 | 1
COM-CT-WH-537-03 | Current | Split New Construction and Natural Replacement to effectively represent baseline. Updated technology descriptions. Updated energy savings. | Commercial | Condensing Tankless Water Heater | Medium Utilization | Natural Replacement | water heating | Condensing Tankless Water Heater - Medium Utilization | >=200 kBtu/hr Thermal efficiency >= 96% Stand-by Loss = negligible | Non-Condensing Storage Water Heater | Storage Water Heater 75 kBtu/hr. and greater Thermal efficiency = 80% Stand-by Loss Q/800 +110√V0 Btu/hr | unit | kBtu/hr input capacity | TRM Version 8.0 | 2024-04-30 | 521 | 1.606 | 0 | 0 | 0 | 0 | 3030 | 0 | 20 | Downstream | 0.02 | 1 | 1
COM-CT-WH-537-04 | Current | Split New Construction and Natural Replacement to effectively represent baseline. Updated technology descriptions. Updated energy savings. | Commercial | Condensing Tankless Water Heater | Medium Utilization | Natural Replacement | water heating | Condensing Tankless Water Heater - Medium Utilization | >=200 kBtu/hr Thermal efficiency >= 98% Stand-by Loss = negligible | Non-Condensing Storage Water Heater | Storage Water Heater 75 kBtu/hr. and greater Thermal efficiency = 80% Stand-by Loss Q/800 +110√V0 Btu/hr | unit | kBtu/hr input capacity | TRM Version 8.0 | 2024-04-30 | 867 | 1.807 | 0 | 0 | 0 | 0 | 3030 | 0 | 20 | Downstream | 0.02 | 1 | 1
COM-CT-WH-538-00 | Current | Updated size descriptions in eTRM to match TRM. Split New Construction and Natural Replacement to effectively represent baseline. Updated technology descriptions. Updated energy savings. | Commercial | Condensing Tankless Water Heater | Medium Utilization | New Construction | water heating | Condensing Tankless Water Heater - Medium Utilization | <200 kBtu/hr UEF >= 0.95 Stand-by Loss = negligible | Non-Condensing Storage Water Heater | Storage Water Heater 75 kBtu/hr. and greater Uniform Energy Factor (UEF)=0.8107-0.00021Vs | unit | kBtu/hr input capacity | TRM Version 8.0 | 2024-04-30 | 178 | 1.503 | 0 | 0 | 0 | 0 | 1030 | 0 | 20 | Downstream | 0.02 | 1 | 1
COM-CT-WH-538-01 | Current | Split New Construction and Natural Replacement to effectively represent baseline. Updated technology descriptions. Updated energy savings. | Commercial | Condensing Tankless Water Heater | Medium Utilization | New Construction | water heating | Condensing Tankless Water Heater - Medium Utilization | >=200 kBtu/hr Thermal efficiency >= 96% Stand-by Loss = negligible | Non-Condensing Storage Water Heater | Storage Water Heater 75 kBtu/hr. and greater Thermal efficiency = 90% Stand-by Loss 0.84(Q/800 +110√V0)Btu/hr | unit | kBtu/hr input capacity | TRM Version 8.0 | 2024-04-30 | 295 | 0.535 | 0 | 0 | 0 | 0 | 1030 | 0 | 20 | Downstream | 0.02 | 1 | 1
COM-CT-WH-538-02 | Current | Split New Construction and Natural Replacement to effectively represent baseline. Updated technology descriptions. Updated energy savings. | Commercial | Condensing Tankless Water Heater | Medium Utilization | New Construction | water heating | Condensing Tankless Water Heater - Medium Utilization | >=1000 < 2500 kBtu/hr Thermal efficiency >= 98% Stand-by Loss = negligible | Non-Condensing Storage Water Heater | Storage Water Heater 75 kBtu/hr. and greater Thermal efficiency = 80% Stand-by Loss Q/800 +110√V0 Btu/hr | unit | kBtu/hr input capacity | TRM Version 8.0 | 2024-04-30 | 438 | 0.714 | 0 | 0 | 0 | 0 | 1030 | 0 | 20 | Downstream | 0.02 | 1 | 1
COM-CT-WH-538-03 | Current | Split New Construction and Natural Replacement to effectively represent baseline. Updated technology descriptions. Updated energy savings. | Commercial | Condensing Tankless Water Heater | Medium Utilization | New Construction | water heating | Condensing Tankless Water Heater - Medium Utilization | >=2500 kBtu/hr Thermal efficiency >= 98% Stand-by Loss = negligible | Non-Condensing Storage Water Heater | Storage Water Heater 75 kBtu/hr. and greater Thermal efficiency = 80% Stand-by Loss Q/800 +110√V0 Btu/hr | unit | kBtu/hr input capacity | TRM Version 8.0 | 2024-04-30 | 728 | 0.714 | 0 | 0 | 0 | 0 | 1030 | 0 | 20 | Downstream | 0.02 | 1 | 1
COM-CS-WH-527-00 | Current | Split New Construction and Natural Replacement to effectively represent baseline and efficient efficiencies. Updated savings. | Commercial | Condensing Storage Water Heater | High Utilization | Natural Replacement | water heating | Condensing storage water heater | > 75 kBTU/hr and <= 105 kBTU/hr, rated nominal volume <= 120 US gallon, single-phase power, water temp <180 deg f, UEF >= 0.86 < 0.89 | Non-condensing storage water heater | > 75 kBTU/hr and <= 105 kBTU/hr, rated nominal volume <= 120 US gallon, single-phase power, water temp <180 deg f, UEF = 0.6597 - 0.00024Vs |  | kBtu/hr input capacity | TRM Version 8.0 | 2024-04-30 | 0 | 5.699 | 0 | 0 | 0 | 0 | 2591 | 0 | 15 | Downstream | 0.05 | 1 | 1
COM-CS-WH-527-01 | Current | Split New Construction and Natural Replacement to effectively represent baseline and efficient efficiencies. Updated savings. | Commercial | Condensing Storage Water Heater | High Utilization | Natural Replacement | water heating | Condensing storage water heater | > 75 kBTU/hr and <= 105 kBTU/hr, rated nominal volume <= 120 US gallon, single-phase power, water temp <180 deg f, UEF >= 0.89 | Non-condensing storage water heater | > 75 kBTU/hr and <= 105 kBTU/hr, rated nominal volume <= 120 US gallon, single-phase power, water temp <180 deg f, UEF = 0.6597 - 0.00024Vs |  | kBtu/hr input capacity | TRM Version 8.0 | 2024-04-30 | 0 | 6.497 | 0 | 0 | 0 | 0 | 2591 | 0 | 15 | Downstream | 0.05 | 1 | 1
COM-CS-WH-527-02 | Current | Split New Construction and Natural Replacement to effectively represent baseline and efficient efficiencies. Updated savings. | Commercial | Condensing Storage Water Heater | High Utilization | Natural Replacement | water heating | Condensing storage water heater | All water heaters not described by UEF baseline definition with thermal efficiency >= 92% < 95%, <= 250 kBTU/hr | Non-condensing storage water heater | All water heaters not described by UEF baseline definition with thermal efficiency >= 80% |  | kBtu/hr input capacity | TRM Version 8.0 | 2024-04-30 | 0 | 2.577 | 0 | 0 | 0 | 0 | 2591 | 0 | 15 | Downstream | 0.05 | 1 | 1
COM-CS-WH-527-03 | Current | Split New Construction and Natural Replacement to effectively represent baseline and efficient efficiencies. Updated savings. | Commercial | Condensing Storage Water Heater | High Utilization | Natural Replacement | water heating | Condensing storage water heater | All water heaters not described by UEF baseline definition with thermal efficiency >= 95% < 97%, <= 250 kBTU/hr | Non-condensing storage water heater | All water heaters not described by UEF baseline definition with thermal efficiency >= 80% |  | kBtu/hr input capacity | TRM Version 8.0 | 2024-04-30 | 0 | 3.221 | 0 | 0 | 0 | 0 | 2591 | 0 | 15 | Downstream | 0.05 | 1 | 1
COM-CS-WH-527-04 | Current | Split New Construction and Natural Replacement to effectively represent baseline and efficient efficiencies. Updated savings. | Commercial | Condensing Storage Water Heater | High Utilization | Natural Replacement | water heating | Condensing storage water heater | All water heaters not described by UEF baseline definition with thermal efficiency >= 97%, <= 250 kBTU/hr | Non-condensing storage water heater | All water heaters not described by UEF baseline definition with thermal efficiency >= 80% |  | kBtu/hr input capacity | TRM Version 8.0 | 2024-04-30 | 0 | 3.651 | 0 | 0 | 0 | 0 | 2591 | 0 | 15 | Downstream | 0.05 | 1 | 1
COM-CS-WH-527-05 | Current | Split New Construction and Natural Replacement to effectively represent baseline and efficient efficiencies. Updated savings. | Commercial | Condensing Storage Water Heater | High Utilization | Natural Replacement | water heating | Condensing storage water heater | All water heaters not described by UEF baseline definition with thermal efficiency >= 92% < 95%, > 250 kBTU/hr | Non-condensing storage water heater | All water heaters not described by UEF baseline definition with thermal efficiency >= 80% |  | kBtu/hr input capacity | TRM Version 8.0 | 2024-04-30 | 0 | 2.577 | 0 | 0 | 0 | 0 | 4464 | 0 | 15 | Downstream | 0.05 | 1 | 1
COM-CS-WH-527-06 | Current | Split New Construction and Natural Replacement to effectively represent baseline and efficient efficiencies. Updated savings. | Commercial | Condensing Storage Water Heater | High Utilization | Natural Replacement | water heating | Condensing storage water heater | All water heaters not described by UEF baseline definition with thermal efficiency >= 95% < 97%, > 250 kBTU/hr | Non-condensing storage water heater | All water heaters not described by UEF baseline definition with thermal efficiency >= 80% |  | kBtu/hr input capacity | TRM Version 8.0 | 2024-04-30 | 0 | 3.221 | 0 | 0 | 0 | 0 | 4464 | 0 | 15 | Downstream | 0.05 | 1 | 1
COM-CS-WH-527-07 | Current | Split New Construction and Natural Replacement to effectively represent baseline and efficient efficiencies. Updated savings. | Commercial | Condensing Storage Water Heater | High Utilization | Natural Replacement | water heating | Condensing storage water heater | All water heaters not described by UEF baseline definition with thermal efficiency >= 97%, > 250 kBTU/hr | Non-condensing storage water heater | All water heaters not described by UEF baseline definition with thermal efficiency >= 80% |  | kBtu/hr input capacity | TRM Version 8.0 | 2024-04-30 | 0 | 3.651 | 0 | 0 | 0 | 0 | 4464 | 0 | 15 | Downstream | 0.05 | 1 | 1
COM-CS-WH-528-00 | Current | Split New Construction and Natural Replacement to effectively represent baseline and efficient efficiencies. Updated savings. | Commercial | Condensing Storage Water Heater | High Utilization | New Construction | water heating | Condensing storage water heater | > 75 kBTU/hr and <= 105 kBTU/hr, rated nominal volume <= 120 US gallon, single-phase power, water temp <180 deg f, UEF >= 0.86 < 0.89 | Non-condensing storage water heater | > 75 kBTU/hr and <= 105 kBTU/hr, rated nominal volume <= 120 US gallon, single-phase power, water temp <180 deg f, UEF = 0.8107 - 0.00021Vs |  | kBtu/hr input capacity | TRM Version 8.0 | 2024-04-30 | 0 | 1.323 | 0 | 0 | 0 | 0 | 2591 | 0 | 15 | Downstream | 0.05 | 1 | 1
COM-CS-WH-528-01 | Current | Split New Construction and Natural Replacement to effectively represent baseline and efficient efficiencies. Updated savings. | Commercial | Condensing Storage Water Heater | High Utilization | New Construction | water heating | Condensing storage water heater | > 75 kBTU/hr and <= 105 kBTU/hr, rated nominal volume <= 120 US gallon, single-phase power, water temp <180 deg f, UEF >= 0.89 | Non-condensing storage water heater | > 75 kBTU/hr and <= 105 kBTU/hr, rated nominal volume <= 120 US gallon, single-phase power, water temp <180 deg f, UEF = 0.8107 - 0.00021Vs |  | kBtu/hr input capacity | TRM Version 8.0 | 2024-04-30 | 0 | 1.968 | 0 | 0 | 0 | 0 | 2591 | 0 | 15 | Downstream | 0.05 | 1 | 1
COM-CS-WH-528-02 | Current | Split New Construction and Natural Replacement to effectively represent baseline and efficient efficiencies. Updated savings. | Commercial | Condensing Storage Water Heater | High Utilization | New Construction | water heating | Condensing storage water heater | All water heaters not described by UEF baseline definition with thermal efficiency >= 95 < 97%, <= 250 kBTU/hr | Non-condensing storage water heater | All water heaters not described by UEF baseline definition with thermal efficiency = 90% |  | kBtu/hr input capacity | TRM Version 8.0 | 2024-04-30 | 0 | 0.954 | 0 | 0 | 0 | 0 | 2591 | 0 | 15 | Downstream | 0.05 | 1 | 1
COM-CS-WH-528-03 | Current | Split New Construction and Natural Replacement to effectively represent baseline and efficient efficiencies. Updated savings. | Commercial | Condensing Storage Water Heater | High Utilization | New Construction | water heating | Condensing storage water heater | All water heaters not described by UEF baseline definition with thermal efficiency >= 97%, <= 250 kBTU/hr | Non-condensing storage water heater | All water heaters not described by UEF baseline definition with thermal efficiency = 90% |  | kBtu/hr input capacity | TRM Version 8.0 | 2024-04-30 | 0 | 1.336 | 0 | 0 | 0 | 0 | 2591 | 0 | 15 | Downstream | 0.05 | 1 | 1
COM-CS-WH-528-04 | Current | Split New Construction and Natural Replacement to effectively represent baseline and efficient efficiencies. Updated savings. | Commercial | Condensing Storage Water Heater | High Utilization | New Construction | water heating | Condensing storage water heater | All water heaters not described by UEF baseline definition with thermal efficiency >= 95 < 97%, > 250 kBTU/hr | Non-condensing storage water heater | All water heaters not described by UEF baseline definition with thermal efficiency = 90% |  | kBtu/hr input capacity | TRM Version 8.0 | 2024-04-30 | 0 | 0.954 | 0 | 0 | 0 | 0 | 4464 | 0 | 15 | Downstream | 0.05 | 1 | 1
COM-CS-WH-528-05 | Current | Split New Construction and Natural Replacement to effectively represent baseline and efficient efficiencies. Updated savings. | Commercial | Condensing Storage Water Heater | High Utilization | New Construction | water heating | Condensing storage water heater | All water heaters not described by UEF baseline definition with thermal efficiency >= 97%, > 250 kBTU/hr | Non-condensing storage water heater | All water heaters not described by UEF baseline definition with thermal efficiency = 90% |  | kBtu/hr input capacity | TRM Version 8.0 | 2024-04-30 | 0 | 1.336 | 0 | 0 | 0 | 0 | 4464 | 0 | 15 | Downstream | 0.05 | 1 | 1
COM-CS-WH-529-00 | Current | Split New Construction and Natural Replacement to effectively represent baseline and efficient efficiencies. Updated savings. | Commercial | Condensing Storage Water Heater | Low Utilization | Natural Replacement | water heating | Condensing storage water heater | > 75 kBTU/hr and <= 105 kBTU/hr, rated nominal volume <= 120 US gallon, single-phase power, water temp <180 deg f, UEF >= 0.86 < 0.89 | Non-condensing storage water heater | > 75 kBTU/hr and <= 105 kBTU/hr, rated nominal volume <= 120 US gallon, single-phase power, water temp <180 deg f, UEF = 0.6597 - 0.00024Vs |  | kBtu/hr input capacity | TRM Version 8.0 | 2024-04-30 | 0 | 2.515 | 0 | 0 | 0 | 0 | 2591 | 0 | 15 | Downstream | 0.05 | 1 | 1
COM-CS-WH-529-01 | Current | Split New Construction and Natural Replacement to effectively represent baseline and efficient efficiencies. Updated savings. | Commercial | Condensing Storage Water Heater | Low Utilization | Natural Replacement | water heating | Condensing storage water heater | > 75 kBTU/hr and <= 105 kBTU/hr, rated nominal volume <= 120 US gallon, single-phase power, water temp <180 deg f, UEF >= 0.89 | Non-condensing storage water heater | > 75 kBTU/hr and <= 105 kBTU/hr, rated nominal volume <= 120 US gallon, single-phase power, water temp <180 deg f, UEF = 0.6597 - 0.00024Vs |  | kBtu/hr input capacity | TRM Version 8.0 | 2024-04-30 | 0 | 2.868 | 0 | 0 | 0 | 0 | 2591 | 0 | 15 | Downstream | 0.05 | 1 | 1
COM-CS-WH-529-02 | Current | Split New Construction and Natural Replacement to effectively represent baseline and efficient efficiencies. Updated savings. | Commercial | Condensing Storage Water Heater | Low Utilization | Natural Replacement | water heating | Condensing storage water heater | All water heaters not described by UEF baseline definition with thermal efficiency >= 92% < 95%, <= 250 kBTU/hr | Non-condensing storage water heater | All water heaters not described by UEF baseline definition with thermal efficiency >= 80% |  | kBtu/hr input capacity | TRM Version 8.0 | 2024-04-30 | 0 | 1.137 | 0 | 0 | 0 | 0 | 2591 | 0 | 15 | Downstream | 0.05 | 1 | 1
COM-CS-WH-529-03 | Current | Split New Construction and Natural Replacement to effectively represent baseline and efficient efficiencies. Updated savings. | Commercial | Condensing Storage Water Heater | Low Utilization | Natural Replacement | water heating | Condensing storage water heater | All water heaters not described by UEF baseline definition with thermal efficiency >= 95% < 97%, <= 250 kBTU/hr | Non-condensing storage water heater | All water heaters not described by UEF baseline definition with thermal efficiency >= 80% |  | kBtu/hr input capacity | TRM Version 8.0 | 2024-04-30 | 0 | 1.422 | 0 | 0 | 0 | 0 | 2591 | 0 | 15 | Downstream | 0.05 | 1 | 1
COM-CS-WH-529-04 | Current | Split New Construction and Natural Replacement to effectively represent baseline and efficient efficiencies. Updated savings. | Commercial | Condensing Storage Water Heater | Low Utilization | Natural Replacement | water heating | Condensing storage water heater | All water heaters not described by UEF baseline definition with thermal efficiency >= 97%, <= 250 kBTU/hr | Non-condensing storage water heater | All water heaters not described by UEF baseline definition with thermal efficiency >= 80% |  | kBtu/hr input capacity | TRM Version 8.0 | 2024-04-30 | 0 | 1.611 | 0 | 0 | 0 | 0 | 2591 | 0 | 15 | Downstream | 0.05 | 1 | 1
COM-CS-WH-529-05 | Current | Split New Construction and Natural Replacement to effectively represent baseline and efficient efficiencies. Updated savings. | Commercial | Condensing Storage Water Heater | Low Utilization | Natural Replacement | water heating | Condensing storage water heater | All water heaters not described by UEF baseline definition with thermal efficiency >= 92% < 95%, > 250 kBTU/hr | Non-condensing storage water heater | All water heaters not described by UEF baseline definition with thermal efficiency >= 80% |  | kBtu/hr input capacity | TRM Version 8.0 | 2024-04-30 | 0 | 1.137 | 0 | 0 | 0 | 0 | 4464 | 0 | 15 | Downstream | 0.05 | 1 | 1
COM-CS-WH-529-06 | Current | Split New Construction and Natural Replacement to effectively represent baseline and efficient efficiencies. Updated savings. | Commercial | Condensing Storage Water Heater | Low Utilization | Natural Replacement | water heating | Condensing storage water heater | All water heaters not described by UEF baseline definition with thermal efficiency >= 95% < 97%, > 250 kBTU/hr | Non-condensing storage water heater | All water heaters not described by UEF baseline definition with thermal efficiency >= 80% |  | kBtu/hr input capacity | TRM Version 8.0 | 2024-04-30 | 0 | 1.422 | 0 | 0 | 0 | 0 | 4464 | 0 | 15 | Downstream | 0.05 | 1 | 1
COM-CS-WH-529-07 | Current | Split New Construction and Natural Replacement to effectively represent baseline and efficient efficiencies. Updated savings. | Commercial | Condensing Storage Water Heater | Low Utilization | Natural Replacement | water heating | Condensing storage water heater | All water heaters not described by UEF baseline definition with thermal efficiency >= 97%, > 250 kBTU/hr | Non-condensing storage water heater | All water heaters not described by UEF baseline definition with thermal efficiency >= 80% |  | kBtu/hr input capacity | TRM Version 8.0 | 2024-04-30 | 0 | 1.611 | 0 | 0 | 0 | 0 | 4464 | 0 | 15 | Downstream | 0.05 | 1 | 1
COM-CS-WH-530-00 | Current | Split New Construction and Natural Replacement to effectively represent baseline and efficient efficiencies. Updated savings. | Commercial | Condensing Storage Water Heater | Low Utilization | New Construction | water heating | Condensing storage water heater | > 75 kBTU/hr and <= 105 kBTU/hr, rated nominal volume <= 120 US gallon, single-phase power, water temp <180 deg f, UEF >= 0.86 < 0.89 | Non-condensing storage water heater | > 75 kBTU/hr and <= 105 kBTU/hr, rated nominal volume <= 120 US gallon, single-phase power, water temp <180 deg f, UEF = 0.8107 - 0.00021Vs |  | kBtu/hr input capacity | TRM Version 8.0 | 2024-04-30 | 0 | 0.584 | 0 | 0 | 0 | 0 | 2591 | 0 | 15 | Downstream | 0.05 | 1 | 1
COM-CS-WH-530-01 | Current | Split New Construction and Natural Replacement to effectively represent baseline and efficient efficiencies. Updated savings. | Commercial | Condensing Storage Water Heater | Low Utilization | New Construction | water heating | Condensing storage water heater | > 75 kBTU/hr and <= 105 kBTU/hr, rated nominal volume <= 120 US gallon, single-phase power, water temp <180 deg f, UEF >= 0.89 | Non-condensing storage water heater | > 75 kBTU/hr and <= 105 kBTU/hr, rated nominal volume <= 120 US gallon, single-phase power, water temp <180 deg f, UEF = 0.8107 - 0.00021Vs |  | kBtu/hr input capacity | TRM Version 8.0 | 2024-04-30 | 0 | 0.869 | 0 | 0 | 0 | 0 | 2591 | 0 | 15 | Downstream | 0.05 | 1 | 1
COM-CS-WH-530-02 | Current | Split New Construction and Natural Replacement to effectively represent baseline and efficient efficiencies. Updated savings. | Commercial | Condensing Storage Water Heater | Low Utilization | New Construction | water heating | Condensing storage water heater | All water heaters not described by UEF baseline definition with thermal efficiency >= 95 < 97%, <= 250 kBTU/hr | Non-condensing storage water heater | All water heaters not described by UEF baseline definition with thermal efficiency = 90% |  | kBtu/hr input capacity | TRM Version 8.0 | 2024-04-30 | 0 | 0.421 | 0 | 0 | 0 | 0 | 2591 | 0 | 15 | Downstream | 0.05 | 1 | 1
COM-CS-WH-530-03 | Current | Split New Construction and Natural Replacement to effectively represent baseline and efficient efficiencies. Updated savings. | Commercial | Condensing Storage Water Heater | Low Utilization | New Construction | water heating | Condensing storage water heater | All water heaters not described by UEF baseline definition with thermal efficiency >= 97%, <= 250 kBTU/hr | Non-condensing storage water heater | All water heaters not described by UEF baseline definition with thermal efficiency = 90% |  | kBtu/hr input capacity | TRM Version 8.0 | 2024-04-30 | 0 | 0.59 | 0 | 0 | 0 | 0 | 2591 | 0 | 15 | Downstream | 0.05 | 1 | 1
COM-CS-WH-530-04 | Current | Split New Construction and Natural Replacement to effectively represent baseline and efficient efficiencies. Updated savings. | Commercial | Condensing Storage Water Heater | Low Utilization | New Construction | water heating | Condensing storage water heater | All water heaters not described by UEF baseline definition with thermal efficiency >= 95 < 97%, > 250 kBTU/hr | Non-condensing storage water heater | All water heaters not described by UEF baseline definition with thermal efficiency = 90% |  | kBtu/hr input capacity | TRM Version 8.0 | 2024-04-30 | 0 | 0.421 | 0 | 0 | 0 | 0 | 4464 | 0 | 15 | Downstream | 0.05 | 1 | 1
COM-CS-WH-530-05 | Current | Split New Construction and Natural Replacement to effectively represent baseline and efficient efficiencies. Updated savings. | Commercial | Condensing Storage Water Heater | Low Utilization | New Construction | water heating | Condensing storage water heater | All water heaters not described by UEF baseline definition with thermal efficiency >= 97%, > 250 kBTU/hr | Non-condensing storage water heater | All water heaters not described by UEF baseline definition with thermal efficiency = 90% |  | kBtu/hr input capacity | TRM Version 8.0 | 2024-04-30 | 0 | 0.59 | 0 | 0 | 0 | 0 | 4464 | 0 | 15 | Downstream | 0.05 | 1 | 1
COM-CS-WH-531-00 | Current | Split New Construction and Natural Replacement to effectively represent baseline and efficient efficiencies. Updated savings. | Commercial | Condensing Storage Water Heater | Medium Utilization | Natural Replacement | water heating | Condensing storage water heater | > 75 kBTU/hr and <= 105 kBTU/hr, rated nominal volume <= 120 US gallon, single-phase power, water temp <180 deg f, UEF >= 0.86 < 0.89 | Non-condensing storage water heater | > 75 kBTU/hr and <= 105 kBTU/hr, rated nominal volume <= 120 US gallon, single-phase power, water temp <180 deg f, UEF = 0.6597 - 0.00024Vs |  | kBtu/hr input capacity | TRM Version 8.0 | 2024-04-30 | 0 | 4.103 | 0 | 0 | 0 | 0 | 2591 | 0 | 15 | Downstream | 0.05 | 1 | 1
COM-CS-WH-531-01 | Current | Split New Construction and Natural Replacement to effectively represent baseline and efficient efficiencies. Updated savings. | Commercial | Condensing Storage Water Heater | Medium Utilization | Natural Replacement | water heating | Condensing storage water heater | > 75 kBTU/hr and <= 105 kBTU/hr, rated nominal volume <= 120 US gallon, single-phase power, water temp <180 deg f, UEF >= 0.89 | Non-condensing storage water heater | > 75 kBTU/hr and <= 105 kBTU/hr, rated nominal volume <= 120 US gallon, single-phase power, water temp <180 deg f, UEF = 0.6597 - 0.00024Vs |  | kBtu/hr input capacity | TRM Version 8.0 | 2024-04-30 | 0 | 4.677 | 0 | 0 | 0 | 0 | 2591 | 0 | 15 | Downstream | 0.05 | 1 | 1
COM-CS-WH-531-02 | Current | Split New Construction and Natural Replacement to effectively represent baseline and efficient efficiencies. Updated savings. | Commercial | Condensing Storage Water Heater | Medium Utilization | Natural Replacement | water heating | Condensing storage water heater | All water heaters not described by UEF baseline definition with thermal efficiency >= 92% < 95%, <= 250 kBTU/hr | Non-condensing storage water heater | All water heaters not described by UEF baseline definition with thermal efficiency >= 80% |  | kBtu/hr input capacity | TRM Version 8.0 | 2024-04-30 | 0 | 1.855 | 0 | 0 | 0 | 0 | 2591 | 0 | 15 | Downstream | 0.05 | 1 | 1
COM-CS-WH-531-03 | Current | Split New Construction and Natural Replacement to effectively represent baseline and efficient efficiencies. Updated savings. | Commercial | Condensing Storage Water Heater | Medium Utilization | Natural Replacement | water heating | Condensing storage water heater | All water heaters not described by UEF baseline definition with thermal efficiency >= 95% < 97%, <= 250 kBTU/hr | Non-condensing storage water heater | All water heaters not described by UEF baseline definition with thermal efficiency >= 80% |  | kBtu/hr input capacity | TRM Version 8.0 | 2024-04-30 | 0 | 2.319 | 0 | 0 | 0 | 0 | 2591 | 0 | 15 | Downstream | 0.05 | 1 | 1
COM-CS-WH-531-04 | Current | Split New Construction and Natural Replacement to effectively represent baseline and efficient efficiencies. Updated savings. | Commercial | Condensing Storage Water Heater | Medium Utilization | Natural Replacement | water heating | Condensing storage water heater | All water heaters not described by UEF baseline definition with thermal efficiency >= 97%, <= 250 kBTU/hr | Non-condensing storage water heater | All water heaters not described by UEF baseline definition with thermal efficiency >= 80% |  | kBtu/hr input capacity | TRM Version 8.0 | 2024-04-30 | 0 | 2.628 | 0 | 0 | 0 | 0 | 2591 | 0 | 15 | Downstream | 0.05 | 1 | 1
COM-CS-WH-531-05 | Current | Split New Construction and Natural Replacement to effectively represent baseline and efficient efficiencies. Updated savings. | Commercial | Condensing Storage Water Heater | Medium Utilization | Natural Replacement | water heating | Condensing storage water heater | All water heaters not described by UEF baseline definition with thermal efficiency >= 92% < 95%, > 250 kBTU/hr | Non-condensing storage water heater | All water heaters not described by UEF baseline definition with thermal efficiency >= 80% |  | kBtu/hr input capacity | TRM Version 8.0 | 2024-04-30 | 0 | 1.855 | 0 | 0 | 0 | 0 | 4464 | 0 | 15 | Downstream | 0.05 | 1 | 1
COM-CS-WH-531-06 | Current | Split New Construction and Natural Replacement to effectively represent baseline and efficient efficiencies. Updated savings. | Commercial | Condensing Storage Water Heater | Medium Utilization | Natural Replacement | water heating | Condensing storage water heater | All water heaters not described by UEF baseline definition with thermal efficiency >= 95% < 97%, > 250 kBTU/hr | Non-condensing storage water heater | All water heaters not described by UEF baseline definition with thermal efficiency >= 80% |  | kBtu/hr input capacity | TRM Version 8.0 | 2024-04-30 | 0 | 2.319 | 0 | 0 | 0 | 0 | 4464 | 0 | 15 | Downstream | 0.05 | 1 | 1
COM-CS-WH-531-07 | Current | Split New Construction and Natural Replacement to effectively represent baseline and efficient efficiencies. Updated savings. | Commercial | Condensing Storage Water Heater | Medium Utilization | Natural Replacement | water heating | Condensing storage water heater | All water heaters not described by UEF baseline definition with thermal efficiency >= 97%, > 250 kBTU/hr | Non-condensing storage water heater | All water heaters not described by UEF baseline definition with thermal efficiency >= 80% |  | kBtu/hr input capacity | TRM Version 8.0 | 2024-04-30 | 0 | 2.628 | 0 | 0 | 0 | 0 | 4464 | 0 | 15 | Downstream | 0.05 | 1 | 1
COM-CS-WH-532-00 | Current | Split New Construction and Natural Replacement to effectively represent baseline and efficient efficiencies. Updated savings. | Commercial | Condensing Storage Water Heater | Medium Utilization | New Construction | water heating | Condensing storage water heater | > 75 kBTU/hr and <= 105 kBTU/hr, rated nominal volume <= 120 US gallon, single-phase power, water temp <180 deg f, UEF >= 0.86 < 0.89 | Non-condensing storage water heater | > 75 kBTU/hr and <= 105 kBTU/hr, rated nominal volume <= 120 US gallon, single-phase power, water temp <180 deg f, UEF = 0.8107 - 0.00021Vs |  | kBtu/hr input capacity | TRM Version 8.0 | 2024-04-30 | 0 | 0.952 | 0 | 0 | 0 | 0 | 2591 | 0 | 15 | Downstream | 0.05 | 1 | 1
COM-CS-WH-532-01 | Current | Split New Construction and Natural Replacement to effectively represent baseline and efficient efficiencies. Updated savings. | Commercial | Condensing Storage Water Heater | Medium Utilization | New Construction | water heating | Condensing storage water heater | > 75 kBTU/hr and <= 105 kBTU/hr, rated nominal volume <= 120 US gallon, single-phase power, water temp <180 deg f, UEF >= 0.89 | Non-condensing storage water heater | > 75 kBTU/hr and <= 105 kBTU/hr, rated nominal volume <= 120 US gallon, single-phase power, water temp <180 deg f, UEF = 0.8107 - 0.00021Vs |  | kBtu/hr input capacity | TRM Version 8.0 | 2024-04-30 | 0 | 1.417 | 0 | 0 | 0 | 0 | 2591 | 0 | 15 | Downstream | 0.05 | 1 | 1
COM-CS-WH-532-02 | Current | Split New Construction and Natural Replacement to effectively represent baseline and efficient efficiencies. Updated savings. | Commercial | Condensing Storage Water Heater | Medium Utilization | New Construction | water heating | Condensing storage water heater | All water heaters not described by UEF baseline definition with thermal efficiency >= 95 < 97%, <= 250 kBTU/hr | Non-condensing storage water heater | All water heaters not described by UEF baseline definition with thermal efficiency = 90% |  | kBtu/hr input capacity | TRM Version 8.0 | 2024-04-30 | 0 | 0.687 | 0 | 0 | 0 | 0 | 2591 | 0 | 15 | Downstream | 0.05 | 1 | 1
COM-CS-WH-532-03 | Current | Split New Construction and Natural Replacement to effectively represent baseline and efficient efficiencies. Updated savings. | Commercial | Condensing Storage Water Heater | Medium Utilization | New Construction | water heating | Condensing storage water heater | All water heaters not described by UEF baseline definition with thermal efficiency >= 97%, <= 250 kBTU/hr | Non-condensing storage water heater | All water heaters not described by UEF baseline definition with thermal efficiency = 90% |  | kBtu/hr input capacity | TRM Version 8.0 | 2024-04-30 | 0 | 0.962 | 0 | 0 | 0 | 0 | 2591 | 0 | 15 | Downstream | 0.05 | 1 | 1
COM-CS-WH-532-04 | Current | Split New Construction and Natural Replacement to effectively represent baseline and efficient efficiencies. Updated savings. | Commercial | Condensing Storage Water Heater | Medium Utilization | New Construction | water heating | Condensing storage water heater | All water heaters not described by UEF baseline definition with thermal efficiency >= 95 < 97%, > 250 kBTU/hr | Non-condensing storage water heater | All water heaters not described by UEF baseline definition with thermal efficiency = 90% |  | kBtu/hr input capacity | TRM Version 8.0 | 2024-04-30 | 0 | 0.687 | 0 | 0 | 0 | 0 | 4464 | 0 | 15 | Downstream | 0.05 | 1 | 1
COM-CS-WH-532-05 | Current | Split New Construction and Natural Replacement to effectively represent baseline and efficient efficiencies. Updated savings. | Commercial | Condensing Storage Water Heater | Medium Utilization | New Construction | water heating | Condensing storage water heater | All water heaters not described by UEF baseline definition with thermal efficiency >= 97%, > 250 kBTU/hr | Non-condensing storage water heater | All water heaters not described by UEF baseline definition with thermal efficiency = 90% |  | kBtu/hr input capacity | TRM Version 8.0 | 2024-04-30 | 0 | 0.962 | 0 | 0 | 0 | 0 | 4464 | 0 | 15 | Downstream | 0.05 | 1 | 1
COM-DK-SH-527-01 | Current | Updated savings values | Commercial | Demand Control Kitchen Ventilation |  | Retrofit | space heating | Demand Control Kitchen Ventilation | 0 - 5,000 CFM | Constant Volume Kitchen Ventilation |  | unit |  | TRM Version 8.0 | 2024-04-30 | 4307 | 0 | 15865 | 0 | 0 | 0 | 10980 | 0 | 15 | Downstream | 0.38 | 1 | 1
COM-DK-SH-527-02 | Current | Updated savings values | Commercial | Demand Control Kitchen Ventilation |  | Retrofit | space heating | Demand Control Kitchen Ventilation | 0 - 5,000 CFM | Constant Volume Kitchen Ventilation |  | unit |  | TRM Version 8.0 | 2024-04-30 | 4307 | 0 | 15865 | 0 | 0 | 0 | 10980 | 0 | 15 | Low-Income | 0 | 1 | 1
COM-DK-SH-527-04 | Current | Updated savings values | Commercial | Demand Control Kitchen Ventilation |  | Retrofit | space heating | Demand Control Kitchen Ventilation | 0 - 5,000 CFM | Constant Volume Kitchen Ventilation |  | unit |  | TRM Version 8.0 | 2024-04-30 | 4307 | 0 | 15865 | 0 | 0 | 0 | 10980 | 0 | 15 | Midstream | 0.05 | 1 | 1
COM-DK-SH-528-01 | Current | Updated savings values | Commercial | Demand Control Kitchen Ventilation |  | Retrofit | space heating | Demand Control Kitchen Ventilation | 10,001 - 15,000 CFM | Constant Volume Kitchen Ventilation |  | unit |  | TRM Version 8.0 | 2024-04-30 | 17947 | 0 | 29586 | 0 | 0 | 0 | 45750 | 0 | 15 | Downstream | 0.38 | 1 | 1
COM-DK-SH-528-02 | Current | Updated savings values | Commercial | Demand Control Kitchen Ventilation |  | Retrofit | space heating | Demand Control Kitchen Ventilation | 10,001 - 15,000 CFM | Constant Volume Kitchen Ventilation |  | unit |  | TRM Version 8.0 | 2024-04-30 | 17947 | 0 | 29586 | 0 | 0 | 0 | 45750 | 0 | 15 | Low-Income | 0 | 1 | 1
COM-DK-SH-528-04 | Current | Updated savings values | Commercial | Demand Control Kitchen Ventilation |  | Retrofit | space heating | Demand Control Kitchen Ventilation | 10,001 - 15,000 CFM | Constant Volume Kitchen Ventilation |  | unit |  | TRM Version 8.0 | 2024-04-30 | 17947 | 0 | 29586 | 0 | 0 | 0 | 45750 | 0 | 15 | Midstream | 0.05 | 1 | 1
COM-DK-SH-529-01 | Current | Updated savings values | Commercial | Demand Control Kitchen Ventilation |  | Retrofit | space heating | Demand Control Kitchen Ventilation | 5,001 - 10,000 CFM | Constant Volume Kitchen Ventilation |  | unit |  | TRM Version 8.0 | 2024-04-30 | 10768 | 0 | 22364 | 0 | 0 | 0 | 27450 | 0 | 15 | Downstream | 0.38 | 1 | 1
COM-DK-SH-529-02 | Current | Updated savings values | Commercial | Demand Control Kitchen Ventilation |  | Retrofit | space heating | Demand Control Kitchen Ventilation | 5,001 - 10,000 CFM | Constant Volume Kitchen Ventilation |  | unit |  | TRM Version 8.0 | 2024-04-30 | 10768 | 0 | 22364 | 0 | 0 | 0 | 27450 | 0 | 15 | Low-Income | 0 | 1 | 1
COM-DK-SH-529-04 | Current | Updated savings values | Commercial | Demand Control Kitchen Ventilation |  | Retrofit | space heating | Demand Control Kitchen Ventilation | 5,001 - 10,000 CFM | Constant Volume Kitchen Ventilation |  | unit |  | TRM Version 8.0 | 2024-04-30 | 10768 | 0 | 22364 | 0 | 0 | 0 | 27450 | 0 | 15 | Midstream | 0.05 | 1 | 1
COM-CS-WH-502-04 | Replaced | Replaced in TRM Version 8.0 | Commercial | Condensing Storage Water Heater | Low Utilization | New Construction/Natural Replacement | water heating | Condensing Storage Water Heater - Low Utilization | > 75 kBtu/hr and <=250 kBtu/hr. inputEstimated overall efficiency of units shipped = 94.5% | Non-condensing storage water heater | Non-condensing storage water heaterGreater than 75 kBtu/hr. inputEstimated overall efficiency of units shipped = 80.1% |  | kBtu/hr input capacity | TRM Version 5.0 | 2020-11-12 | 0 | 1.36 | 0 | 0 | 0 | 0 | 2591 | 0 | 15 | Low-Income | 0 | 1 | 1
COM-CS-WH-503-04 | Replaced | Replaced in TRM Version 8.0 | Commercial | Condensing Storage Water Heater | Medium Utilization | New Construction/Natural Replacement | water heating | Condensing Storage Water Heater - Medium Utilization | > 75 kBtu/hr and <=250 kBtu/hr. inputEstimated overall efficiency of units shipped = 94.5% | Non-condensing storage water heater | Greater than 75 kBtu/hr. inputEstimated overall efficiency of units shipped = 80.1% |  | kBtu/hr input capacity | TRM Version 5.0 | 2020-11-12 | 0 | 2.22 | 0 | 0 | 0 | 0 | 2591 | 0 | 15 | Low-Income | 0 | 1 | 1
COM-CS-WH-504-04 | Replaced | Replaced in TRM Version 8.0 | Commercial | Condensing Storage Water Heater | High Utilization | New Construction/Natural Replacement | water heating | Condensing Storage Water Heater - High Utilization | > 75 kBtu/hr and <=250 kBtu/hr. inputEstimated overall efficiency of units shipped = 94.5% | Non-condensing storage water heater | Greater than 75 kBtu/hr. inputEstimated overall efficiency of units shipped = 80.1% |  | kBtu/hr input capacity | TRM Version 5.0 | 2020-11-12 | 0 | 3.09 | 0 | 0 | 0 | 0 | 2591 | 0 | 15 | Low-Income | 0 | 1 | 1
COM-CT-WH-511-04 | Replaced | Replaced in TRM Version 8.0 | Commercial | Condensing Tankless Water Heater | Low Utilization | New Construction/Natural Replacement | water heating | Condensing Tankless Water Heater - Low Utilization | >=200 kBtu/hrThermal efficiency = 92.9%Stand-by Loss = negligible | Non-Condensing Storage Water Heater | 75 kBtu/hr. and greaterThermal efficiency of units shipped = 80.1%Stand-by Loss Q/0.8 +110√V0 | unit | kBtu/hr input capacity | TRM Version 5.0 | 2020-11-12 | 326 | 0.79 | 0 | 0 | 0 | 0 | 2227 | 0 | 20 | Low-Income | 0 | 1 | 1
COM-CT-WH-512-04 | Replaced | Replaced in TRM Version 8.0 | Commercial | Condensing Tankless Water Heater | Medium Utilization | New Construction/Natural Replacement | water heating | Condensing Tankless Water Heater - Medium Utilization | >=200 kBtu/hrThermal efficiency = 92.9%Stand-by Loss = negligible | Non-Condensing Storage Water Heater | 75 kBtu/hr. and greaterThermal efficiency of units shipped = 80.1%Stand-by Loss Q/0.8 +110√V0 | unit | kBtu/hr input capacity | TRM Version 5.0 | 2020-11-12 | 326 | 1.29 | 0 | 0 | 0 | 0 | 2227 | 0 | 20 | Low-Income | 0 | 1 | 1
COM-CT-WH-513-04 | Replaced | Replaced in TRM Version 8.0 | Commercial | Condensing Tankless Water Heater | High Utilization | New Construction/Natural Replacement | water heating | Condensing Tankless Water Heater - High Utilization | >=200 kBtu/hrThermal efficiency = 92.9%Stand-by Loss = negligible | Non-Condensing Storage Water Heater | 75 kBtu/hr. and greaterThermal efficiency of units shipped = 80.1%Stand-by Loss Q/0.8 +110√V0 | unit | kBtu/hr input capacity | TRM Version 5.0 | 2020-11-12 | 326 | 1.79 | 0 | 0 | 0 | 0 | 2227 | 0 | 20 | Low-Income | 0 | 1 | 1
COM-CS-WH-505-04 | Replaced | Replaced in TRM Version 8.0 | Commercial | Condensing Storage Water Heater | Low Utilization | New Construction/Natural Replacement | water heating | Condensing Storage Water Heater - Low Utilization | >250 kBtu/hr. inputEstimated overall efficiency of units shipped = 94.5% | Non-condensing storage water heater | Greater than 75 kBtu/hr. inputEstimated overall efficiency of units shipped = 80.1% |  | kBtu/hr input capacity | TRM Version 5.0 | 2020-11-12 | 0 | 1.36 | 0 | 0 | 0 | 0 | 4464 | 0 | 15 | Low-Income | 0 | 1 | 1
COM-CS-WH-506-04 | Replaced | Replaced in TRM Version 8.0 | Commercial | Condensing Storage Water Heater | Medium Utilization | New Construction/Natural Replacement | water heating | Condensing Storage Water Heater - Medium Utilization | >250 kBtu/hr. inputEstimated overall efficiency of units shipped = 94.5% | Non-condensing storage water heater | Greater than 75 kBtu/hr. inputEstimated overall efficiency of units shipped = 80.1% |  | kBtu/hr input capacity | TRM Version 5.0 | 2020-11-12 | 0 | 2.22 | 0 | 0 | 0 | 0 | 4464 | 0 | 15 | Low-Income | 0 | 1 | 1
COM-CS-WH-507-04 | Replaced | Replaced in TRM Version 8.0 | Commercial | Condensing Storage Water Heater | High Utilization | New Construction/Natural Replacement | water heating | Condensing Storage Water Heater - High Utilization | >250 kBtu/hr. inputEstimated overall efficiency of units shipped = 94.5% | Non-condensing storage water heater | Greater than 75 kBtu/hr. inputEstimated overall efficiency of units shipped = 80.1% |  | kBtu/hr input capacity | TRM Version 5.0 | 2020-11-12 | 0 | 3.09 | 0 | 0 | 0 | 0 | 4464 | 0 | 15 | Low-Income | 0 | 1 | 1
COM-CT-WH-508-04 | Replaced | Replaced in TRM Version 8.0 | Commercial | Condensing Tankless Water Heater | Low Utilization | New Construction/Natural Replacement | water heating | Condensing Tankless Water Heater - Low Utilization | >75 and <200 kBtu/hrThermal efficiency = 92.9%Stand-by Loss = negligible | Non-Condensing Storage Water Heater | 75 kBtu/hr. and greaterThermal efficiency of units shipped = 80.1%Stand-by Loss Q/0.8 +110√V0 | unit | kBtu/hr input capacity | TRM Version 5.0 | 2020-11-12 | 212 | 0.79 | 0 | 0 | 0 | 0 | 2227 | 0 | 20 | Low-Income | 0 | 1 | 1
COM-CT-WH-509-04 | Replaced | Replaced in TRM Version 8.0 | Commercial | Condensing Tankless Water Heater | Medium Utilization | New Construction/Natural Replacement | water heating | Condensing Tankless Water Heater - Medium Utilization | >75 and <200 kBtu/hrThermal efficiency = 92.9%Stand-by Loss = negligible | Non-Condensing Storage Water Heater | 75 kBtu/hr. and greaterThermal efficiency of units shipped = 80.1%Stand-by Loss Q/0.8 +110√V0 | unit | kBtu/hr input capacity | TRM Version 5.0 | 2020-11-12 | 212 | 1.29 | 0 | 0 | 0 | 0 | 2227 | 0 | 20 | Low-Income | 0 | 1 | 1
COM-CT-WH-510-04 | Replaced | Replaced in TRM Version 8.0 | Commercial | Condensing Tankless Water Heater | High Utilization | New Construction/Natural Replacement | water heating | Condensing Tankless Water Heater - High Utilization | >75 and <200 kBtu/hrThermal efficiency = 92.9%Stand-by Loss = negligible | Non-Condensing Storage Water Heater | 75 kBtu/hr. and greaterThermal efficiency of units shipped = 80.1%Stand-by Loss Q/0.8 +110√V0 | unit | kBtu/hr input capacity | TRM Version 5.0 | 2020-11-12 | 212 | 1.79 | 0 | 0 | 0 | 0 | 2227 | 0 | 20 | Low-Income | 0 | 1 | 1
COM-DK-SH-521-02 | Replaced | Updated in TRM V8.0 | Commercial | Demand Control Kitchen Ventilation |  | Retrofit | space heating | Demand Control Kitchen Ventilation | 0 - 5,000 CFM | Constant Volume Kitchen Ventilation |  | unit |  | TRM Version 5.0 | 2020-11-12 | 4207 | 0 | 4940 | 0 | 0 | 0 | 4766 | 0 | 15 | Low-Income | 0 | 1 | 1
COM-DK-SH-524-02 | Replaced | Updated in TRM V8.0 | Commercial | Demand Control Kitchen Ventilation |  | New Construction/Natural Replacement | space heating | Demand Control Kitchen Ventilation | 0 - 5,000 CFM | Constant Volume Kitchen Ventilation |  | unit |  | TRM Version 5.0 | 2020-11-12 | 4207 | 0 | 4940 | 0 | 0 | 0 | 2383 | 0 | 15 | Low-Income | 0 | 1 | 1
MRS-SH-WH-569-02 | Replaced | Updated in TRM Version 6.0 | Commercial | Showerhead | Multi-residential | New Construction | water heating | Low-flow showerhead | 1.25 GPM |  | 2.0 GPM | unit |  | TRM Version 5.0 | 2020-11-12 | 23 | 0 | 0 | 0 | 8020 | 0 | actual cost |  | 10 | Low-Income | 0 | 0.845 | 1
MRS-SH-WH-571-02 | Replaced | Updated in TRM Version 6.0 | Commercial | Showerhead | Multi-residential | Retrofit | water heating | Low-flow showerhead | 1.25 GPM | Average existing stock | 2.5 GPM | unit |  | TRM Version 5.0 | 2020-11-12 | 38.2 | 0 | 0 | 0 | 12105 | 0 | actual cost |  | 10 | Low-Income | 0 | 0.845 | 1
MRS-SH-WH-570-02 | Replaced | Updated in TRM Version 6.0 | Commercial | Showerhead | Multi-residential | New Construction | water heating | Low-flow showerhead | 1.50 GPM |  | 2.0 GPM | unit |  | TRM Version 5.0 | 2020-11-12 | 15.3 | 0 | 0 | 0 | 4237 | 0 | actual cost |  | 10 | Low-Income | 0 | 0.845 | 1
MRS-SH-WH-572-02 | Replaced | Updated in TRM Version 6.0 | Commercial | Showerhead | Multi-residential | Retrofit | water heating | Low-flow showerhead | 1.50 GPM | Average existing stock | 2.5 GPM | unit |  | TRM Version 5.0 | 2020-11-12 | 30.6 | 0 | 0 | 0 | 8322 | 0 | actual cost |  | 10 | Low-Income | 0 | 0.845 | 1
COM-DK-SH-523-02 | Replaced | Updated in TRM V8.0 | Commercial | Demand Control Kitchen Ventilation |  | Retrofit | space heating | Demand Control Kitchen Ventilation | 10,001 - 15,000 CFM | Constant Volume Kitchen Ventilation |  | unit |  | TRM Version 5.0 | 2020-11-12 | 17529 | 0 | 28929 | 0 | 0 | 0 | 19859 | 0 | 15 | Low-Income | 0 | 1 | 1
COM-DK-SH-526-02 | Replaced | Updated in TRM V8.0 | Commercial | Demand Control Kitchen Ventilation |  | New Construction/Natural Replacement | space heating | Demand Control Kitchen Ventilation | 10,001 - 15,000 CFM | Constant Volume Kitchen Ventilation |  | unit |  | TRM Version 5.0 | 2020-11-12 | 17529 | 0 | 28929 | 0 | 0 | 0 | 9929 | 0 | 15 | Low-Income | 0 | 1 | 1
COM-CU-SH-515-04 | Replaced | Updated in TRM Version 6.0 with new incremental cost and negative, not positive electric savings. | Commercial | Condensing Unit Heater |  | Natural Replacement | space heating | Condensing Unit Heater | 125-200 kBtu/hr 90% Thermal Efficiency, 89% Annual Efficiency | Non-Condensing Unit Heater | 80% Thermal Efficiency, 78% Annual Efficiency |  | kBtu/hr input capacity | TRM Version 5.0 | 2020-11-12 | 0 | 7.89 | -530 | 0 | 0 | 0 | 0 | 12.9 | 18 | Low-Income | 0 | 1 | 1
COM-CU-SH-518-04 | Replaced | Updated in TRM Version 6.0 with new incremental cost and negative, not positive electric savings. | Commercial | Condensing Unit Heater |  | New Construction | space heating | Condensing Unit Heater | 125-200 kBtu/hr 90% Thermal Efficiency, 89% Annual Efficiency | Non-Condensing Unit Heater | 80% Thermal Efficiency, 78% Annual Efficiency |  | kBtu/hr input capacity | TRM Version 5.0 | 2020-11-12 | 0 | 5.92 | -398 | 0 | 0 | 0 | 0 | 12.9 | 18 | Low-Income | 0 | 1 | 1
COM-CU-SH-516-04 | Replaced | Updated in TRM Version 6.0 with new incremental cost and negative, not positive electric savings. | Commercial | Condensing Unit Heater |  | Natural Replacement | space heating | Condensing Unit Heater | 225-300 kBtu/hr 90% Thermal Efficiency, 89% Annual Efficiency | Non-Condensing Unit Heater | 80% Thermal Efficiency, 78% Annual Efficiency |  | kBtu/hr input capacity | TRM Version 5.0 | 2020-11-12 | 0 | 7.89 | -546 | 0 | 0 | 0 | 0 | 12.9 | 18 | Low-Income | 0 | 1 | 1
COM-CU-SH-519-04 | Replaced | Updated in TRM Version 6.0 with new incremental cost and negative, not positive electric savings. | Commercial | Condensing Unit Heater |  | New Construction | space heating | Condensing Unit Heater | 225-300 kBtu/hr 90% Thermal Efficiency, 89% Annual Efficiency | Non-Condensing Unit Heater | 80% Thermal Efficiency, 78% Annual Efficiency |  | kBtu/hr input capacity | TRM Version 5.0 | 2020-11-12 | 0 | 5.92 | -410 | 0 | 0 | 0 | 0 | 12.9 | 18 | Low-Income | 0 | 1 | 1
COM-CF-SH-494-04 | Current |  | Commercial | Condensing Furnace |  | New Construction | space heating | High Efficiency Condensing Furnace | >=97% AFUE | Condensing Furnace | 95% AFUE |  | kBtu/hr | TRM Version 5.0 | 2020-11-12 | 0 | 0.884 | 0 | 0 | 0 | 0 | 188 | 0 | 18 | Low-Income | 0 | 1 | 1
COM-CF-SH-495-04 | Current |  | Commercial | Condensing Furnace |  | Natural Replacement | space heating | High Efficiency Condensing Furnace | >=97% AFUE | Condensing Furnace | 95% AFUE |  | kBtu/hr | TRM Version 5.0 | 2020-11-12 | 0 | 1.178 | 0 | 0 | 0 | 0 | 188 | 0 | 18 | Low-Income | 0 | 1 | 1
RES-CF-SH-492-01 | Current |  | Residential | Condensing Furnace |  | New Construction | space heating | High Efficiency Condensing Furnace | >=97% AFUE | Condensing Furnace | 95% AFUE |  | kBtu/hr | TRM Version 5.0 | 2020-11-12 | 0 | 0.343 | 0 | 0 | 0 | 0 | 188 | 0 | 18 | Low-Income | 0 | 1 | 1
COM-CU-SH-514-04 | Replaced | Updated in TRM Version 6.0 with new incremental cost and negative, not positive electric savings. | Commercial | Condensing Unit Heater |  | Natural Replacement | space heating | Condensing Unit Heater | 30-100 kBtu/hr - 90% Thermal Efficiency, 89% Annual Efficiency | Non-Condensing Unit Heater | 80% Thermal Efficiency, 78% Annual Efficiency |  | kBtu/hr input capacity | TRM Version 5.0 | 2020-11-12 | 0 | 7.89 | -296 | 0 | 0 | 0 | 0 | 12.9 | 18 | Low-Income | 0 | 1 | 1
COM-CU-SH-517-04 | Replaced | Updated in TRM Version 6.0 with new incremental cost and negative, not positive electric savings. | Commercial | Condensing Unit Heater |  | New Construction | space heating | Condensing Unit Heater | 30-100 kBtu/hr - 90% Thermal Efficiency, 89% Annual Efficiency | Non-Condensing Unit Heater | 80% Thermal Efficiency, 78% Annual Efficiency |  | kBtu/hr input capacity | TRM Version 5.0 | 2020-11-12 | 0 | 5.92 | -222 | 0 | 0 | 0 | 0 | 12.9 | 18 | Low-Income | 0 | 1 | 1
COM-DK-SH-522-02 | Replaced | Updated in TRM V8.0 | Commercial | Demand Control Kitchen Ventilation |  | Retrofit | space heating | Demand Control Kitchen Ventilation | 5,001 - 10,000 CFM | Constant Volume Kitchen Ventilation |  | unit |  | TRM Version 5.0 | 2020-11-12 | 10517 | 0 | 16294 | 0 | 0 | 0 | 11915 | 0 | 15 | Low-Income | 0 | 1 | 1
COM-DK-SH-525-02 | Replaced | Updated in TRM V8.0 | Commercial | Demand Control Kitchen Ventilation |  | New Construction/Natural Replacement | space heating | Demand Control Kitchen Ventilation | 5,001 - 10,000 CFM | Constant Volume Kitchen Ventilation |  | unit |  | TRM Version 5.0 | 2020-11-12 | 10517 | 0 | 16294 | 0 | 0 | 0 | 5958 | 0 | 15 | Low-Income | 0 | 1 | 1
COM-CO-FS-520-04 | Replaced | Updated in TRM Version 6.0 | Commercial | Convection Ovens |  | New Construction/Natural Replacement | food service | Energy Star Convection Ovens | Energy Star Rated Convection Oven (Full Size) | Conventional Convection Oven (Full Size) |  | unit |  | TRM Version 5.0 | 2020-11-12 | 865 | 0 | 40.1 | 0 | 0 | 0 | 1200 | 0 | 12 | Low-Income | 0 | 1 | 1
COM-FR-FS-324-04 | Replaced | Updated in TRM Version 7.0 | Commercial | Fryer |  | New Construction/Natural Replacement | food service | Energy Star Fryer | Energy Star Rated Fryer | Non-Energy Star rated Fryer |  | unit |  | TRM Version 5.0 | 2020-11-12 | 1408 | 0 | 0 | 0 | 0 | 0 | 2476 | 0 | 12 | Low-Income | 0 | 1 | 1
COM-RO-FS-651-04 | Replaced | Updated in V6.0 | Commercial | Rack Oven |  | New Construction/Natural Replacement | food service | ENERGY STAR Rack Oven | Energy Star Rated Rack Oven, Double | Conventiona rack oven |  | unit |  | TRM Version 5.0 | 2020-11-12 | 1076 | 0 | 1685 | 0 | 0 | 0 | 2591 | 0 | 12 | Low-Income | 0 | 1 | 1
COM-RO-FS-650-04 | Replaced | Updated in V6.0 | Commercial | Rack Oven |  | New Construction/Natural Replacement | food service | ENERGY STAR Rack Oven | Energy Star Rated Rack Oven, Single | Conventiona rack oven |  | unit |  | TRM Version 5.0 | 2020-11-12 | 830 | 0 | 749 | 0 | 0 | 0 | 1544 | 0 | 12 | Low-Income | 0 | 1 | 1
COM-SC-FS-325-04 | Replaced | Updated in TRM Version 7.0 | Commercial | Steam Cookers |  | New Construction/Natural Replacement | food service | Energy Star Steam Cookers | Energy Star Rated Steam Cooker | Boiler-based steam cooker |  | unit |  | TRM Version 5.0 | 2020-11-12 | 8889 | 0 | 0 | 0 | 340142 | 0 | 3880 | 0 | 12 | Low-Income | 0 | 1 | 1
COM-DW-WH-555-02 | Replaced | Updated in TRM Version 6.0 | Commercial | Dishwasher |  | New Construction/Natural Replacement | water heating | Energy Star Dishwasher | Multi Tank Conveyor - High Temperature | Non-Energy Star Dishwasher |  | unit |  | TRM Version 5.0 | 2020-11-12 | 2260 | 0 | 9680 | 0 | 304677 | 0 | 1386 | 0 | 20 | Low-Income | 0 | 1 | 1
COM-DW-WH-556-02 | Replaced | Updated in TRM Version 6.0 | Commercial | Dishwasher |  | New Construction/Natural Replacement | water heating | Energy Star Dishwasher | Multi Tank Conveyor - Low Temperature | Non-Energy Star Dishwasher |  | unit |  | TRM Version 5.0 | 2020-11-12 | 2383 | 0 | 0 | 0 | 354276 | 0 | 1386 | 0 | 20 | Low-Income | 0 | 1 | 1
COM-OL-WH-329-04 | Replaced | Updated in TRM Version 6.0 | Commercial | Ozone Laundry |  | New Construction/Retrofit | water heating | Commercial Ozone Laundry Treatment | Ozone Treatment Tunnel Washer <= 120 lbs | Commercial laundry with no ozone treatment system |  |  | lbs/yr | TRM Version 5.0 | 2020-11-12 | 0 | 0.0305 | 0 | 0.0015 | 0 | 1.27 | 71429 | 0 | 15 | Low-Income | 0 | 1 | 1
COM-OL-WH-331-04 | Replaced | Updated in TRM Version 6.0 | Commercial | Ozone Laundry |  | New Construction/Retrofit | water heating | Commercial Ozone Laundry Treatment | Ozone Treatment Tunnel Washer=> 500 lbs | Commercial laundry with no ozone treatment system |  |  | lbs/yr | TRM Version 5.0 | 2020-11-12 | 0 | 0.0305 | 0 | 0.0015 | 0 | 1.27 | 228571 | 0 | 15 | Low-Income | 0 | 1 | 1
COM-OL-WH-330-04 | Replaced | Updated in TRM Version 6.0 | Commercial | Ozone Laundry |  | New Construction/Retrofit | water heating | Commercial Ozone Laundry Treatment | Ozone Treatment Tunnel Washer121 lbs to 499 lbs | Commercial laundry with no ozone treatment system |  |  | lbs/yr | TRM Version 5.0 | 2020-11-12 | 0 | 0.0305 | 0 | 0.0015 | 0 | 1.27 | 150000 | 0 | 15 | Low-Income | 0 | 1 | 1
COM-OL-WH-326-04 | Replaced | Updated in TRM Version 6.0 | Commercial | Ozone Laundry |  | New Construction/Retrofit | water heating | Commercial Ozone Laundry Treatment | Ozone Treatment Washer extractor =< 60 lbs | Commercial laundry with no ozone treatment system |  |  | lbs/yr | TRM Version 5.0 | 2020-11-12 | 0 | 0.0383 | 0 | 0.00213 | 0 | 2.08 | 15714 | 0 | 15 | Low-Income | 0 | 1 | 1
COM-OL-WH-327-04 | Replaced | Updated in TRM Version 6.0 | Commercial | Ozone Laundry |  | New Construction/Retrofit | water heating | Commercial Ozone Laundry Treatment | Ozone Treatment Washer extractor 61 lbs to 499 lbs | Commercial laundry with no ozone treatment system |  |  | lbs/yr | TRM Version 5.0 | 2020-11-12 | 0 | 0.0383 | 0 | 0.00213 | 0 | 2.08 | 35714 | 0 | 15 | Low-Income | 0 | 1 | 1
COM-OL-WH-328-04 | Replaced | Updated in TRM Version 6.0 | Commercial | Ozone Laundry |  | New Construction/Retrofit | water heating | Commercial Ozone Laundry Treatment | Ozone Treatment Washer extractor=> 500 lbs | Commercial laundry with no ozone treatment system |  |  | lbs/yr | TRM Version 5.0 | 2020-11-12 | 0 | 0.0383 | 0 | 0.00213 | 0 | 2.08 | 44286 | 0 | 15 | Low-Income | 0 | 1 | 1
COM-UB-FS-332-04 | Replaced | Updated in TRM Version 7.0 | Commercial | Under-Fired Broilers |  | New Construction/Natural Replacement | food service | High Efficiency Under-Fired Broilers - 3 foot | pre-heat =< 40,500 Btu and cooking energy rate =< 72,000 Btu/hr | Conventional Efficiency Under-Fired Broiler | pre-heat =< 48,000 Btu and cooking energy rate =< 96,000 Btu/hr | unit |  | TRM Version 5.0 | 2020-11-12 | 2511 | 0 | 0 | 0 | 0 | 0 | 1900 | 0 | 12 | Low-Income | 0 | 1 | 1
COM-UB-FS-333-04 | Replaced | Updated in TRM Version 7.0 | Commercial | Under-Fired Broilers |  | New Construction/Natural Replacement | food service | High Efficiency Under-Fired Broilers - 4 foot | pre-heat 40,501 to 54,000 Btu and a cooking energy rate 72,001 to 96,000 Btu/hr | Conventional Efficiency Under-Fired Broiler | pre-heat 48,001 to 64,000 Btu and a cooking energy rate 96,000 to 128,000 Btu/hr | unit |  | TRM Version 5.0 | 2020-11-12 | 3347 | 0 | 0 | 0 | 0 | 0 | 1900 | 0 | 12 | Low-Income | 0 | 1 | 1
COM-UB-FS-334-04 | Replaced | Updated in TRM Version 7.0 | Commercial | Under-Fired Broilers |  | New Construction/Natural Replacement | food service | High Efficiency Under-Fired Broilers - 5 foot | pre-heat 54,001 to 67,500 Btu and cooking energy rate 96,001 to 120,000 Btu/hr | Conventional Efficiency Under-Fired Broiler | pre-heat 64,001 to 80,000 Btu and cooking energy rate 128,001 to 160,000 Btu/hr | unit |  | TRM Version 5.0 | 2020-11-12 | 4184 | 0 | 0 | 0 | 0 | 0 | 1900 | 0 | 12 | Low-Income | 0 | 1 | 1
COM-UB-FS-335-04 | Replaced | Updated in TRM Version 7.0 | Commercial | Under-Fired Broilers |  | New Construction/Natural Replacement | food service | High Efficiency Under-Fired Broilers - 6 foot | pre-heat 67,501 to 81,000 Btu and cooking energy rate 120,001 to 144,000 Btu/hr | Conventional Efficiency Under-Fired Broiler | pre-heat 80,001 to 96,000 Btu and cooking energy rate 160,001 to 192,000 Btu/hr | unit |  | TRM Version 5.0 | 2020-11-12 | 5021 | 0 | 0 | 0 | 0 | 0 | 1900 | 0 | 12 | Low-Income | 0 | 1 | 1
COM-DW-WH-553-02 | Replaced | Updated in TRM Version 6.0 | Commercial | Dishwasher |  | New Construction/Natural Replacement | water heating | Energy Star Dishwasher | Single Tank Conveyor – High Temperature | Non-Energy Star Dishwasher |  | unit |  | TRM Version 5.0 | 2020-11-12 | 540 | 0 | 4251 | 0 | 80303 | 0 | 2929 | 0 | 20 | Low-Income | 0 | 1 | 1
COM-DW-WH-554-02 | Replaced | Updated in TRM Version 6.0 | Commercial | Dishwasher |  | New Construction/Natural Replacement | water heating | Energy Star Dishwasher | Single Tank Conveyor - Low Temperature | Non-Energy Star Dishwasher |  | unit |  | TRM Version 5.0 | 2020-11-12 | 1652 | 0 | 0 | 0 | 245631 | 0 | 0 | 0 | 20 | Low-Income | 0 | 1 | 1
COM-DW-WH-551-02 | Replaced | Updated in TRM Version 6.0 | Commercial | Dishwasher |  | New Construction/Natural Replacement | water heating | Energy Star Dishwasher | Stationary Single Tank Door – High Temperature | Non-Energy Star Dishwasher |  | unit |  | TRM Version 5.0 | 2020-11-12 | 890 | 0 | 4173 | 0 | 132263 | 0 | 1100 | 0 | 15 | Low-Income | 0 | 1 | 1
COM-IH-SH-577-08 | Retired | retired in TRM 6.0 | Commercial | Infrared Heaters |  | Retrofit | space heating | 2-Stage Infrared Heaters | 0 - 49,999 BTU/hr | Regular Unit Heater |  |  | kBtu/hr input capacity | TRM Version 5.0 | 2020-11-12 | 0 | 13.1 | 0 | 0 | 0 | 0 | 0 | 30.28 | 17 | Low-Income | 0 | 1 | 1
COM-IH-SH-580-08 | Retired | retired in TRM 6.0 | Commercial | Infrared Heaters |  | New Construction | space heating | 2-Stage Infrared Heaters | 0 - 49,999 BTU/hr | Regular Unit Heater |  |  | kBtu/hr input capacity | TRM Version 5.0 | 2020-11-12 | 0 | 9.8 | 0 | 0 | 0 | 0 | 0 | 11.22 | 17 | Low-Income | 0 | 1 | 1
COM-IH-SH-583-08 | Retired | retired in TRM 6.0 | Commercial | Infrared Heaters |  | Retrofit | space heating | Single Stage & High Intensity Infrared Heaters | 0 - 49,999 BTU/hr | Regular Unit Heater |  |  | kBtu/hr input capacity | TRM Version 5.0 | 2020-11-12 | 0 | 11.5 | 0 | 0 | 0 | 0 | 0 | 30.28 | 17 | Low-Income | 0 | 1 | 1
COM-IH-SH-586-08 | Retired | retired in TRM 6.0 | Commercial | Infrared Heaters |  | New Construction | space heating | Single Stage & High Intensity Infrared Heaters | 0 - 49,999 BTU/hr | Regular Unit Heater |  |  | kBtu/hr input capacity | TRM Version 5.0 | 2020-11-12 | 0 | 8.6 | 0 | 0 | 0 | 0 | 0 | 11.22 | 17 | Low-Income | 0 | 1 | 1
COM-DW-WH-552-02 | Replaced | Updated in TRM Version 6.0 | Commercial | Dishwasher |  | New Construction/Natural Replacement | water heating | Energy Star Dishwasher | Stationary Single Tank Door – Low Temperature | Non-Energy Star Dishwasher |  | unit |  | TRM Version 5.0 | 2020-11-12 | 2256 | 0 | 0 | 0 | 304205 | 0 | 0 | 0 | 15 | Low-Income | 0 | 1 | 1
COM-DW-WH-549-02 | Replaced | Updated in TRM Version 6.0 | Commercial | Dishwasher |  | New Construction/Natural Replacement | water heating | Energy Star Dishwasher | Undercounter – High Temperature | Non-Energy Star Dishwasher |  | unit |  | TRM Version 5.0 | 2020-11-12 | 137 | 0 | 1791 | 0 | 20371 | 0 | 171 | 0 | 10 | Low-Income | 0 | 1 | 1
COM-DW-WH-550-02 | Replaced | Updated in TRM Version 6.0 | Commercial | Dishwasher |  | New Construction/Natural Replacement | water heating | Energy Star Dishwasher | Undercounter – Low Temperature | Non-Energy Star Dishwasher |  | unit |  | TRM Version 5.0 | 2020-11-12 | 322 | 0 | 0 | 0 | 47827 | 0 | 71 | 0 | 10 | Low-Income | 0 | 1 | 1
COM-CU-SH-515-04 | Replaced | Updated in TRM Version 8.0 | Commercial | Condensing Unit Heater |  | Natural Replacement | space heating | Condensing Unit Heater | 125-200 kBtu/hr 90% Thermal Efficiency, 89% Annual Efficiency | Non-Condensing Unit Heater | 80% Thermal Efficiency, 78% Annual Efficiency |  | kBtu/hr input capacity | TRM Version 6.0 | 2021-12-16 | 0 | 7.89 | -530 | 0 | 0 | 0 | 0 | 16.08 | 18 | Low-Income | 0 | 1 | 1
COM-CU-SH-518-04 | Replaced | Updated in TRM Version 8.0 | Commercial | Condensing Unit Heater |  | New Construction | space heating | Condensing Unit Heater | 125-200 kBtu/hr 90% Thermal Efficiency, 89% Annual Efficiency | Non-Condensing Unit Heater | 80% Thermal Efficiency, 78% Annual Efficiency |  | kBtu/hr input capacity | TRM Version 6.0 | 2021-12-16 | 0 | 5.92 | -398 | 0 | 0 | 0 | 0 | 16.08 | 18 | Low-Income | 0 | 1 | 1
COM-CU-SH-516-04 | Replaced | Updated in TRM Version 8.0 | Commercial | Condensing Unit Heater |  | Natural Replacement | space heating | Condensing Unit Heater | 225-300 kBtu/hr 90% Thermal Efficiency, 89% Annual Efficiency | Non-Condensing Unit Heater | 80% Thermal Efficiency, 78% Annual Efficiency |  | kBtu/hr input capacity | TRM Version 6.0 | 2021-12-16 | 0 | 7.89 | -546 | 0 | 0 | 0 | 0 | 16.08 | 18 | Low-Income | 0 | 1 | 1
COM-CU-SH-519-04 | Replaced | Updated in TRM Version 8.0 | Commercial | Condensing Unit Heater |  | New Construction | space heating | Condensing Unit Heater | 225-300 kBtu/hr 90% Thermal Efficiency, 89% Annual Efficiency | Non-Condensing Unit Heater | 80% Thermal Efficiency, 78% Annual Efficiency |  | kBtu/hr input capacity | TRM Version 6.0 | 2021-12-16 | 0 | 5.92 | -410 | 0 | 0 | 0 | 0 | 16.08 | 18 | Low-Income | 0 | 1 | 1
COM-CU-SH-514-04 | Replaced | Updated in TRM Version 8.0 | Commercial | Condensing Unit Heater |  | Natural Replacement | space heating | Condensing Unit Heater | 30-100 kBtu/hr - 90% Thermal Efficiency, 89% Annual Efficiency | Non-Condensing Unit Heater | 80% Thermal Efficiency, 78% Annual Efficiency |  | kBtu/hr input capacity | TRM Version 6.0 | 2021-12-16 | 0 | 7.89 | -296 | 0 | 0 | 0 | 0 | 16.08 | 18 | Low-Income | 0 | 1 | 1
COM-CU-SH-517-04 | Replaced | Updated in TRM Version 8.0 | Commercial | Condensing Unit Heater |  | New Construction | space heating | Condensing Unit Heater | 30-100 kBtu/hr - 90% Thermal Efficiency, 89% Annual Efficiency | Non-Condensing Unit Heater | 80% Thermal Efficiency, 78% Annual Efficiency |  | kBtu/hr input capacity | TRM Version 6.0 | 2021-12-16 | 0 | 5.92 | -222 | 0 | 0 | 0 | 0 | 16.08 | 18 | Low-Income | 0 | 1 | 1
COM-DW-WH-555-02 | Replaced | Updated in TRM Version 7.0; revised from TRM Version 5.0: natural gas, electric savings, and water savings | Commercial | Dishwasher |  | New Construction/Natural Replacement | water heating | Energy Star Dishwasher | Multi Tank Conveyor - High Temperature | Non-Energy Star Dishwasher |  | unit |  | TRM Version 6.0 | 2021-12-16 | 2260 | 0 | 10673 | 0 | 335926 | 0 | 1386 | 0 | 20 | Low-Income | 0 | 1 | 1
COM-DW-WH-556-02 | Replaced | Updated in TRM Version 7.0; revised from TRM Version 5.0: natural gas, electric savings, and water savings | Commercial | Dishwasher |  | New Construction/Natural Replacement | water heating | Energy Star Dishwasher | Multi Tank Conveyor - Low Temperature | Non-Energy Star Dishwasher |  | unit |  | TRM Version 6.0 | 2021-12-16 | 2628 | 0 | 0 | 0 | 390612 | 0 | 1386 | 0 | 20 | Low-Income | 0 | 1 | 1
COM-DW-WH-553-02 | Replaced | Updated in TRM Version 7.0; revised from TRM Version 5.0: natural gas, electric savings, and water savings | Commercial | Dishwasher |  | New Construction/Natural Replacement | water heating | Energy Star Dishwasher | Single Tank Conveyor – High Temperature | Non-Energy Star Dishwasher |  | unit |  | TRM Version 6.0 | 2021-12-16 | 596 | 0 | 4686 | 0 | 88539 | 0 | 2929 | 0 | 20 | Low-Income | 0 | 1 | 1
RES-CF-SH-493-01 | Current |  | Residential | Condensing Furnace |  | Natural Replacement | space heating | High Efficiency Condensing Furnace | >=97% AFUE | Condensing Furnace | 95% AFUE |  | kBtu/hr | TRM Version 5.0 | 2020-11-12 | 0 | 0.446 | 0 | 0 | 0 | 0 | 188 | 0 | 18 | Low-Income | 0 | 1 | 1
RES-SH-WH-567-02 | Current |  | Residential | Showerhead |  | Retrofit | water heating | Low-flow showerhead | 1.25 GPM (Per household) | Average Existing Stock | 2.5 GPM | unit |  | TRM Version 5.0 | 2020-11-12 | 28.2 | 0 | 0 | 0 | 13885 | 0 | actual cost |  | 10 | Low-Income | 0 | 0.851 | 1
RES-SH-WH-568-02 | Current |  | Residential | Showerhead |  | Retrofit | water heating | Low-flow showerhead | 1.5 GPM (Per Household) | Average Existing Stock | 2.5 GPM | unit |  | TRM Version 5.0 | 2020-11-12 | 22.5 | 0 | 0 | 0 | 9546 | 0 | actual cost |  | 10 | Low-Income | 0 | 0.851 | 1
RES-SH-WH-567-06 | Current |  | Residential | Showerhead |  | New Construction | water heating | Low-flow showerhead | 1.25 GPM (Per household) | Average Existing Stock | 2.0 GPM | unit |  | TRM Version 5.0 | 2020-11-12 | 16.9 | 0 | 0 | 0 | 9119 | 0 | actual cost |  | 10 | Low-Income | 0 | 0.851 | 1
RES-SH-WH-568-06 | Current |  | Residential | Showerhead |  | New Construction | water heating | Low-flow showerhead | 1.5 GPM (Per Household) | Average Existing Stock | 2.0 GPM | unit |  | TRM Version 5.0 | 2020-11-12 | 11.3 | 0 | 0 | 0 | 4860 | 0 | actual cost |  | 10 | Low-Income | 0 | 0.851 | 1
COM-DS-SH-560-02 | Current |  | Commercial | Dock Door Seals |  | Retrofit | space heating | Dock Door Seals | 10' x 10' | Dock door with deteriorated seals |  | unit |  | TRM Version 5.0 | 2020-11-12 | 1736 | 0 | 433 | 0 | 0 | 0 | 2968 | 0 | 10 | Low-Income | 0 | 1 | 1
COM-DS-SH-564-02 | Current |  | Commercial | Dock Door Seals |  | Retrofit | space heating | Dock Door Seals | 10' x 10' | Dock door without seals |  | unit |  | TRM Version 5.0 | 2020-11-12 | 4501 | 0 | 1123 | 0 | 0 | 0 | 2615 | 0 | 10 | Low-Income | 0 | 1 | 1
COM-CM-SH-497-04 | Current |  | Commercial | Condensing Make Up Air Unit | Commercial | New Construction/Natural Replacement | space heating | Condensing Make Up Air Unit (MUA) - Commercial | 2 Speed | Conventional MUA | 80% Thermal Efficiency |  | CFM | TRM Version 5.0 | 2020-11-12 | 0 | 1.22 | 0 | 1.24 | 0 | 0 | 870 | 1.01 | 20 | Low-Income | 0 | 1 | 1
COM-DW-WH-554-02 | Replaced | Updated in TRM Version 7.0; revised from TRM Version 5.0: natural gas, electric savings, and water savings | Commercial | Dishwasher |  | New Construction/Natural Replacement | water heating | Energy Star Dishwasher | Single Tank Conveyor - Low Temperature | Non-Energy Star Dishwasher |  | unit |  | TRM Version 6.0 | 2021-12-16 | 1822 | 0 | 0 | 0 | 270824 | 0 | 0 | 0 | 20 | Low-Income | 0 | 1 | 1
COM-DW-WH-551-02 | Replaced | Updated in TRM Version 7.0; revised from TRM Version 5.0: natural gas, electric savings, and water savings | Commercial | Dishwasher |  | New Construction/Natural Replacement | water heating | Energy Star Dishwasher | Stationary Single Tank Door – High Temperature | Non-Energy Star Dishwasher |  | unit |  | TRM Version 6.0 | 2021-12-16 | 981 | 0 | 4601 | 0 | 145828 | 0 | 1100 | 0 | 15 | Low-Income | 0 | 1 | 1
COM-DW-WH-552-02 | Replaced | Updated in TRM Version 7.0; revised from TRM Version 5.0: natural gas, electric savings, and water savings | Commercial | Dishwasher |  | New Construction/Natural Replacement | water heating | Energy Star Dishwasher | Stationary Single Tank Door – Low Temperature | Non-Energy Star Dishwasher |  | unit |  | TRM Version 6.0 | 2021-12-16 | 2256 | 0 | 0 | 0 | 335406 | 0 | 0 | 0 | 15 | Low-Income | 0 | 1 | 1
COM-DW-WH-549-02 | Replaced | Updated in TRM Version 7.0; revised from TRM Version 5.0: natural gas, electric savings, and water savings | Commercial | Dishwasher |  | New Construction/Natural Replacement | water heating | Energy Star Dishwasher | Undercounter – High Temperature | Non-Energy Star Dishwasher |  | unit |  | TRM Version 6.0 | 2021-12-16 | 151 | 0 | 1975 | 0 | 22460 | 0 | 171 | 0 | 10 | Low-Income | 0 | 1 | 1
COM-CM-SH-500-04 | Current |  | Commercial | Condensing Make Up Air Unit | Multi-Residential and Long Term Care | New Construction/Natural Replacement | space heating | Condensing Make Up Air Unit (MUA) - Commercial | 2 Speed | Conventional MUA | 80% Thermal Efficiency |  | CFM | TRM Version 5.0 | 2020-11-12 | 0 | 2.45 | 0 | 1.61 | 0 | 0 | 870 | 1.01 | 20 | Low-Income | 0 | 1 | 1
COM-DF-SH-545-02 | Current |  | Commercial | Destratification Fans |  | New Construction | space heating | HVLS (High Volume Low Speed) Destratification Fans | 20 ft fan diameter | No destratification fans |  | fan |  | TRM Version 5.0 | 2020-11-12 | 1472 | 0 | 0 | 0 | 0 | 0 | 7961 | 0 | 15 | Low-Income | 0 | 1 | 1
COM-DF-SH-546-02 | Current |  | Commercial | Destratification Fans |  | Retrofit | space heating | HVLS (High Volume Low Speed) Destratification Fans | 20 ft fan diameter | No destratification fans |  | fan |  | TRM Version 5.0 | 2020-11-12 | 2029 | 0 | 0 | 0 | 0 | 0 | 7961 | 0 | 15 | Low-Income | 0 | 1 | 1
COM-DF-SH-547-02 | Current |  | Commercial | Destratification Fans |  | New Construction | space heating | HVLS (High Volume Low Speed) Destratification Fans | 24 ft fan diameter | No destratification fans |  | fan |  | TRM Version 5.0 | 2020-11-12 | 2120 | 0 | 0 | 0 | 0 | 0 | 7961 | 0 | 15 | Low-Income | 0 | 1 | 1
COM-DF-SH-548-02 | Current |  | Commercial | Destratification Fans |  | Retrofit | space heating | HVLS (High Volume Low Speed) Destratification Fans | 24 ft fan diameter | No destratification fans |  | fan |  | TRM Version 5.0 | 2020-11-12 | 2922 | 0 | 0 | 0 | 0 | 0 | 7961 | 0 | 15 | Low-Income | 0 | 1 | 1
COM-DS-SH-559-02 | Current |  | Commercial | Dock Door Seals |  | Retrofit | space heating | Dock Door Seals | 8' x 10' | Dock door with deteriorated seals |  | unit |  | TRM Version 5.0 | 2020-11-12 | 2041 | 0 | 509 | 0 | 0 | 0 | 1617 | 0 | 10 | Low-Income | 0 | 1 | 1
COM-DS-SH-563-02 | Current |  | Commercial | Dock Door Seals |  | Retrofit | space heating | Dock Door Seals | 8' x 10' | Dock door without seals |  | unit |  | TRM Version 5.0 | 2020-11-12 | 5087 | 0 | 1269 | 0 | 0 | 0 | 1455 | 0 | 10 | Low-Income | 0 | 1 | 1
COM-DS-SH-557-02 | Current |  | Commercial | Dock Door Seals |  | Retrofit | space heating | Dock Door Seals | 8' x 8' | Dock door with deteriorated seals |  | unit |  | TRM Version 5.0 | 2020-11-12 | 1897 | 0 | 451 | 0 | 0 | 0 | 1425 | 0 | 10 | Low-Income | 0 | 1 | 1
COM-DW-WH-550-02 | Replaced | Updated in TRM Version 7.0; revised from TRM Version 5.0: natural gas, electric savings, and water savings | Commercial | Dishwasher |  | New Construction/Natural Replacement | water heating | Energy Star Dishwasher | Undercounter – Low Temperature | Non-Energy Star Dishwasher |  | unit |  | TRM Version 6.0 | 2021-12-16 | 355 | 0 | 0 | 0 | 52733 | 0 | 71 | 0 | 10 | Low-Income | 0 | 1 | 1
COM-IH-SH-579-08 | Retired | retired in TRM 6.0 | Commercial | Infrared Heaters |  | Retrofit | space heating | 2-Stage Infrared Heaters | 165,000 - 300,000 BTU/hr | Regular Unit Heater |  |  | kBtu/hr input capacity | TRM Version 5.0 | 2020-11-12 | 0 | 13.1 | 1040 | 0 | 0 | 0 | 0 | 30.28 | 17 | Low-Income | 0 | 1 | 1
COM-IH-SH-582-08 | Retired | retired in TRM 6.0 | Commercial | Infrared Heaters |  | New Construction | space heating | 2-Stage Infrared Heaters | 165,000 - 300,000 BTU/hr | Regular Unit Heater |  |  | kBtu/hr input capacity | TRM Version 5.0 | 2020-11-12 | 0 | 9.8 | 510 | 0 | 0 | 0 | 0 | 11.22 | 17 | Low-Income | 0 | 1 | 1
COM-IH-SH-585-08 | Retired | retired in TRM 6.0 | Commercial | Infrared Heaters |  | Retrofit | space heating | Single Stage & High Intensity Infrared Heaters | 165,000 - 300,000 BTU/hr | Regular Unit Heater |  |  | kBtu/hr input capacity | TRM Version 5.0 | 2020-11-12 | 0 | 11.5 | 1040 | 0 | 0 | 0 | 0 | 30.28 | 17 | Low-Income | 0 | 1 | 1
COM-IH-SH-588-08 | Retired | retired in TRM 6.0 | Commercial | Infrared Heaters |  | New Construction | space heating | Single Stage & High Intensity Infrared Heaters | 165,000 - 300,000 BTU/hr | Regular Unit Heater |  |  | kBtu/hr input capacity | TRM Version 5.0 | 2020-11-12 | 0 | 8.6 | 510 | 0 | 0 | 0 | 0 | 11.22 | 17 | Low-Income | 0 | 1 | 1
COM-IH-SH-578-08 | Retired | retired in TRM 6.0 | Commercial | Infrared Heaters |  | Retrofit | space heating | 2-Stage Infrared Heaters | 50,000 - 164,999 BTU/hr | Regular Unit Heater |  |  | kBtu/hr input capacity | TRM Version 5.0 | 2020-11-12 | 0 | 13.1 | 300 | 0 | 0 | 0 | 0 | 30.28 | 17 | Low-Income | 0 | 1 | 1
COM-IH-SH-581-08 | Retired | retired in TRM 6.0 | Commercial | Infrared Heaters |  | New Construction | space heating | 2-Stage Infrared Heaters | 50,000 - 164,999 BTU/hr | Regular Unit Heater |  |  | kBtu/hr input capacity | TRM Version 5.0 | 2020-11-12 | 0 | 9.8 | 225 | 0 | 0 | 0 | 0 | 11.22 | 17 | Low-Income | 0 | 1 | 1
COM-IH-SH-584-08 | Retired | retired in TRM 6.0 | Commercial | Infrared Heaters |  | Retrofit | space heating | Single Stage & High Intensity Infrared Heaters | 50,000 - 164,999 BTU/hr | Regular Unit Heater |  |  | kBtu/hr input capacity | TRM Version 5.0 | 2020-11-12 | 0 | 11.5 | 300 | 0 | 0 | 0 | 0 | 30.28 | 17 | Low-Income | 0 | 1 | 1
COM-IH-SH-587-08 | Retired | retired in TRM 6.0 | Commercial | Infrared Heaters |  | New Construction | space heating | Single Stage & High Intensity Infrared Heaters | 50,000 - 164,999 BTU/hr | Regular Unit Heater |  |  | kBtu/hr input capacity | TRM Version 5.0 | 2020-11-12 | 0 | 8.6 | 225 | 0 | 0 | 0 | 0 | 11.22 | 17 | Low-Income | 0 | 1 | 1
COM-IH-SH-577-03 | Retired | retired in TRM 6.0 | Commercial | Infrared Heaters |  | Retrofit | space heating | 2-Stage Infrared Heaters | 0 - 49,999 BTU/hr | Regular Unit Heater |  |  | kBtu/hr input capacity | TRM Version 5.0 | 2020-11-12 | 0 | 13.1 | 0 | 0 | 0 | 0 | 0 | 30.28 | 17 | Midstream | 0.33 | 1 | 1
COM-IH-SH-580-03 | Retired | retired in TRM 6.0 | Commercial | Infrared Heaters |  | New Construction | space heating | 2-Stage Infrared Heaters | 0 - 49,999 BTU/hr | Regular Unit Heater |  |  | kBtu/hr input capacity | TRM Version 5.0 | 2020-11-12 | 0 | 9.8 | 0 | 0 | 0 | 0 | 0 | 11.22 | 17 | Midstream | 0.33 | 1 | 1
COM-IH-SH-583-03 | Retired | retired in TRM 6.0 | Commercial | Infrared Heaters |  | Retrofit | space heating | Single Stage & High Intensity Infrared Heaters | 0 - 49,999 BTU/hr | Regular Unit Heater |  |  | kBtu/hr input capacity | TRM Version 5.0 | 2020-11-12 | 0 | 11.5 | 0 | 0 | 0 | 0 | 0 | 30.28 | 17 | Midstream | 0.33 | 1 | 1
COM-IH-SH-586-03 | Retired | retired in TRM 6.0 | Commercial | Infrared Heaters |  | New Construction | space heating | Single Stage & High Intensity Infrared Heaters | 0 - 49,999 BTU/hr | Regular Unit Heater |  |  | kBtu/hr input capacity | TRM Version 5.0 | 2020-11-12 | 0 | 8.6 | 0 | 0 | 0 | 0 | 0 | 11.22 | 17 | Midstream | 0.33 | 1 | 1
COM-IH-SH-579-03 | Retired | retired in TRM 6.0 | Commercial | Infrared Heaters |  | Retrofit | space heating | 2-Stage Infrared Heaters | 165,000 - 300,000 BTU/hr | Regular Unit Heater |  |  | kBtu/hr input capacity | TRM Version 5.0 | 2020-11-12 | 0 | 13.1 | 1040 | 0 | 0 | 0 | 0 | 30.28 | 17 | Midstream | 0.33 | 1 | 1
COM-IH-SH-582-03 | Retired | retired in TRM 6.0 | Commercial | Infrared Heaters |  | New Construction | space heating | 2-Stage Infrared Heaters | 165,000 - 300,000 BTU/hr | Regular Unit Heater |  |  | kBtu/hr input capacity | TRM Version 5.0 | 2020-11-12 | 0 | 9.8 | 510 | 0 | 0 | 0 | 0 | 11.22 | 17 | Midstream | 0.33 | 1 | 1
COM-IH-SH-585-03 | Retired | retired in TRM 6.0 | Commercial | Infrared Heaters |  | Retrofit | space heating | Single Stage & High Intensity Infrared Heaters | 165,000 - 300,000 BTU/hr | Regular Unit Heater |  |  | kBtu/hr input capacity | TRM Version 5.0 | 2020-11-12 | 0 | 11.5 | 1040 | 0 | 0 | 0 | 0 | 30.28 | 17 | Midstream | 0.33 | 1 | 1
COM-IH-SH-588-03 | Retired | retired in TRM 6.0 | Commercial | Infrared Heaters |  | New Construction | space heating | Single Stage & High Intensity Infrared Heaters | 165,000 - 300,000 BTU/hr | Regular Unit Heater |  |  | kBtu/hr input capacity | TRM Version 5.0 | 2020-11-12 | 0 | 8.6 | 510 | 0 | 0 | 0 | 0 | 11.22 | 17 | Midstream | 0.33 | 1 | 1
COM-DS-SH-561-02 | Current |  | Commercial | Dock Door Seals |  | Retrofit | space heating | Dock Door Seals | 8' x 8' | Dock door without seals |  | unit |  | TRM Version 5.0 | 2020-11-12 | 4853 | 0 | 1155 | 0 | 0 | 0 | 1263 | 0 | 10 | Low-Income | 0 | 1 | 1
COM-DS-SH-558-02 | Current |  | Commercial | Dock Door Seals |  | Retrofit | space heating | Dock Door Seals | 8' x 9' | Dock door with deteriorated seals |  | unit |  | TRM Version 5.0 | 2020-11-12 | 1977 | 0 | 481 | 0 | 0 | 0 | 1580 | 0 | 10 | Low-Income | 0 | 1 | 1
COM-DS-SH-562-02 | Current |  | Commercial | Dock Door Seals |  | Retrofit | space heating | Dock Door Seals | 8' x 9' | Dock door without seals |  | unit |  | TRM Version 5.0 | 2020-11-12 | 4988 | 0 | 1214 | 0 | 0 | 0 | 1417 | 0 | 10 | Low-Income | 0 | 1 | 1
RES-AT-SH-320-03 | Current |  | Residential | Adaptive Thermostat |  | New Construction | space heating | Adaptive Thermostats | Adaptive Thermostat | Programmable Thermostat |  | unit |  | TRM Version 5.0 | 2020-11-12 | 105 | 0 | 206 | 0 | 0 | 0 | 200 | 0 | 15 | Low-Income | 0 | 1 | 1
RES-AT-SH-321-03 | Current |  | Residential | Adaptive Thermostat |  | Retrofit | space heating | Adaptive Thermostats - Direct Install | Adaptive Thermostat | Non-Programmable Thermostat |  | unit |  | TRM Version 5.0 | 2020-11-12 | 217 | 0 | 235 | 0 | 0 | 0 | 300 | 0 | 15 | Low-Income | 0 | 1 | 1
RES-AT-SH-322-03 | Current |  | Residential | Adaptive Thermostat |  | Retrofit | space heating | Adaptive Thermostats - Direct Install | Adaptive Thermostat | Programmable Thermostat |  | unit |  | TRM Version 5.0 | 2020-11-12 | 173 | 0 | 235 | 0 | 0 | 0 | 300 | 0 | 15 | Low-Income | 0 | 1 | 1
RES-AT-SH-323-03 | Current |  | Residential | Adaptive Thermostat |  | Retrofit | space heating | Adaptive Thermostats - Retail Purchase | Adaptive Thermostat | Blended value. Non Programmable and programmable Thermostat |  | unit |  | TRM Version 5.0 | 2020-11-12 | 185 | 0 | 176 | 0 | 0 | 0 | 300 | 0 | 15 | Low-Income | 0 | 1 | 1
RES-AT-SH-324-03 | Current |  | Residential | Adaptive Thermostat |  | Retrofit | space heating | Adaptive Thermostats - Direct Install | Adaptive Thermostat | Non-Programmable Thermostat | No central air conditioning | unit |  | TRM Version 5.0 | 2020-11-12 | 217 | 0 | 0 | 0 | 0 | 0 | 300 | 0 | 15 | Low-Income | 0 | 1 | 1
RES-AT-SH-325-03 | Current |  | Residential | Adaptive Thermostat |  | Retrofit | space heating | Adaptive Thermostats - Direct Install | Adaptive Thermostat | Programmable Thermostat | No central air conditioning | unit |  | TRM Version 5.0 | 2020-11-12 | 173 | 0 | 0 | 0 | 0 | 0 | 300 | 0 | 15 | Low-Income | 0 | 1 | 1
RES-FA-WH-461-03 | Current |  | Residential | Faucet Aerator |  | Retrofit | water heating | Faucet Aerator | Bathroom, 1.0 GPM | Standard flow bathroom aerator (code compliant) | 2.2 GPM | unit |  | TRM Version 7.0 | 2022-11-30 | 6.65 | 0 | 0 | 0 | 2501 | 0 | 0.6 | 0 | 10 | Low-Income | 0 | 0.6458 | 1
RES-FA-WH-460-03 | Current |  | Residential | Faucet Aerator |  | Retrofit | water heating | Faucet Aerator | Bathroom, 1.5 GPM | Standard flow bathroom aerator (code compliant) | 2.2 GPM | unit |  | TRM Version 7.0 | 2022-11-30 | 3.88 | 0 | 0 | 0 | 1459 | 0 | 0.6 | 0 | 10 | Low-Income | 0 | 0.6458 | 1
RES-TW-WH-576-02 | Current |  | Residential | Tankless Water Heater |  | New Construction/Natural Replacement | water heating | Tankless Water Heater | Condensing Tankless Water Heater, EF = 0.91 | Storage Tank Water Heater, EF=0.67 | EF=0.67 | unit |  | TRM Version 7.0 | 2022-11-30 | 130.7 | 0 | 0 | 0 | 0 | 0 | 2066 | 0 | 20 | Low-Income | 0 | 1 | 1
COM-CM-SH-496-04 | Current |  | Commercial | Condensing Make Up Air Unit | Commercial | New Construction/Natural Replacement | space heating | Condensing Make Up Air Unit (MUA) - Commercial | Constant Speed | Conventional MUA | 80% Thermal Efficiency |  | CFM | TRM Version 5.0 | 2020-11-12 | 0 | 0.407 | 0 | 0 | 0 | 0 | 870 | 0.66 | 20 | Low-Income | 0 | 1 | 1
COM-CM-SH-499-04 | Current |  | Commercial | Condensing Make Up Air Unit | Multi-Residential and Long Term Care | New Construction/Natural Replacement | space heating | Condensing Make Up Air Unit (MUA) - Commercial | Constant Speed | Conventional MUA | 80% Thermal Efficiency |  | CFM | TRM Version 5.0 | 2020-11-12 | 0 | 0.919 | 0 | 0 | 0 | 0 | 870 | 0.66 | 20 | Low-Income | 0 | 1 | 1
RES-HP-SH-565-02 | Current |  | Residential | Heat Reflector Panels |  | Retrofit | space heating | Heat Reflector Panels | Heat reflector panel installed behind radiator | No heat reflector panel installed behind radiator |  | unit |  | TRM Version 5.0 | 2020-11-12 | 143.2 | 0 | 0 | 0 | 0 | 0 | actual cost |  | 25 | Low-Income | 0 | 1 | 1
RES-TW-WH-575-02 | Current |  | Residential | Tankless Water Heater |  | New Construction/Natural Replacement | water heating | Tankless Water Heater | High Efficiency Non-Condensing Tankless Water Heater, EF = 0.82 | Storage Tank Water Heater, EF=0.67 | EF=0.67 | unit |  | TRM Version 7.0 | 2022-11-30 | 90.7 | 0 | 0 | 0 | 0 | 0 | 1667 | 0 | 20 | Low-Income | 0 | 1 | 1
RES-SW-WH-574-02 | Current |  | Residential | Storage Water Heater |  | New Construction | water heating | High Efficiency Gas Storage Water Heaters | High efficiency storage tank water heater (Energy Factor of 0.80) | ENERGY STAR power vented storage tank water heater | Energy factor of 0.67 | unit |  | TRM Version 7.0 | 2022-11-30 | 44.1 | 0 | 0 | 0 | 0 | 0 | 545 | 0 | 16 | Low-Income | 0 | 1 | 1
COM-HRV-SH-336-04 | Current |  | Commercial | Heat Recovery Ventialation | High Use | New Construction/Natural Replacement | space heating | High Efficient 65% Heat Recovery Ventilation High Use Group (Multi-Residential, Health Care, Nursing Homes) | HRV with Minimum 65% Sensible Heat Recovery Effectiveness at 32°F | HRV with Minimum 55% Sensible Heat Recovery Effectiveness as per Ontario Building Code 2017 |  |  | CFM | TRM Version 5.0 | 2020-11-12 | 0 | 0.7 | 0 | 0 | 0 | 0 | 0 | 1 | 14 | Low-Income | 0 | 1 | 1
COM-HRV-SH-337-04 | Current |  | Commercial | Heat Recovery Ventialation | Low Use | New Construction/Natural Replacement | space heating | High Efficient 65% Heat Recovery Ventilation Low Use Group (Office, Warehouse, School) | HRV with Minimum 65% Sensible Heat Recovery Effectiveness at 32°F | HRV with Minimum 55% Sensible Heat Recovery Effectiveness as per Ontario Building Code 2017 |  |  | CFM | TRM Version 5.0 | 2020-11-12 | 0 | 0.25 | 0 | 0 | 0 | 0 | 0 | 1 | 14 | Low-Income | 0 | 1 | 1
COM-HRV-SH-338-04 | Current |  | Commercial | Heat Recovery Ventialation | Medium Use | New Construction/Natural Replacement | space heating | High Efficient 65% Heat Recovery Ventilation Medium Use Group (Hotel, Restaurant, Retail) | HRV with Minimum 65% Sensible Heat Recovery Effectiveness at 32°F | HRV with Minimum 55% Sensible Heat Recovery Effectiveness as per Ontario Building Code 2017 |  |  | CFM | TRM Version 5.0 | 2020-11-12 | 0 | 0.39 | 0 | 0 | 0 | 0 | 0 | 1 | 14 | Low-Income | 0 | 1 | 1
COM-HRV-SH-345-04 | Current |  | Commercial | Heat Recovery Ventialation | Multi-Family, Health Care and Nursing Homes | New Construction/Natural Replacement | space heating | High Efficient 65% Heat Recovery Ventilation High Use Group (Multi-Residential, Health Care, Nursing Homes) | HRV with Minimum 65% Sensible Heat Recovery Effectiveness at 32°F | HRV with Minimum 55% Sensible Heat Recovery Effectiveness as per Ontario Building Code 2017 |  |  | CFM | TRM Version 5.0 | 2020-11-12 | 0 | 0.7 | 0 | 0 | 0 | 0 | 0 | 1 | 14 | Low-Income | 0 | 1 | 1
COM-HRV-SH-346-04 | Current |  | Commercial | Heat Recovery Ventialation | Hotels | New Construction/Natural Replacement | space heating | High Efficient 65% Heat Recovery Ventilation Medium Use Group (Hotel, Restaurant, Retail) | HRV with Minimum 65% Sensible Heat Recovery Effectiveness at 32°F | HRV with Minimum 55% Sensible Heat Recovery Effectiveness as per Ontario Building Code 2017 |  |  | CFM | TRM Version 5.0 | 2020-11-12 | 0 | 0.5 | 0 | 0 | 0 | 0 | 0 | 1 | 14 | Low-Income | 0 | 1 | 1
COM-HRV-SH-347-04 | Current |  | Commercial | Heat Recovery Ventialation | Restaurant | New Construction/Natural Replacement | space heating | High Efficient 65% Heat Recovery Ventilation Medium Use Group (Hotel, Restaurant, Retail) | HRV with Minimum 65% Sensible Heat Recovery Effectiveness at 32°F | HRV with Minimum 55% Sensible Heat Recovery Effectiveness as per Ontario Building Code 2017 |  |  | CFM | TRM Version 5.0 | 2020-11-12 | 0 | 0.36 | 0 | 0 | 0 | 0 | 0 | 1 | 14 | Low-Income | 0 | 1 | 1
COM-HRV-SH-348-04 | Current |  | Commercial | Heat Recovery Ventialation | Retail | New Construction/Natural Replacement | space heating | High Efficient 65% Heat Recovery Ventilation Medium Use Group (Hotel, Restaurant, Retail) | HRV with Minimum 65% Sensible Heat Recovery Effectiveness at 32°F | HRV with Minimum 55% Sensible Heat Recovery Effectiveness as per Ontario Building Code 2017 |  |  | CFM | TRM Version 5.0 | 2020-11-12 | 0 | 0.3 | 0 | 0 | 0 | 0 | 0 | 1 | 14 | Low-Income | 0 | 1 | 1
COM-IH-SH-578-03 | Retired | retired in TRM 6.0 | Commercial | Infrared Heaters |  | Retrofit | space heating | 2-Stage Infrared Heaters | 50,000 - 164,999 BTU/hr | Regular Unit Heater |  |  | kBtu/hr input capacity | TRM Version 5.0 | 2020-11-12 | 0 | 13.1 | 300 | 0 | 0 | 0 | 0 | 30.28 | 17 | Midstream | 0.33 | 1 | 1
COM-IH-SH-581-03 | Retired | retired in TRM 6.0 | Commercial | Infrared Heaters |  | New Construction | space heating | 2-Stage Infrared Heaters | 50,000 - 164,999 BTU/hr | Regular Unit Heater |  |  | kBtu/hr input capacity | TRM Version 5.0 | 2020-11-12 | 0 | 9.8 | 225 | 0 | 0 | 0 | 0 | 11.22 | 17 | Midstream | 0.33 | 1 | 1
COM-IH-SH-584-03 | Retired | retired in TRM 6.0 | Commercial | Infrared Heaters |  | Retrofit | space heating | Single Stage & High Intensity Infrared Heaters | 50,000 - 164,999 BTU/hr | Regular Unit Heater |  |  | kBtu/hr input capacity | TRM Version 5.0 | 2020-11-12 | 0 | 11.5 | 300 | 0 | 0 | 0 | 0 | 30.28 | 17 | Midstream | 0.33 | 1 | 1
COM-IH-SH-587-03 | Retired | retired in TRM 6.0 | Commercial | Infrared Heaters |  | New Construction | space heating | Single Stage & High Intensity Infrared Heaters | 50,000 - 164,999 BTU/hr | Regular Unit Heater |  |  | kBtu/hr input capacity | TRM Version 5.0 | 2020-11-12 | 0 | 8.6 | 225 | 0 | 0 | 0 | 0 | 11.22 | 17 | Midstream | 0.33 | 1 | 1
COM-HRV-SH-349-04 | Current |  | Commercial | Heat Recovery Ventialation | Office | New Construction/Natural Replacement | space heating | High Efficient 65% Heat Recovery Ventilation Low Use Group (Office, Warehouse, School) | HRV with Minimum 65% Sensible Heat Recovery Effectiveness at 32°F | HRV with Minimum 55% Sensible Heat Recovery Effectiveness as per Ontario Building Code 2017 |  |  | CFM | TRM Version 5.0 | 2020-11-12 | 0 | 0.27 | 0 | 0 | 0 | 0 | 0 | 1 | 14 | Low-Income | 0 | 1 | 1
COM-HRV-SH-350-04 | Current |  | Commercial | Heat Recovery Ventialation | Warehouse | New Construction/Natural Replacement | space heating | High Efficient 65% Heat Recovery Ventilation Low Use Group (Office, Warehouse, School) | HRV with Minimum 65% Sensible Heat Recovery Effectiveness at 32°F | HRV with Minimum 55% Sensible Heat Recovery Effectiveness as per Ontario Building Code 2017 |  |  | CFM | TRM Version 5.0 | 2020-11-12 | 0 | 0.25 | 0 | 0 | 0 | 0 | 0 | 1 | 14 | Low-Income | 0 | 1 | 1
COM-HRV-SH-351-04 | Current |  | Commercial | Heat Recovery Ventialation | School | New Construction/Natural Replacement | space heating | High Efficient 65% Heat Recovery Ventilation Low Use Group (Office, Warehouse, School) | HRV with Minimum 65% Sensible Heat Recovery Effectiveness at 32°F | HRV with Minimum 55% Sensible Heat Recovery Effectiveness as per Ontario Building Code 2017 |  |  | CFM | TRM Version 5.0 | 2020-11-12 | 0 | 0.22 | 0 | 0 | 0 | 0 | 0 | 1 | 14 | Low-Income | 0 | 1 | 1
COM-HRV-SH-339-04 | Current |  | Commercial | Heat Recovery Ventialation | High Use | New Construction/Natural Replacement | space heating | High Efficient 75% Heat Recovery Ventilation High Use Group (Multi-Residential, Health Care, Nursing Homes) | HRV with Minimum 75% Sensible Heat Recovery Effectiveness at 32°F | HRV with Minimum 55% Sensible Heat Recovery Effectiveness as per Ontario Building Code 2017 |  |  | CFM | TRM Version 5.0 | 2020-11-12 | 0 | 1.39 | 0 | 0 | 0 | 0 | 0 | 2 | 14 | Low-Income | 0 | 1 | 1
COM-HRV-SH-340-04 | Current |  | Commercial | Heat Recovery Ventialation | Low Use | New Construction/Natural Replacement | space heating | High Efficient 75% Heat Recovery Ventilation Low Use Group (Office, Warehouse, School) | HRV with Minimum 75% Sensible Heat Recovery Effectiveness at 32°F | HRV with Minimum 55% Sensible Heat Recovery Effectiveness as per Ontario Building Code 2017 |  |  | CFM | TRM Version 5.0 | 2020-11-12 | 0 | 0.5 | 0 | 0 | 0 | 0 | 0 | 2 | 14 | Low-Income | 0 | 1 | 1
COM-HRV-SH-341-04 | Current |  | Commercial | Heat Recovery Ventialation | Medium Use | New Construction/Natural Replacement | space heating | High Efficient 75% Heat Recovery Ventilation Medium Use Group (Hotel, Restaurant, Retail) | HRV with Minimum 75% Sensible Heat Recovery Effectiveness at 32°F | HRV with Minimum 55% Sensible Heat Recovery Effectiveness as per Ontario Building Code 2017 |  |  | CFM | TRM Version 5.0 | 2020-11-12 | 0 | 0.78 | 0 | 0 | 0 | 0 | 0 | 2 | 14 | Low-Income | 0 | 1 | 1
COM-HRV-SH-352-04 | Current |  | Commercial | Heat Recovery Ventialation | Multi-Family, Health Care and Nursing Homes | New Construction/Natural Replacement | space heating | High Efficient 75% Heat Recovery Ventilation High Use Group (Multi-Residential, Health Care, Nursing Homes) | HRV with Minimum 75% Sensible Heat Recovery Effectiveness at 32°F | HRV with Minimum 55% Sensible Heat Recovery Effectiveness as per Ontario Building Code 2017 |  |  | CFM | TRM Version 5.0 | 2020-11-12 | 0 | 1.39 | 0 | 0 | 0 | 0 | 0 | 2 | 14 | Low-Income | 0 | 1 | 1
COM-HRV-SH-353-04 | Current |  | Commercial | Heat Recovery Ventialation | Hotels | New Construction/Natural Replacement | space heating | High Efficient 75% Heat Recovery Ventilation Medium Use Group (Hotel, Restaurant, Retail) | HRV with Minimum 75% Sensible Heat Recovery Effectiveness at 32°F | HRV with Minimum 55% Sensible Heat Recovery Effectiveness as per Ontario Building Code 2017 |  |  | CFM | TRM Version 5.0 | 2020-11-12 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 2 | 14 | Low-Income | 0 | 1 | 1
COM-HRV-SH-354-04 | Current |  | Commercial | Heat Recovery Ventialation | Restaurant | New Construction/Natural Replacement | space heating | High Efficient 75% Heat Recovery Ventilation Medium Use Group (Hotel, Restaurant, Retail) | HRV with Minimum 75% Sensible Heat Recovery Effectiveness at 32°F | HRV with Minimum 55% Sensible Heat Recovery Effectiveness as per Ontario Building Code 2017 |  |  | CFM | TRM Version 5.0 | 2020-11-12 | 0 | 0.72 | 0 | 0 | 0 | 0 | 0 | 2 | 14 | Low-Income | 0 | 1 | 1
COM-HRV-SH-355-04 | Current |  | Commercial | Heat Recovery Ventialation | Retail | New Construction/Natural Replacement | space heating | High Efficient 75% Heat Recovery Ventilation Medium Use Group (Hotel, Restaurant, Retail) | HRV with Minimum 75% Sensible Heat Recovery Effectiveness at 32°F | HRV with Minimum 55% Sensible Heat Recovery Effectiveness as per Ontario Building Code 2017 |  |  | CFM | TRM Version 5.0 | 2020-11-12 | 0 | 0.61 | 0 | 0 | 0 | 0 | 0 | 2 | 14 | Low-Income | 0 | 1 | 1
COM-HRV-SH-356-04 | Current |  | Commercial | Heat Recovery Ventialation | Office | New Construction/Natural Replacement | space heating | High Efficient 75% Heat Recovery Ventilation Low Use Group (Office, Warehouse, School) | HRV with Minimum 75% Sensible Heat Recovery Effectiveness at 32°F | HRV with Minimum 55% Sensible Heat Recovery Effectiveness as per Ontario Building Code 2017 |  |  | CFM | TRM Version 5.0 | 2020-11-12 | 0 | 0.53 | 0 | 0 | 0 | 0 | 0 | 2 | 14 | Low-Income | 0 | 1 | 1
COM-HRV-SH-357-04 | Current |  | Commercial | Heat Recovery Ventialation | Warehouse | New Construction/Natural Replacement | space heating | High Efficient 75% Heat Recovery Ventilation Low Use Group (Office, Warehouse, School) | HRV with Minimum 75% Sensible Heat Recovery Effectiveness at 32°F | HRV with Minimum 55% Sensible Heat Recovery Effectiveness as per Ontario Building Code 2017 |  |  | CFM | TRM Version 5.0 | 2020-11-12 | 0 | 0.51 | 0 | 0 | 0 | 0 | 0 | 2 | 14 | Low-Income | 0 | 1 | 1
COM-HRV-SH-358-04 | Current |  | Commercial | Heat Recovery Ventialation | School | New Construction/Natural Replacement | space heating | High Efficient 75% Heat Recovery Ventilation Low Use Group (Office, Warehouse, School) | HRV with Minimum 75% Sensible Heat Recovery Effectiveness at 32°F | HRV with Minimum 55% Sensible Heat Recovery Effectiveness as per Ontario Building Code 2017 |  |  | CFM | TRM Version 5.0 | 2020-11-12 | 0 | 0.45 | 0 | 0 | 0 | 0 | 0 | 2 | 14 | Low-Income | 0 | 1 | 1
COM-HRV-SH-342-04 | Current |  | Commercial | Heat Recovery Ventialation | High Use | New Construction/Natural Replacement | space heating | High Efficient 85% Heat Recovery Ventilation High Use Group (Multi-Residential, Health Care, Nursing Homes) | HRV with Minimum 85% Sensible Heat Recovery Effectiveness at 32°F | HRV with Minimum 55% Sensible Heat Recovery Effectiveness as per Ontario Building Code 2017 |  |  | CFM | TRM Version 5.0 | 2020-11-12 | 0 | 2.09 | 0 | 0 | 0 | 0 | 0 | 3 | 14 | Low-Income | 0 | 1 | 1
COM-HRV-SH-343-04 | Current |  | Commercial | Heat Recovery Ventialation | Low Use | New Construction/Natural Replacement | space heating | High Efficient 85% Heat Recovery Ventilation Low Use Group (Office, Warehouse, School) | HRV with Minimum 85% Sensible Heat Recovery Effectiveness at 32°F | HRV with Minimum 55% Sensible Heat Recovery Effectiveness as per Ontario Building Code 2017 |  |  | CFM | TRM Version 5.0 | 2020-11-12 | 0 | 0.74 | 0 | 0 | 0 | 0 | 0 | 3 | 14 | Low-Income | 0 | 1 | 1
COM-HRV-SH-344-04 | Current |  | Commercial | Heat Recovery Ventialation | Medium Use | New Construction/Natural Replacement | space heating | High Efficient 85% Heat Recovery Ventilation Medium Use Group (Hotel, Restaurant, Retail) | HRV with Minimum 85% Sensible Heat Recovery Effectiveness at 32°F | HRV with Minimum 55% Sensible Heat Recovery Effectiveness as per Ontario Building Code 2017 |  |  | CFM | TRM Version 5.0 | 2020-11-12 | 0 | 1.16 | 0 | 0 | 0 | 0 | 0 | 3 | 14 | Low-Income | 0 | 1 | 1
COM-HRV-SH-359-04 | Current |  | Commercial | Heat Recovery Ventialation | Multi-Family, Health Care and Nursing Homes | New Construction/Natural Replacement | space heating | High Efficient 85% Heat Recovery Ventilation High Use Group (Multi-Residential, Health Care, Nursing Homes) | HRV with Minimum 85% Sensible Heat Recovery Effectiveness at 32°F | HRV with Minimum 55% Sensible Heat Recovery Effectiveness as per Ontario Building Code 2017 |  |  | CFM | TRM Version 5.0 | 2020-11-12 | 0 | 2.09 | 0 | 0 | 0 | 0 | 0 | 3 | 14 | Low-Income | 0 | 1 | 1
COM-HRV-SH-360-04 | Current |  | Commercial | Heat Recovery Ventialation | Hotels | New Construction/Natural Replacement | space heating | High Efficient 85% Heat Recovery Ventilation Medium Use Group (Hotel, Restaurant, Retail) | HRV with Minimum 85% Sensible Heat Recovery Effectiveness at 32°F | HRV with Minimum 55% Sensible Heat Recovery Effectiveness as per Ontario Building Code 2017 |  |  | CFM | TRM Version 5.0 | 2020-11-12 | 0 | 1.49 | 0 | 0 | 0 | 0 | 0 | 3 | 14 | Low-Income | 0 | 1 | 1
COM-HRV-SH-361-04 | Current |  | Commercial | Heat Recovery Ventialation | Restaurant | New Construction/Natural Replacement | space heating | High Efficient 85% Heat Recovery Ventilation Medium Use Group (Hotel, Restaurant, Retail) | HRV with Minimum 85% Sensible Heat Recovery Effectiveness at 32°F | HRV with Minimum 55% Sensible Heat Recovery Effectiveness as per Ontario Building Code 2017 |  |  | CFM | TRM Version 5.0 | 2020-11-12 | 0 | 1.08 | 0 | 0 | 0 | 0 | 0 | 3 | 14 | Low-Income | 0 | 1 | 1
COM-HRV-SH-362-04 | Current |  | Commercial | Heat Recovery Ventialation | Retail | New Construction/Natural Replacement | space heating | High Efficient 85% Heat Recovery Ventilation Medium Use Group (Hotel, Restaurant, Retail) | HRV with Minimum 85% Sensible Heat Recovery Effectiveness at 32°F | HRV with Minimum 55% Sensible Heat Recovery Effectiveness as per Ontario Building Code 2017 |  |  | CFM | TRM Version 5.0 | 2020-11-12 | 0 | 0.91 | 0 | 0 | 0 | 0 | 0 | 3 | 14 | Low-Income | 0 | 1 | 1
COM-HRV-SH-363-04 | Current |  | Commercial | Heat Recovery Ventialation | Office | New Construction/Natural Replacement | space heating | High Efficient 85% Heat Recovery Ventilation Low Use Group (Office, Warehouse, School) | HRV with Minimum 85% Sensible Heat Recovery Effectiveness at 32°F | HRV with Minimum 55% Sensible Heat Recovery Effectiveness as per Ontario Building Code 2017 |  |  | CFM | TRM Version 5.0 | 2020-11-12 | 0 | 0.8 | 0 | 0 | 0 | 0 | 0 | 3 | 14 | Low-Income | 0 | 1 | 1
COM-HRV-SH-364-04 | Current |  | Commercial | Heat Recovery Ventialation | Warehouse | New Construction/Natural Replacement | space heating | High Efficient 85% Heat Recovery Ventilation Low Use Group (Office, Warehouse, School) | HRV with Minimum 85% Sensible Heat Recovery Effectiveness at 32°F | HRV with Minimum 55% Sensible Heat Recovery Effectiveness as per Ontario Building Code 2017 |  |  | CFM | TRM Version 5.0 | 2020-11-12 | 0 | 0.76 | 0 | 0 | 0 | 0 | 0 | 3 | 14 | Low-Income | 0 | 1 | 1
COM-HRV-SH-365-04 | Current |  | Commercial | Heat Recovery Ventialation | School | New Construction/Natural Replacement | space heating | High Efficient 85% Heat Recovery Ventilation Low Use Group (Office, Warehouse, School) | HRV with Minimum 85% Sensible Heat Recovery Effectiveness at 32°F | HRV with Minimum 55% Sensible Heat Recovery Effectiveness as per Ontario Building Code 2017 |  |  | CFM | TRM Version 5.0 | 2020-11-12 | 0 | 0.67 | 0 | 0 | 0 | 0 | 0 | 3 | 14 | Low-Income | 0 | 1 | 1
RES-FA-WH-462-03 | Current |  | Residential | Faucet Aerator |  | Retrofit | water heating | Faucet Aerator | Kitchen, 1.0 GPM | Standard flow kitchen aerator (code compliant) | 2.2 GPM | unit |  | TRM Version 7.0 | 2022-11-30 | 20.57 | 0 | 0 | 0 | 7742 | 0 | 1.14 | 0 | 10 | Low-Income | 0 | 0.6768 | 1
RES-FA-WH-463-03 | Current |  | Residential | Faucet Aerator |  | Retrofit | water heating | Faucet Aerator | Kitchen, 1.5 GPM | Standard flow kitchen aerator (code compliant) | 2.2 GPM | unit |  | TRM Version 7.0 | 2022-11-30 | 12 | 0 | 0 | 0 | 4516 | 0 | 1.14 | 0 | 10 | Low-Income | 0 | 0.6768 | 1
COM-ERV-SH-380-03 | Current |  | Commercial | Energy Recovery Ventilation | High Use Group | New Construction/Natural Replacement | space heating | High Efficient 65% Energy Recovery Ventilation High Use Group (Multi-Residential, Health Care, Nursing Homes) | Minimum 65% Sensible Heat Recovery Effectiveness and 63% Total Energy Recovery Effectiveness at 32°F | Minimum 55% Energy Recovery Effectiveness as per Ontario Building Code 2017 |  |  | CFM | TRM Version 5.0 | 2020-11-12 | 0 | 0.85 | 0 | 0 | 0 | 0 | 0 | 1 | 14 | Low-Income | 0 | 1 | 1
COM-ERV-SH-381-03 | Current |  | Commercial | Energy Recovery Ventilation | Medium Use Group | New Construction/Natural Replacement | space heating | High Efficient 65% Energy Recovery Ventilation Medium Use Group (Hotel, Restaurant, Retail) | Minimum 65% Sensible Heat Recovery Effectiveness and 63% Total Energy Recovery Effectiveness at 32°F | Minimum 55% Energy Recovery Effectiveness as per Ontario Building Code 2017 |  |  | CFM | TRM Version 5.0 | 2020-11-12 | 0 | 0.47 | 0 | 0 | 0 | 0 | 0 | 1 | 14 | Low-Income | 0 | 1 | 1
COM-ERV-SH-382-03 | Current |  | Commercial | Energy Recovery Ventilation | Low Use Group | New Construction/Natural Replacement | space heating | High Efficient 65% Energy Recovery Ventilation Low Use Group (Office, Warehouse, School) | Minimum 65% Sensible Heat Recovery Effectiveness and 63% Total Energy Recovery Effectiveness at 32°F | Minimum 55% Energy Recovery Effectiveness as per Ontario Building Code 2017 |  |  | CFM | TRM Version 5.0 | 2020-11-12 | 0 | 0.3 | 0 | 0 | 0 | 0 | 0 | 1 | 14 | Low-Income | 0 | 1 | 1
COM-ERV-SH-383-03 | Current |  | Commercial | Energy Recovery Ventilation | Multi-Residential, Health Care, Nursing Homes | New Construction/Natural Replacement | space heating | High Efficient 65% Energy Recovery Ventilation High Use Group (Multi-Residential, Health Care, Nursing Homes) | Minimum 65% Sensible Heat Recovery Effectiveness and 63% Total Energy Recovery Effectiveness at 32°F | Minimum 55% Energy Recovery Effectiveness as per Ontario Building Code 2017 |  |  | CFM | TRM Version 5.0 | 2020-11-12 | 0 | 0.85 | 0 | 0 | 0 | 0 | 0 | 1 | 14 | Low-Income | 0 | 1 | 1
COM-ERV-SH-384-03 | Current |  | Commercial | Energy Recovery Ventilation | Hotel | New Construction/Natural Replacement | space heating | High Efficient 65% Energy Recovery Ventilation Medium Use Group (Hotel, Restaurant, Retail) | Minimum 65% Sensible Heat Recovery Effectiveness and 63% Total Energy Recovery Effectiveness at 32°F | Minimum 55% Energy Recovery Effectiveness as per Ontario Building Code 2017 |  |  | CFM | TRM Version 5.0 | 2020-11-12 | 0 | 0.61 | 0 | 0 | 0 | 0 | 0 | 1 | 14 | Low-Income | 0 | 1 | 1
COM-ERV-SH-385-03 | Current |  | Commercial | Energy Recovery Ventilation | Restaurant | New Construction/Natural Replacement | space heating | High Efficient 65% Energy Recovery Ventilation Medium Use Group (Hotel, Restaurant, Retail) | Minimum 65% Sensible Heat Recovery Effectiveness and 63% Total Energy Recovery Effectiveness at 32°F | Minimum 55% Energy Recovery Effectiveness as per Ontario Building Code 2017 |  |  | CFM | TRM Version 5.0 | 2020-11-12 | 0 | 0.44 | 0 | 0 | 0 | 0 | 0 | 1 | 14 | Low-Income | 0 | 1 | 1
COM-ERV-SH-386-03 | Current |  | Commercial | Energy Recovery Ventilation | Retail | New Construction/Natural Replacement | space heating | High Efficient 65% Energy Recovery Ventilation Medium Use Group (Hotel, Restaurant, Retail) | Minimum 65% Sensible Heat Recovery Effectiveness and 63% Total Energy Recovery Effectiveness at 32°F | Minimum 55% Energy Recovery Effectiveness as per Ontario Building Code 2017 |  |  | CFM | TRM Version 5.0 | 2020-11-12 | 0 | 0.37 | 0 | 0 | 0 | 0 | 0 | 1 | 14 | Low-Income | 0 | 1 | 1
COM-ERV-SH-387-03 | Current |  | Commercial | Energy Recovery Ventilation | Office | New Construction/Natural Replacement | space heating | High Efficient 65% Energy Recovery Ventilation Low Use Group (Office, Warehouse, School) | Minimum 65% Sensible Heat Recovery Effectiveness and 63% Total Energy Recovery Effectiveness at 32°F | Minimum 55% Energy Recovery Effectiveness as per Ontario Building Code 2017 |  |  | CFM | TRM Version 5.0 | 2020-11-12 | 0 | 0.32 | 0 | 0 | 0 | 0 | 0 | 1 | 14 | Low-Income | 0 | 1 | 1
COM-ERV-SH-388-03 | Current |  | Commercial | Energy Recovery Ventilation | Warehouse | New Construction/Natural Replacement | space heating | High Efficient 65% Energy Recovery Ventilation Low Use Group (Office, Warehouse, School) | Minimum 65% Sensible Heat Recovery Effectiveness and 63% Total Energy Recovery Effectiveness at 32°F | Minimum 55% Energy Recovery Effectiveness as per Ontario Building Code 2017 |  |  | CFM | TRM Version 5.0 | 2020-11-12 | 0 | 0.31 | 0 | 0 | 0 | 0 | 0 | 1 | 14 | Low-Income | 0 | 1 | 1
COM-ERV-SH-389-03 | Current |  | Commercial | Energy Recovery Ventilation | School | New Construction/Natural Replacement | space heating | High Efficient 65% Energy Recovery Ventilation Low Use Group (Office, Warehouse, School) | Minimum 65% Sensible Heat Recovery Effectiveness and 63% Total Energy Recovery Effectiveness at 32°F | Minimum 55% Energy Recovery Effectiveness as per Ontario Building Code 2017 |  |  | CFM | TRM Version 5.0 | 2020-11-12 | 0 | 0.27 | 0 | 0 | 0 | 0 | 0 | 1 | 14 | Low-Income | 0 | 1 | 1
COM-ERV-SH-380-07 | Current |  | Commercial | Energy Recovery Ventilation | High Use Group | New Construction/Natural Replacement | space heating | High Efficient 75% Energy Recovery Ventilation High Use Group (Multi-Residential, Health Care, Nursing Homes) | Minimum 75% Sensible Heat Recovery Effectiveness and 73% Total Energy Recovery Effectiveness at 32°F | Minimum 55% Energy Recovery Effectiveness as per Ontario Building Code 2017 |  |  | CFM | TRM Version 5.0 | 2020-11-12 | 0 | 1.7 | 0 | 0 | 0 | 0 | 0 | 2 | 14 | Low-Income | 0 | 1 | 1
COM-ERV-SH-381-07 | Current |  | Commercial | Energy Recovery Ventilation | Medium Use Group | New Construction/Natural Replacement | space heating | High Efficient 75% Energy Recovery Ventilation Medium Use Group (Hotel, Restaurant, and Retail) | Minimum 75% Sensible Heat Recovery Effectiveness and 73% Total Energy Recovery Effectiveness at 32°F | Minimum 55% Energy Recovery Effectiveness as per Ontario Building Code 2017 |  |  | CFM | TRM Version 5.0 | 2020-11-12 | 0 | 0.95 | 0 | 0 | 0 | 0 | 0 | 2 | 14 | Low-Income | 0 | 1 | 1
COM-ERV-SH-382-07 | Current |  | Commercial | Energy Recovery Ventilation | Low Use Group | New Construction/Natural Replacement | space heating | High Efficient 75% Energy Recovery Ventilation Low Use Group (Office, Warehouse, School) | Minimum 75% Sensible Heat Recovery Effectiveness and 73% Total Energy Recovery Effectiveness at 32°F | Minimum 55% Energy Recovery Effectiveness as per Ontario Building Code 2017 |  |  | CFM | TRM Version 5.0 | 2020-11-12 | 0 | 0.61 | 0 | 0 | 0 | 0 | 0 | 2 | 14 | Low-Income | 0 | 1 | 1
COM-ERV-SH-383-07 | Current |  | Commercial | Energy Recovery Ventilation | Multi-Residential, Health Care, Nursing Homes | New Construction/Natural Replacement | space heating | High Efficient 75% Energy Recovery Ventilation High Use Group (Multi-Residential, Health Care, Nursing Homes) | Minimum 75% Sensible Heat Recovery Effectiveness and 73% Total Energy Recovery Effectiveness at 32°F | Minimum 55% Energy Recovery Effectiveness as per Ontario Building Code 2017 |  |  | CFM | TRM Version 5.0 | 2020-11-12 | 0 | 1.7 | 0 | 0 | 0 | 0 | 0 | 2 | 14 | Low-Income | 0 | 1 | 1
COM-ERV-SH-384-07 | Current |  | Commercial | Energy Recovery Ventilation | Hotel | New Construction/Natural Replacement | space heating | High Efficient 75% Energy Recovery Ventilation Medium Use Group (Hotel, Restaurant, and Retail) | Minimum 75% Sensible Heat Recovery Effectiveness and 73% Total Energy Recovery Effectiveness at 32°F | Minimum 55% Energy Recovery Effectiveness as per Ontario Building Code 2017 |  |  | CFM | TRM Version 5.0 | 2020-11-12 | 0 | 1.22 | 0 | 0 | 0 | 0 | 0 | 2 | 14 | Low-Income | 0 | 1 | 1
COM-ERV-SH-385-07 | Current |  | Commercial | Energy Recovery Ventilation | Restaurant | New Construction/Natural Replacement | space heating | High Efficient 75% Energy Recovery Ventilation Medium Use Group (Hotel, Restaurant, and Retail) | Minimum 75% Sensible Heat Recovery Effectiveness and 73% Total Energy Recovery Effectiveness at 32°F | Minimum 55% Energy Recovery Effectiveness as per Ontario Building Code 2017 |  |  | CFM | TRM Version 5.0 | 2020-11-12 | 0 | 0.88 | 0 | 0 | 0 | 0 | 0 | 2 | 14 | Low-Income | 0 | 1 | 1
COM-ERV-SH-386-07 | Current |  | Commercial | Energy Recovery Ventilation | Retail | New Construction/Natural Replacement | space heating | High Efficient 75% Energy Recovery Ventilation Medium Use Group (Hotel, Restaurant, and Retail) | Minimum 75% Sensible Heat Recovery Effectiveness and 73% Total Energy Recovery Effectiveness at 32°F | Minimum 55% Energy Recovery Effectiveness as per Ontario Building Code 2017 |  |  | CFM | TRM Version 5.0 | 2020-11-12 | 0 | 0.74 | 0 | 0 | 0 | 0 | 0 | 2 | 14 | Low-Income | 0 | 1 | 1
COM-ERV-SH-387-07 | Current |  | Commercial | Energy Recovery Ventilation | Office | New Construction/Natural Replacement | space heating | High Efficient 75% Energy Recovery Ventilation Low Use Group (Office, Warehouse, School) | Minimum 75% Sensible Heat Recovery Effectiveness and 73% Total Energy Recovery Effectiveness at 32°F | Minimum 55% Energy Recovery Effectiveness as per Ontario Building Code 2017 |  |  | CFM | TRM Version 5.0 | 2020-11-12 | 0 | 0.65 | 0 | 0 | 0 | 0 | 0 | 2 | 14 | Low-Income | 0 | 1 | 1
COM-ERV-SH-388-07 | Current |  | Commercial | Energy Recovery Ventilation | Warehouse | New Construction/Natural Replacement | space heating | High Efficient 75% Energy Recovery Ventilation Low Use Group (Office, Warehouse, School) | Minimum 75% Sensible Heat Recovery Effectiveness and 73% Total Energy Recovery Effectiveness at 32°F | Minimum 55% Energy Recovery Effectiveness as per Ontario Building Code 2017 |  |  | CFM | TRM Version 5.0 | 2020-11-12 | 0 | 0.62 | 0 | 0 | 0 | 0 | 0 | 2 | 14 | Low-Income | 0 | 1 | 1
COM-ERV-SH-389-07 | Current |  | Commercial | Energy Recovery Ventilation | School | New Construction/Natural Replacement | space heating | High Efficient 75% Energy Recovery Ventilation Low Use Group (Office, Warehouse, School) | Minimum 75% Sensible Heat Recovery Effectiveness and 73% Total Energy Recovery Effectiveness at 32°F | Minimum 55% Energy Recovery Effectiveness as per Ontario Building Code 2017 |  |  | CFM | TRM Version 5.0 | 2020-11-12 | 0 | 0.55 | 0 | 0 | 0 | 0 | 0 | 2 | 14 | Low-Income | 0 | 1 | 1
COM-ERV-SH-390-03 | Current |  | Commercial | Energy Recovery Ventilation | High Use Group | New Construction/Natural Replacement | space heating | High Efficient 85% Energy Recovery Ventilation High Use Group (Multi-Residential, Health Care, Nursing Homes) | Minimum 85% Sensible Heat Recovery Effectiveness and 83% Total Energy Recovery Effectiveness at 32°F | Minimum 55% Energy Recovery Effectiveness as per Ontario Building Code 2017 |  |  | CFM | TRM Version 5.0 | 2020-11-12 | 0 | 2.56 | 0 | 0 | 0 | 0 | 0 | 3 | 14 | Low-Income | 0 | 1 | 1
COM-ERV-SH-391-03 | Current |  | Commercial | Energy Recovery Ventilation | Medium Use Group | New Construction/Natural Replacement | space heating | High Efficient 85% Energy Recovery Ventilation Medium Use Group (Hotel, Restaurant, Retail) | Minimum 85% Sensible Heat Recovery Effectiveness and 83% Total Energy Recovery Effectiveness at 32°F | Minimum 55% Energy Recovery Effectiveness as per Ontario Building Code 2017 |  |  | CFM | TRM Version 5.0 | 2020-11-12 | 0 | 1.42 | 0 | 0 | 0 | 0 | 0 | 3 | 14 | Low-Income | 0 | 1 | 1
COM-ERV-SH-392-03 | Current |  | Commercial | Energy Recovery Ventilation | Low Use Group | New Construction/Natural Replacement | space heating | High Efficient 85% Energy Recovery Ventilation Low Use Group (Office, Warehouse, School) | Minimum 85% Sensible Heat Recovery Effectiveness and 83% Total Energy Recovery Effectiveness at 32°F | Minimum 55% Energy Recovery Effectiveness as per Ontario Building Code 2017 |  |  | CFM | TRM Version 5.0 | 2020-11-12 | 0 | 0.91 | 0 | 0 | 0 | 0 | 0 | 3 | 14 | Low-Income | 0 | 1 | 1
COM-ERV-SH-393-03 | Current |  | Commercial | Energy Recovery Ventilation | Multi-Residential, Health Care, Nursing Homes | New Construction/Natural Replacement | space heating | High Efficient 85% Energy Recovery Ventilation High Use Group (Multi-Residential, Health Care, Nursing Homes) | Minimum 85% Sensible Heat Recovery Effectiveness and 83% Total Energy Recovery Effectiveness at 32°F | Minimum 55% Energy Recovery Effectiveness as per Ontario Building Code 2017 |  |  | CFM | TRM Version 5.0 | 2020-11-12 | 0 | 2.56 | 0 | 0 | 0 | 0 | 0 | 3 | 14 | Low-Income | 0 | 1 | 1
COM-ERV-SH-394-03 | Current |  | Commercial | Energy Recovery Ventilation | Hotel | New Construction/Natural Replacement | space heating | High Efficient 85% Energy Recovery Ventilation Medium Use Group (Hotel, Restaurant, Retail) | Minimum 85% Sensible Heat Recovery Effectiveness and 83% Total Energy Recovery Effectiveness at 32°F | Minimum 55% Energy Recovery Effectiveness as per Ontario Building Code 2017 |  |  | CFM | TRM Version 5.0 | 2020-11-12 | 0 | 1.83 | 0 | 0 | 0 | 0 | 0 | 3 | 14 | Low-Income | 0 | 1 | 1
COM-ERV-SH-395-03 | Current |  | Commercial | Energy Recovery Ventilation | Restaurant | New Construction/Natural Replacement | space heating | High Efficient 85% Energy Recovery Ventilation Medium Use Group (Hotel, Restaurant, Retail) | Minimum 85% Sensible Heat Recovery Effectiveness and 83% Total Energy Recovery Effectiveness at 32°F | Minimum 55% Energy Recovery Effectiveness as per Ontario Building Code 2017 |  |  | CFM | TRM Version 5.0 | 2020-11-12 | 0 | 1.32 | 0 | 0 | 0 | 0 | 0 | 3 | 14 | Low-Income | 0 | 1 | 1
COM-ERV-SH-396-03 | Current |  | Commercial | Energy Recovery Ventilation | Retail | New Construction/Natural Replacement | space heating | High Efficient 85% Energy Recovery Ventilation Medium Use Group (Hotel, Restaurant, Retail) | Minimum 85% Sensible Heat Recovery Effectiveness and 83% Total Energy Recovery Effectiveness at 32°F | Minimum 55% Energy Recovery Effectiveness as per Ontario Building Code 2017 |  |  | CFM | TRM Version 5.0 | 2020-11-12 | 0 | 1.11 | 0 | 0 | 0 | 0 | 0 | 3 | 14 | Low-Income | 0 | 1 | 1
COM-ERV-SH-397-03 | Current |  | Commercial | Energy Recovery Ventilation | Office | New Construction/Natural Replacement | space heating | High Efficient 85% Energy Recovery Ventilation Low Use Group (Office, Warehouse, School) | Minimum 85% Sensible Heat Recovery Effectiveness and 83% Total Energy Recovery Effectiveness at 32°F | Minimum 55% Energy Recovery Effectiveness as per Ontario Building Code 2017 |  |  | CFM | TRM Version 5.0 | 2020-11-12 | 0 | 0.97 | 0 | 0 | 0 | 0 | 0 | 3 | 14 | Low-Income | 0 | 1 | 1
COM-ERV-SH-398-03 | Current |  | Commercial | Energy Recovery Ventilation | Warehouse | New Construction/Natural Replacement | space heating | High Efficient 85% Energy Recovery Ventilation Low Use Group (Office, Warehouse, School) | Minimum 85% Sensible Heat Recovery Effectiveness and 83% Total Energy Recovery Effectiveness at 32°F | Minimum 55% Energy Recovery Effectiveness as per Ontario Building Code 2017 |  |  | CFM | TRM Version 5.0 | 2020-11-12 | 0 | 0.93 | 0 | 0 | 0 | 0 | 0 | 3 | 14 | Low-Income | 0 | 1 | 1
COM-ERV-SH-399-03 | Current |  | Commercial | Energy Recovery Ventilation | School | New Construction/Natural Replacement | space heating | High Efficient 85% Energy Recovery Ventilation Low Use Group (Office, Warehouse, School) | Minimum 85% Sensible Heat Recovery Effectiveness and 83% Total Energy Recovery Effectiveness at 32°F | Minimum 55% Energy Recovery Effectiveness as per Ontario Building Code 2017 |  |  | CFM | TRM Version 5.0 | 2020-11-12 | 0 | 0.82 | 0 | 0 | 0 | 0 | 0 | 3 | 14 | Low-Income | 0 | 1 | 1
COM-AC-SH-481-04 | Current |  | Commercial | Air Curtain |  | New Construction/Retrofit | space heating | Air Curtains | Pedestrian Doors 2 x (3' x 7') | Exterior doorway without vestibule or air curtain |  | unit |  | TRM Version 5.0 | 2020-11-12 | 1690 | 0 | 212 | 0 | 0 | 0 | 3150 | 0 | 15 | Low-Income | 0 | 1 | 1
COM-AC-SH-487-04 | Current |  | Commercial | Air Curtain |  | New Construction/Retrofit | space heating | Air Curtains | Pedestrian Doors 2 x (3' x 7') | Exterior doorway with vestibule and no air curtain |  | unit |  | TRM Version 5.0 | 2020-11-12 | 1082 | 0 | 124 | 0 | 0 | 0 | 3150 | 0 | 15 | Low-Income | 0 | 1 | 1
COM-AC-SH-483-04 | Current |  | Commercial | Air Curtain |  | New Construction/Retrofit | space heating | Air Curtains | Pedestrian Doors 2 x (6' x 8') | Exterior doorway without vestibule or air curtain |  | unit |  | TRM Version 5.0 | 2020-11-12 | 3774 | 0 | 431 | 0 | 0 | 0 | 3350 | 0 | 15 | Low-Income | 0 | 1 | 1
COM-AC-SH-489-04 | Current |  | Commercial | Air Curtain |  | New Construction/Retrofit | space heating | Air Curtains | Pedestrian Doors 2 x (6' x 8') | Exterior doorway with vestibule and no air curtain |  | unit |  | TRM Version 5.0 | 2020-11-12 | 2416 | 0 | 232 | 0 | 0 | 0 | 3350 | 0 | 15 | Low-Income | 0 | 1 | 1
COM-AC-SH-482-04 | Current |  | Commercial | Air Curtain |  | New Construction/Retrofit | space heating | Air Curtains | Pedestrian Doors 2 x (6' x 7') | Exterior doorway without vestibule or air curtain |  | unit |  | TRM Version 5.0 | 2020-11-12 | 3380 | 0 | 367 | 0 | 0 | 0 | 3350 | 0 | 15 | Low-Income | 0 | 1 | 1
COM-AC-SH-488-04 | Current |  | Commercial | Air Curtain |  | New Construction/Retrofit | space heating | Air Curtains | Pedestrian Doors 2 x (6' x 7') | Exterior doorway with vestibule and no air curtain |  | unit |  | TRM Version 5.0 | 2020-11-12 | 2164 | 0 | 192 | 0 | 0 | 0 | 3350 | 0 | 15 | Low-Income | 0 | 1 | 1
COM-AC-SH-478-04 | Current |  | Commercial | Air Curtain |  | New Construction/Retrofit | space heating | Air Curtains | Pedestrian Doors 3' x 7' | Exterior doorway without vestibule or air curtain |  | unit |  | TRM Version 5.0 | 2020-11-12 | 845 | 0 | 106 | 0 | 0 | 0 | 1645 | 0 | 15 | Low-Income | 0 | 1 | 1
COM-AC-SH-484-04 | Current |  | Commercial | Air Curtain |  | New Construction/Retrofit | space heating | Air Curtains | Pedestrian Doors 3' x 7' | Exterior doorway with vestibule and no air curtain |  | unit |  | TRM Version 5.0 | 2020-11-12 | 541 | 0 | 62 | 0 | 0 | 0 | 1645 | 0 | 15 | Low-Income | 0 | 1 | 1
COM-AC-SH-479-04 | Current |  | Commercial | Air Curtain |  | New Construction/Retrofit | space heating | Air Curtains | Pedestrian Doors 6' x 7' | Exterior doorway without vestibule or air curtain |  | unit |  | TRM Version 5.0 | 2020-11-12 | 1690 | 0 | 184 | 0 | 0 | 0 | 1745 | 0 | 15 | Low-Income | 0 | 1 | 1
COM-AC-SH-485-04 | Current |  | Commercial | Air Curtain |  | New Construction/Retrofit | space heating | Air Curtains | Pedestrian Doors 6' x 7' | Exterior doorway with vestibule and no air curtain |  | unit |  | TRM Version 5.0 | 2020-11-12 | 1082 | 0 | 96 | 0 | 0 | 0 | 1745 | 0 | 15 | Low-Income | 0 | 1 | 1
COM-AC-SH-480-04 | Current |  | Commercial | Air Curtain |  | New Construction/Retrofit | space heating | Air Curtains | Pedestrian Doors 6' x 8' | Exterior doorway without vestibule or air curtain |  | unit |  | TRM Version 5.0 | 2020-11-12 | 1887 | 0 | 215 | 0 | 0 | 0 | 1745 | 0 | 15 | Low-Income | 0 | 1 | 1
COM-AC-SH-486-04 | Current |  | Commercial | Air Curtain |  | New Construction/Retrofit | space heating | Air Curtains | Pedestrian Doors 6' x 8' | Exterior doorway with vestibule and no air curtain |  | unit |  | TRM Version 5.0 | 2020-11-12 | 1208 | 0 | 116 | 0 | 0 | 0 | 1745 | 0 | 15 | Low-Income | 0 | 1 | 1
RES-PT-SH-573-02 | Current |  | Residential | Programmable Thermostat |  | Retrofit | space heating | Programmable Thermostat | Programmable thermostat with at least two programming modes (weekday and weekend) | Non Programmable Thermostat |  | unit |  | TRM Version 5.0 | 2020-11-12 | 46 | 0 | 0 | 0 | 0 | 0 | 97 | 0 | 15 | Low-Income | 0 | 1 | 1
RES-PW-WH-566-02 | Current |  | Residential | Pipe Wrap |  | Retrofit | water heating | Pipe Wrap | R 4.35 | No pipe wrap | R-0.435 | ft |  | TRM Version 7.0 | 2022-11-30 | 3.72 | 0 | 0 | 0 | 0 | 0 | 0.39 | 0 | 15 | Low-Income | 0 | 0.939 | 1
COM-DCV-SH-527-02 | Current |  | Commercial | Demand Control Ventilation | Office | New Construction/Natural Replacement | space heating | Demand Control Ventilation with CO2 Sensor (Office) | Scheduled Ventilation (Occupied Periods) | New single-zone, constant volume ventilation system | Provides min outdoor air requirements as specificed in Table 6.2.2.1 of ASHRAE Standard 62.1-2013 [1] |  | sq ft | TRM Version 5.0 | 2020-11-12 | 0 | 0.112 | 0 | 0 | 0 | 0 | 750 | 0 | 15 | Low-Income | 0 | 1 | 1
COM-DCV-SH-528-02 | Current |  | Commercial | Demand Control Ventilation | Office | Retrofit | space heating | Demand Control Ventilation with CO2 Sensor (Office) | Scheduled Ventilation (Occupied Periods) | New single-zone, constant volume ventilation system | Provides min outdoor air requirements as specificed in Table 6.2.2.1 of ASHRAE Standard 62.1-2013 [1] |  | sq ft | TRM Version 5.0 | 2020-11-12 | 0 | 0.112 | 0 | 0 | 0 | 0 | 1050 | 0 | 15 | Low-Income | 0 | 1 | 1
COM-DCV-SH-529-02 | Current |  | Commercial | Demand Control Ventilation | Retail | New Construction/Natural Replacement | space heating | Demand Control Ventilation with CO2 Sensor (Retail) | Scheduled Ventilation (Occupied Periods) | New single-zone, constant volume ventilation system | Provides min outdoor air requirements as specificed in Table 6.2.2.1 of ASHRAE Standard 62.1-2013 [1] |  | sq ft | TRM Version 5.0 | 2020-11-12 | 0 | 0.392 | 0 | 0 | 0 | 0 | 750 | 0 | 15 | Low-Income | 0 | 1 | 1
COM-DCV-SH-530-02 | Current |  | Commercial | Demand Control Ventilation | Retail | Retrofit | space heating | Demand Control Ventilation with CO2 Sensor (Retail) | Scheduled Ventilation (Occupied Periods) | New single-zone, constant volume ventilation system | Provides min outdoor air requirements as specificed in Table 6.2.2.1 of ASHRAE Standard 62.1-2013 [1] |  | sq ft | TRM Version 5.0 | 2020-11-12 | 0 | 0.392 | 0 | 0 | 0 | 0 | 1050 | 0 | 15 | Low-Income | 0 | 1 | 1
COM-DCV-SH-531-02 | Current |  | Commercial | Demand Control Ventilation | Cinemas and Performing Arts | Retrofit | space heating | Demand Control Ventilation with CO2 Sensor (Cinemas and Performing Arts) | Scheduled Ventilation (Occupied Periods) | Existing single-zone, constant volume ventilation system | Provides min outdoor air requirements as specificed in Table 6.2.2.1 of ASHRAE Standard 62.1-2013 [1] |  | sq ft | TRM Version 5.0 | 2020-11-12 | 0 | 1.69 | 0 | 0 | 0 | 0 | 1050 | 0 | 15 | Low-Income | 0 | 1 | 1
COM-DCV-SH-532-02 | Current |  | Commercial | Demand Control Ventilation | Cinemas and Performing Arts | New Construction/Natural Replacement | space heating | Demand Control Ventilation with CO2 Sensor (Cinemas and Performing Arts) | Scheduled Ventilation (Occupied Periods) | Existing single-zone, constant volume ventilation system | Provides min outdoor air requirements as specificed in Table 6.2.2.1 of ASHRAE Standard 62.1-2013 [1] |  | sq ft | TRM Version 5.0 | 2020-11-12 | 0 | 1.69 | 0 | 0 | 0 | 0 | 750 | 0 | 15 | Low-Income | 0 | 1 | 1
COM-DCV-SH-533-02 | Current |  | Commercial | Demand Control Ventilation | Community Center Meeting Space | Retrofit | space heating | Demand Control Ventilation with CO2 Sensor (Community Center Meeting Space) | Scheduled Ventilation (Occupied Periods) | Existing single-zone, constant volume ventilation system | Provides min outdoor air requirements as specificed in Table 6.2.2.1 of ASHRAE Standard 62.1-2013 [1] |  | sq ft | TRM Version 5.0 | 2020-11-12 | 0 | 0.441 | 0 | 0 | 0 | 0 | 1050 | 0 | 15 | Low-Income | 0 | 1 | 1
COM-DCV-SH-534-02 | Current |  | Commercial | Demand Control Ventilation | Community Center Meeting Space | New Construction/Natural Replacement | space heating | Demand Control Ventilation with CO2 Sensor (Community Center Meeting Space) | Scheduled Ventilation (Occupied Periods) | Existing single-zone, constant volume ventilation system | Provides min outdoor air requirements as specificed in Table 6.2.2.1 of ASHRAE Standard 62.1-2013 [1] |  | sq ft | TRM Version 5.0 | 2020-11-12 | 0 | 0.441 | 0 | 0 | 0 | 0 | 750 | 0 | 15 | Low-Income | 0 | 1 | 1
COM-DCV-SH-535-02 | Current |  | Commercial | Demand Control Ventilation | Exercise Center/Sports Arena | Retrofit | space heating | Demand Control Ventilation with CO2 Sensor (Exercise Center/Sports Arena) | Scheduled Ventilation (Occupied Periods) | Existing single-zone, constant volume ventilation system | Provides min outdoor air requirements as specificed in Table 6.2.2.1 of ASHRAE Standard 62.1-2013 [1] |  | sq ft | TRM Version 5.0 | 2020-11-12 | 0 | 0.435 | 0 | 0 | 0 | 0 | 1050 | 0 | 15 | Low-Income | 0 | 1 | 1
COM-DCV-SH-536-02 | Current |  | Commercial | Demand Control Ventilation | Exercise Center/Sports Arena | New Construction/Natural Replacement | space heating | Demand Control Ventilation with CO2 Sensor (Exercise Center/Sports Arena) | Scheduled Ventilation (Occupied Periods) | Existing single-zone, constant volume ventilation system | Provides min outdoor air requirements as specificed in Table 6.2.2.1 of ASHRAE Standard 62.1-2013 [1] |  | sq ft | TRM Version 5.0 | 2020-11-12 | 0 | 0.435 | 0 | 0 | 0 | 0 | 750 | 0 | 15 | Low-Income | 0 | 1 | 1
COM-DCV-SH-537-02 | Current |  | Commercial | Demand Control Ventilation | Hotel Conference Rooms | Retrofit | space heating | Demand Control Ventilation with CO2 Sensor (Hotel Conference Rooms) | Scheduled Ventilation (Occupied Periods) | Existing single-zone, constant volume ventilation system | Provides min outdoor air requirements as specificed in Table 6.2.2.1 of ASHRAE Standard 62.1-2013 [1] |  | sq ft | TRM Version 5.0 | 2020-11-12 | 0 | 1.043 | 0 | 0 | 0 | 0 | 1050 | 0 | 15 | Low-Income | 0 | 1 | 1
COM-DCV-SH-538-02 | Current |  | Commercial | Demand Control Ventilation | Hotel Conference Rooms | New Construction/Natural Replacement | space heating | Demand Control Ventilation with CO2 Sensor (Hotel Conference Rooms) | Scheduled Ventilation (Occupied Periods) | Existing single-zone, constant volume ventilation system | Provides min outdoor air requirements as specificed in Table 6.2.2.1 of ASHRAE Standard 62.1-2013 [1] |  | sq ft | TRM Version 5.0 | 2020-11-12 | 0 | 1.043 | 0 | 0 | 0 | 0 | 750 | 0 | 15 | Low-Income | 0 | 1 | 1
COM-DCV-SH-539-02 | Current |  | Commercial | Demand Control Ventilation | Post-Secondary School Classroom | Retrofit | space heating | Demand Control Ventilation with CO2 Sensor (Post-Secondary School Classroom) | Scheduled Ventilation (Occupied Periods) | Existing single-zone, constant volume ventilation system | Provides min outdoor air requirements as specificed in Table 6.2.2.1 of ASHRAE Standard 62.1-2013 [1] |  | sq ft | TRM Version 5.0 | 2020-11-12 | 0 | 0.601 | 0 | 0 | 0 | 0 | 1050 | 0 | 15 | Low-Income | 0 | 1 | 1
COM-DCV-SH-540-02 | Current |  | Commercial | Demand Control Ventilation | Post-Secondary School Classroom | New Construction/Natural Replacement | space heating | Demand Control Ventilation with CO2 Sensor (Post-Secondary School Classroom) | Scheduled Ventilation (Occupied Periods) | Existing single-zone, constant volume ventilation system | Provides min outdoor air requirements as specificed in Table 6.2.2.1 of ASHRAE Standard 62.1-2013 [1] |  | sq ft | TRM Version 5.0 | 2020-11-12 | 0 | 0.601 | 0 | 0 | 0 | 0 | 750 | 0 | 15 | Low-Income | 0 | 1 | 1
COM-DCV-SH-541-02 | Current |  | Commercial | Demand Control Ventilation | Primary/Secondary School Gymnasium | Retrofit | space heating | Demand Control Ventilation with CO2 Sensor (Primary/Secondary School Gymnasium) | Scheduled Ventilation (Occupied Periods) | Existing single-zone, constant volume ventilation system | Provides min outdoor air requirements as specificed in Table 6.2.2.1 of ASHRAE Standard 62.1-2013 [1] |  | sq ft | TRM Version 5.0 | 2020-11-12 | 0 | 1.484 | 0 | 0 | 0 | 0 | 1050 | 0 | 15 | Low-Income | 0 | 1 | 1
COM-DCV-SH-542-02 | Current |  | Commercial | Demand Control Ventilation | Primary/Secondary School Gymnasium | New Construction/Natural Replacement | space heating | Demand Control Ventilation with CO2 Sensor (Primary/Secondary School Gymnasium) | Scheduled Ventilation (Occupied Periods) | Existing single-zone, constant volume ventilation system | Provides min outdoor air requirements as specificed in Table 6.2.2.1 of ASHRAE Standard 62.1-2013 [1] |  | sq ft | TRM Version 5.0 | 2020-11-12 | 0 | 1.484 | 0 | 0 | 0 | 0 | 750 | 0 | 15 | Low-Income | 0 | 1 | 1
COM-DCV-SH-543-02 | Current |  | Commercial | Demand Control Ventilation | Senior/Nursing/Long-Term Care Facility (Common Areas) | Retrofit | space heating | Demand Control Ventilation with CO2 Sensor (Senior/Nursing/Long-Term Care Facility (Common Areas)) | Scheduled Ventilation (Occupied Periods) | Existing single-zone, constant volume ventilation system | Provides min outdoor air requirements as specificed in Table 6.2.2.1 of ASHRAE Standard 62.1-2013 [1] |  | sq ft | TRM Version 5.0 | 2020-11-12 | 0 | 0.636 | 0 | 0 | 0 | 0 | 1050 | 0 | 15 | Low-Income | 0 | 1 | 1
COM-DCV-SH-544-02 | Current |  | Commercial | Demand Control Ventilation | Senior/Nursing/Long-Term Care Facility (Common Areas) | New Construction/Natural Replacement | space heating | Demand Control Ventilation with CO2 Sensor (Senior/Nursing/Long-Term Care Facility (Common Areas)) | Scheduled Ventilation (Occupied Periods) | Existing single-zone, constant volume ventilation system | Provides min outdoor air requirements as specificed in Table 6.2.2.1 of ASHRAE Standard 62.1-2013 [1] |  | sq ft | TRM Version 5.0 | 2020-11-12 | 0 | 0.636 | 0 | 0 | 0 | 0 | 750 | 0 | 15 | Low-Income | 0 | 1 | 1
COM-AC-SH-471-04 | Current |  | Commercial | Air Curtain |  | New Construction/Retrofit | space heating | Air Curtains | Shipping and Receiving Doors "Dock-In" 10' x 10' | Exterior doorway without air curtain |  | unit |  | TRM Version 5.0 | 2020-11-12 | 5517 | 0 | -2838 | 0 | 0 | 0 | 6345 | 0 | 15 | Low-Income | 0 | 1 | 1
COM-AC-SH-470-04 | Current |  | Commercial | Air Curtain |  | New Construction/Retrofit | space heating | Air Curtains | Shipping and Receiving Doors "Dock-In" 8' x 10' | Exterior doorway without air curtain |  | unit |  | TRM Version 5.0 | 2020-11-12 | 4941 | 0 | -1576 | 0 | 0 | 0 | 5663 | 0 | 15 | Low-Income | 0 | 1 | 1
COM-AC-SH-468-04 | Current |  | Commercial | Air Curtain |  | New Construction/Retrofit | space heating | Air Curtains | Shipping and Receiving Doors "Dock-In" 8' x 8' | Exterior doorway without air curtain |  | unit |  | TRM Version 5.0 | 2020-11-12 | 4713 | 0 | -1688 | 0 | 0 | 0 | 5663 | 0 | 15 | Low-Income | 0 | 1 | 1
COM-AC-SH-469-04 | Current |  | Commercial | Air Curtain |  | New Construction/Retrofit | space heating | Air Curtains | Shipping and Receiving Doors "Dock-In" 8' x 9' | Exterior doorway without air curtain |  | unit |  | TRM Version 5.0 | 2020-11-12 | 4845 | 0 | -1630 | 0 | 0 | 0 | 5663 | 0 | 15 | Low-Income | 0 | 1 | 1
COM-AC-SH-472-04 | Current |  | Commercial | Air Curtain |  | New Construction/Retrofit | space heating | Air Curtains | Shipping and Receiving Doors "Drive-In" 10' x 10' | Exterior doorway without air curtain |  | unit |  | TRM Version 5.0 | 2020-11-12 | 4844 | 0 | 540 | 0 | 0 | 0 | 6345 | 0 | 15 | Low-Income | 0 | 1 | 1
COM-AC-SH-473-04 | Current |  | Commercial | Air Curtain |  | New Construction/Retrofit | space heating | Air Curtains | Shipping and Receiving Doors "Drive-In" 12' x 12' | Exterior doorway without air curtain |  | unit |  | TRM Version 5.0 | 2020-11-12 | 5753 | 0 | 843 | 0 | 0 | 0 | 11158 | 0 | 15 | Low-Income | 0 | 1 | 1
COM-AC-SH-474-04 | Current |  | Commercial | Air Curtain |  | New Construction/Retrofit | space heating | Air Curtains | Shipping and Receiving Doors "Drive-In" 14' x 14' | Exterior doorway without air curtain |  | unit |  | TRM Version 5.0 | 2020-11-12 | 6504 | 0 | 772 | 0 | 0 | 0 | 14159 | 0 | 15 | Low-Income | 0 | 1 | 1
COM-AC-SH-475-04 | Current |  | Commercial | Air Curtain |  | New Construction/Retrofit | space heating | Air Curtains | Shipping and Receiving Doors "Drive-In" 16' x 16' | Exterior doorway without air curtain |  | unit |  | TRM Version 5.0 | 2020-11-12 | 7081 | 0 | 987 | 0 | 0 | 0 | 22226 | 0 | 15 | Low-Income | 0 | 1 | 1
COM-AC-SH-476-04 | Current |  | Commercial | Air Curtain |  | New Construction/Retrofit | space heating | Air Curtains | Shipping and Receiving Doors "Drive-In" 18' x 18' | Exterior doorway without air curtain |  | unit |  | TRM Version 5.0 | 2020-11-12 | 7459 | 0 | 488 | 0 | 0 | 0 | 24699 | 0 | 15 | Low-Income | 0 | 1 | 1
COM-AC-SH-477-04 | Current |  | Commercial | Air Curtain |  | New Construction/Retrofit | space heating | Air Curtains | Shipping and Receiving Doors "Drive-In" 20' x 20' | Exterior doorway without air curtain |  | unit |  | TRM Version 5.0 | 2020-11-12 | 7605 | 0 | 596 | 0 | 0 | 0 | 45256 | 0 | 15 | Low-Income | 0 | 1 | 1
COM-ERV-SH-300-03 | Current |  | Commercial | Energy Recovery Ventilation | High Use Group | New Construction/Retrofit | space heating | High Efficient 55% Energy Recovery Ventilation High Use Group (Multi-Residential, Health Care, Nursing Homes) | Ventilation with ERV Integrated | Ventilation without ERV |  |  | CFM | TRM Version 5.0 | 2020-11-12 | 0 | 4.52 | 0 | 0 | 0 | 0 | 0 | 4.86 | 14 | Low-Income | 0 | 1 | 1
COM-ERV-SH-302-03 | Current |  | Commercial | Energy Recovery Ventilation | Medium Use Group | New Construction/Retrofit | space heating | High Efficient 55% Energy Recovery Ventilation Medium Use Group (Hotel, Restaurant, Retail) | Ventilation with ERV Integrated | Ventilation without ERV |  |  | CFM | TRM Version 5.0 | 2020-11-12 | 0 | 2.51 | 0 | 0 | 0 | 0 | 0 | 4.86 | 14 | Low-Income | 0 | 1 | 1
COM-ERV-SH-304-03 | Current |  | Commercial | Energy Recovery Ventilation | Low Use Group | New Construction/Retrofit | space heating | High Efficient 55% Energy Recovery Ventilation Low Use Group (Office, Warehouse, School) | Ventilation with ERV Integrated | Ventilation without ERV |  |  | CFM | TRM Version 5.0 | 2020-11-12 | 0 | 1.6 | 0 | 0 | 0 | 0 | 0 | 4.86 | 14 | Low-Income | 0 | 1 | 1
COM-ERV-SH-306-03 | Current |  | Commercial | Energy Recovery Ventilation | Multi-Residential, Health Care, Nursing Homes | New Construction/Retrofit | space heating | High Efficient 55% Energy Recovery Ventilation High Use Group (Multi-Residential, Health Care, Nursing Homes) | Ventilation with ERV Integrated | Ventilation without ERV |  |  | CFM | TRM Version 5.0 | 2020-11-12 | 0 | 4.52 | 0 | 0 | 0 | 0 | 0 | 4.86 | 14 | Low-Income | 0 | 1 | 1
COM-ERV-SH-308-03 | Current |  | Commercial | Energy Recovery Ventilation | Hotel | New Construction/Retrofit | space heating | High Efficient 55% Energy Recovery Ventilation Medium Use Group (Hotel, Restaurant, Retail) | Ventilation with ERV Integrated | Ventilation without ERV |  |  | CFM | TRM Version 5.0 | 2020-11-12 | 0 | 3.23 | 0 | 0 | 0 | 0 | 0 | 4.86 | 14 | Low-Income | 0 | 1 | 1
COM-ERV-SH-310-03 | Current |  | Commercial | Energy Recovery Ventilation | Restaurant | New Construction/Retrofit | space heating | High Efficient 55% Energy Recovery Ventilation Medium Use Group (Hotel, Restaurant, Retail) | Ventilation with ERV Integrated | Ventilation without ERV |  |  | CFM | TRM Version 5.0 | 2020-11-12 | 0 | 2.34 | 0 | 0 | 0 | 0 | 0 | 4.86 | 14 | Low-Income | 0 | 1 | 1
COM-ERV-SH-312-03 | Current |  | Commercial | Energy Recovery Ventilation | Retail | New Construction/Retrofit | space heating | High Efficient 55% Energy Recovery Ventilation Medium Use Group (Hotel, Restaurant, Retail) | Ventilation with ERV Integrated | Ventilation without ERV |  |  | CFM | TRM Version 5.0 | 2020-11-12 | 0 | 1.96 | 0 | 0 | 0 | 0 | 0 | 4.86 | 14 | Low-Income | 0 | 1 | 1
COM-ERV-SH-314-03 | Current |  | Commercial | Energy Recovery Ventilation | Office | New Construction/Retrofit | space heating | High Efficient 55% Energy Recovery Ventilation Low Use Group (Office, Warehouse, School) | Ventilation with ERV Integrated | Ventilation without ERV |  |  | CFM | TRM Version 5.0 | 2020-11-12 | 0 | 1.72 | 0 | 0 | 0 | 0 | 0 | 4.86 | 14 | Low-Income | 0 | 1 | 1
COM-ERV-SH-316-03 | Current |  | Commercial | Energy Recovery Ventilation | Warehouse | New Construction/Retrofit | space heating | High Efficient 55% Energy Recovery Ventilation Low Use Group (Office, Warehouse, School) | Ventilation with ERV Integrated | Ventilation without ERV |  |  | CFM | TRM Version 5.0 | 2020-11-12 | 0 | 1.64 | 0 | 0 | 0 | 0 | 0 | 4.86 | 14 | Low-Income | 0 | 1 | 1
COM-ERV-SH-318-03 | Current |  | Commercial | Energy Recovery Ventilation | School | New Construction/Retrofit | space heating | High Efficient 55% Energy Recovery Ventilation Low Use Group (Office, Warehouse, School) | Ventilation with ERV Integrated | Ventilation without ERV |  |  | CFM | TRM Version 5.0 | 2020-11-12 | 0 | 1.45 | 0 | 0 | 0 | 0 | 0 | 4.86 | 14 | Low-Income | 0 | 1 | 1
COM-ERV-SH-320-03 | Current |  | Commercial | Energy Recovery Ventilation | High Use Group | New Construction/Retrofit | space heating | High Efficient 65% Energy Recovery Ventilation High Use Group (Multi-Residential, Health Care, Nursing Homes) | Ventilation with ERV Integrated | Ventilation without ERV |  |  | CFM | TRM Version 5.0 | 2020-11-12 | 0 | 5.37 | 0 | 0 | 0 | 0 | 0 | 5.86 | 14 | Low-Income | 0 | 1 | 1
COM-ERV-SH-322-03 | Current |  | Commercial | Energy Recovery Ventilation | Medium Use Group | New Construction/Retrofit | space heating | High Efficient 65% Energy Recovery Ventilation Medium Use Group (Hotel, Restaurant, Retail) | Ventilation with ERV Integrated | Ventilation without ERV |  |  | CFM | TRM Version 5.0 | 2020-11-12 | 0 | 2.98 | 0 | 0 | 0 | 0 | 0 | 5.86 | 14 | Low-Income | 0 | 1 | 1
COM-ERV-SH-324-03 | Current |  | Commercial | Energy Recovery Ventilation | Low Use Group | New Construction/Retrofit | space heating | High Efficient 65% Energy Recovery Ventilation Low Use Group (Office, Warehouse, School) | Ventilation with ERV Integrated | Ventilation without ERV |  |  | CFM | TRM Version 5.0 | 2020-11-12 | 0 | 1.91 | 0 | 0 | 0 | 0 | 0 | 5.86 | 14 | Low-Income | 0 | 1 | 1
COM-ERV-SH-326-03 | Current |  | Commercial | Energy Recovery Ventilation | Multi-Residential, Health Care, Nursing Homes | New Construction/Retrofit | space heating | High Efficient 65% Energy Recovery Ventilation High Use Group (Multi-Residential, Health Care, Nursing Homes) | Ventilation with ERV Integrated | Ventilation without ERV |  |  | CFM | TRM Version 5.0 | 2020-11-12 | 0 | 5.37 | 0 | 0 | 0 | 0 | 0 | 5.86 | 14 | Low-Income | 0 | 1 | 1
COM-ERV-SH-328-03 | Current |  | Commercial | Energy Recovery Ventilation | Hotel | New Construction/Retrofit | space heating | High Efficient 65% Energy Recovery Ventilation Medium Use Group (Hotel, Restaurant, Retail) | Ventilation with ERV Integrated | Ventilation without ERV |  |  | CFM | TRM Version 5.0 | 2020-11-12 | 0 | 3.84 | 0 | 0 | 0 | 0 | 0 | 5.86 | 14 | Low-Income | 0 | 1 | 1
COM-ERV-SH-330-03 | Current |  | Commercial | Energy Recovery Ventilation | Restaurant | New Construction/Retrofit | space heating | High Efficient 65% Energy Recovery Ventilation Medium Use Group (Hotel, Restaurant, Retail) | Ventilation with ERV Integrated | Ventilation without ERV |  |  | CFM | TRM Version 5.0 | 2020-11-12 | 0 | 2.78 | 0 | 0 | 0 | 0 | 0 | 5.86 | 14 | Low-Income | 0 | 1 | 1
COM-ERV-SH-332-03 | Current |  | Commercial | Energy Recovery Ventilation | Retail | New Construction/Retrofit | space heating | High Efficient 65% Energy Recovery Ventilation Medium Use Group (Hotel, Restaurant, Retail) | Ventilation with ERV Integrated | Ventilation without ERV |  |  | CFM | TRM Version 5.0 | 2020-11-12 | 0 | 2.33 | 0 | 0 | 0 | 0 | 0 | 5.86 | 14 | Low-Income | 0 | 1 | 1
COM-ERV-SH-334-03 | Current |  | Commercial | Energy Recovery Ventilation | Office | New Construction/Retrofit | space heating | High Efficient 65% Energy Recovery Ventilation Low Use Group (Office, Warehouse, School) | Ventilation with ERV Integrated | Ventilation without ERV |  |  | CFM | TRM Version 5.0 | 2020-11-12 | 0 | 2.05 | 0 | 0 | 0 | 0 | 0 | 5.86 | 14 | Low-Income | 0 | 1 | 1
COM-ERV-SH-336-03 | Current |  | Commercial | Energy Recovery Ventilation | Warehouse | New Construction/Retrofit | space heating | High Efficient 65% Energy Recovery Ventilation Low Use Group (Office, Warehouse, School) | Ventilation with ERV Integrated | Ventilation without ERV |  |  | CFM | TRM Version 5.0 | 2020-11-12 | 0 | 1.95 | 0 | 0 | 0 | 0 | 0 | 5.86 | 14 | Low-Income | 0 | 1 | 1
COM-ERV-SH-338-03 | Current |  | Commercial | Energy Recovery Ventilation | School | New Construction/Retrofit | space heating | High Efficient 65% Energy Recovery Ventilation Low Use Group (Office, Warehouse, School) | Ventilation with ERV Integrated | Ventilation without ERV |  |  | CFM | TRM Version 5.0 | 2020-11-12 | 0 | 1.73 | 0 | 0 | 0 | 0 | 0 | 5.86 | 14 | Low-Income | 0 | 1 | 1
COM-ERV-SH-340-03 | Current |  | Commercial | Energy Recovery Ventilation | High Use Group | New Construction/Retrofit | space heating | High Efficient 75% Energy Recovery Ventilation High Use Group (Multi-Residential, Health Care, Nursing Homes) | Ventilation with ERV Integrated | Ventilation without ERV |  |  | CFM | TRM Version 5.0 | 2020-11-12 | 0 | 6.22 | 0 | 0 | 0 | 0 | 0 | 6.86 | 14 | Low-Income | 0 | 1 | 1
COM-ERV-SH-342-03 | Current |  | Commercial | Energy Recovery Ventilation | Medium Use Group | New Construction/Retrofit | space heating | High Efficient 75% Energy Recovery Ventilation Medium Use Group (Hotel, Restaurant, and Retail) | Ventilation with ERV Integrated | Ventilation without ERV |  |  | CFM | TRM Version 5.0 | 2020-11-12 | 0 | 3.45 | 0 | 0 | 0 | 0 | 0 | 6.86 | 14 | Low-Income | 0 | 1 | 1
COM-ERV-SH-344-03 | Current |  | Commercial | Energy Recovery Ventilation | Low Use Group | New Construction/Retrofit | space heating | High Efficient 75% Energy Recovery Ventilation Low Use Group (Office, Warehouse, School) | Ventilation with ERV Integrated | Ventilation without ERV |  |  | CFM | TRM Version 5.0 | 2020-11-12 | 0 | 2.21 | 0 | 0 | 0 | 0 | 0 | 6.86 | 14 | Low-Income | 0 | 1 | 1
COM-ERV-SH-346-03 | Current |  | Commercial | Energy Recovery Ventilation | Multi-Residential, Health Care, Nursing Homes | New Construction/Retrofit | space heating | High Efficient 75% Energy Recovery Ventilation High Use Group (Multi-Residential, Health Care, Nursing Homes) | Ventilation with ERV Integrated | Ventilation without ERV |  |  | CFM | TRM Version 5.0 | 2020-11-12 | 0 | 6.22 | 0 | 0 | 0 | 0 | 0 | 6.86 | 14 | Low-Income | 0 | 1 | 1
COM-ERV-SH-348-03 | Current |  | Commercial | Energy Recovery Ventilation | Hotel | New Construction/Retrofit | space heating | High Efficient 75% Energy Recovery Ventilation Medium Use Group (Hotel, Restaurant, and Retail) | Ventilation with ERV Integrated | Ventilation without ERV |  |  | CFM | TRM Version 5.0 | 2020-11-12 | 0 | 4.44 | 0 | 0 | 0 | 0 | 0 | 6.86 | 14 | Low-Income | 0 | 1 | 1
COM-ERV-SH-350-03 | Current |  | Commercial | Energy Recovery Ventilation | Restaurant | New Construction/Retrofit | space heating | High Efficient 75% Energy Recovery Ventilation Medium Use Group (Hotel, Restaurant, and Retail) | Ventilation with ERV Integrated | Ventilation without ERV |  |  | CFM | TRM Version 5.0 | 2020-11-12 | 0 | 3.22 | 0 | 0 | 0 | 0 | 0 | 6.86 | 14 | Low-Income | 0 | 1 | 1
COM-ERV-SH-352-03 | Current |  | Commercial | Energy Recovery Ventilation | Retail | New Construction/Retrofit | space heating | High Efficient 75% Energy Recovery Ventilation Medium Use Group (Hotel, Restaurant, and Retail) | Ventilation with ERV Integrated | Ventilation without ERV |  |  | CFM | TRM Version 5.0 | 2020-11-12 | 0 | 2.7 | 0 | 0 | 0 | 0 | 0 | 6.86 | 14 | Low-Income | 0 | 1 | 1
COM-ERV-SH-354-03 | Current |  | Commercial | Energy Recovery Ventilation | Office | New Construction/Retrofit | space heating | High Efficient 75% Energy Recovery Ventilation Low Use Group (Office, Warehouse, School) | Ventilation with ERV Integrated | Ventilation without ERV |  |  | CFM | TRM Version 5.0 | 2020-11-12 | 0 | 2.37 | 0 | 0 | 0 | 0 | 0 | 6.86 | 14 | Low-Income | 0 | 1 | 1
COM-ERV-SH-356-03 | Current |  | Commercial | Energy Recovery Ventilation | Warehouse | New Construction/Retrofit | space heating | High Efficient 75% Energy Recovery Ventilation Low Use Group (Office, Warehouse, School) | Ventilation with ERV Integrated | Ventilation without ERV |  |  | CFM | TRM Version 5.0 | 2020-11-12 | 0 | 2.26 | 0 | 0 | 0 | 0 | 0 | 6.86 | 14 | Low-Income | 0 | 1 | 1
COM-ERV-SH-358-03 | Current |  | Commercial | Energy Recovery Ventilation | School | New Construction/Retrofit | space heating | High Efficient 75% Energy Recovery Ventilation Low Use Group (Office, Warehouse, School) | Ventilation with ERV Integrated | Ventilation without ERV |  |  | CFM | TRM Version 5.0 | 2020-11-12 | 0 | 2 | 0 | 0 | 0 | 0 | 0 | 6.86 | 14 | Low-Income | 0 | 1 | 1
COM-ERV-SH-360-03 | Current |  | Commercial | Energy Recovery Ventilation | High Use Group | New Construction/Retrofit | space heating | High Efficient 85% Energy Recovery Ventilation High Use Group (Multi-Residential, Health Care, Nursing Homes) | Ventilation with ERV Integrated | Ventilation without ERV |  |  | CFM | TRM Version 5.0 | 2020-11-12 | 0 | 7.07 | 0 | 0 | 0 | 0 | 0 | 7.86 | 14 | Low-Income | 0 | 1 | 1
COM-ERV-SH-362-03 | Current |  | Commercial | Energy Recovery Ventilation | Medium Use Group | New Construction/Retrofit | space heating | High Efficient 85% Energy Recovery Ventilation Medium Use Group (Hotel, Restaurant, Retail) | Ventilation with ERV Integrated | Ventilation without ERV |  |  | CFM | TRM Version 5.0 | 2020-11-12 | 0 | 3.93 | 0 | 0 | 0 | 0 | 0 | 7.86 | 14 | Low-Income | 0 | 1 | 1
COM-ERV-SH-364-03 | Current |  | Commercial | Energy Recovery Ventilation | Low Use Group | New Construction/Retrofit | space heating | High Efficient 85% Energy Recovery Ventilation Low Use Group (Office, Warehouse, School) | Ventilation with ERV Integrated | Ventilation without ERV |  |  | CFM | TRM Version 5.0 | 2020-11-12 | 0 | 2.51 | 0 | 0 | 0 | 0 | 0 | 7.86 | 14 | Low-Income | 0 | 1 | 1
COM-ERV-SH-366-03 | Current |  | Commercial | Energy Recovery Ventilation | Multi-Residential, Health Care, Nursing Homes | New Construction/Retrofit | space heating | High Efficient 85% Energy Recovery Ventilation High Use Group (Multi-Residential, Health Care, Nursing Homes) | Ventilation with ERV Integrated | Ventilation without ERV |  |  | CFM | TRM Version 5.0 | 2020-11-12 | 0 | 7.07 | 0 | 0 | 0 | 0 | 0 | 7.86 | 14 | Low-Income | 0 | 1 | 1
COM-ERV-SH-368-03 | Current |  | Commercial | Energy Recovery Ventilation | Hotel | New Construction/Retrofit | space heating | High Efficient 85% Energy Recovery Ventilation Medium Use Group (Hotel, Restaurant, Retail) | Ventilation with ERV Integrated | Ventilation without ERV |  |  | CFM | TRM Version 5.0 | 2020-11-12 | 0 | 5.05 | 0 | 0 | 0 | 0 | 0 | 7.86 | 14 | Low-Income | 0 | 1 | 1
COM-ERV-SH-370-03 | Current |  | Commercial | Energy Recovery Ventilation | Restaurant | New Construction/Retrofit | space heating | High Efficient 85% Energy Recovery Ventilation Medium Use Group (Hotel, Restaurant, Retail) | Ventilation with ERV Integrated | Ventilation without ERV |  |  | CFM | TRM Version 5.0 | 2020-11-12 | 0 | 3.66 | 0 | 0 | 0 | 0 | 0 | 7.86 | 14 | Low-Income | 0 | 1 | 1
COM-ERV-SH-372-03 | Current |  | Commercial | Energy Recovery Ventilation | Retail | New Construction/Retrofit | space heating | High Efficient 85% Energy Recovery Ventilation Medium Use Group (Hotel, Restaurant, Retail) | Ventilation with ERV Integrated | Ventilation without ERV |  |  | CFM | TRM Version 5.0 | 2020-11-12 | 0 | 3.07 | 0 | 0 | 0 | 0 | 0 | 7.86 | 14 | Low-Income | 0 | 1 | 1
COM-ERV-SH-374-03 | Current |  | Commercial | Energy Recovery Ventilation | Office | New Construction/Retrofit | space heating | High Efficient 85% Energy Recovery Ventilation Low Use Group (Office, Warehouse, School) | Ventilation with ERV Integrated | Ventilation without ERV |  |  | CFM | TRM Version 5.0 | 2020-11-12 | 0 | 2.69 | 0 | 0 | 0 | 0 | 0 | 7.86 | 14 | Low-Income | 0 | 1 | 1
COM-ERV-SH-376-03 | Current |  | Commercial | Energy Recovery Ventilation | Warehouse | New Construction/Retrofit | space heating | High Efficient 85% Energy Recovery Ventilation Low Use Group (Office, Warehouse, School) | Ventilation with ERV Integrated | Ventilation without ERV |  |  | CFM | TRM Version 5.0 | 2020-11-12 | 0 | 2.57 | 0 | 0 | 0 | 0 | 0 | 7.86 | 14 | Low-Income | 0 | 1 | 1
COM-ERV-SH-378-03 | Current |  | Commercial | Energy Recovery Ventilation | School | New Construction/Retrofit | space heating | High Efficient 85% Energy Recovery Ventilation Low Use Group (Office, Warehouse, School) | Ventilation with ERV Integrated | Ventilation without ERV |  |  | CFM | TRM Version 5.0 | 2020-11-12 | 0 | 2.27 | 0 | 0 | 0 | 0 | 0 | 7.86 | 14 | Low-Income | 0 | 1 | 1
COM-ERV-SH-301-03 | Current |  | Commercial | Energy Recovery Ventilation | High Use Group | New Construction/Retrofit | space heating | High Efficient 55% Energy Recovery Ventilation High Use Group (Multi-Residential, Health Care, Nursing Homes) | Ventilation with ERV Standalone | Ventilation without ERV |  |  | CFM | TRM Version 5.0 | 2020-11-12 | 0 | 4.52 | 0 | -4.39 | 0 | 0 | 0 | 7.8 | 14 | Low-Income | 0 | 1 | 1
COM-ERV-SH-303-03 | Current |  | Commercial | Energy Recovery Ventilation | Medium Use Group | New Construction/Retrofit | space heating | High Efficient 55% Energy Recovery Ventilation Medium Use Group (Hotel, Restaurant, Retail) | Ventilation with ERV Standalone | Ventilation without ERV |  |  | CFM | TRM Version 5.0 | 2020-11-12 | 0 | 2.51 | 0 | -2.44 | 0 | 0 | 0 | 7.8 | 14 | Low-Income | 0 | 1 | 1
COM-ERV-SH-305-03 | Current |  | Commercial | Energy Recovery Ventilation | Low Use Group | New Construction/Retrofit | space heating | High Efficient 55% Energy Recovery Ventilation Low Use Group (Office, Warehouse, School) | Ventilation with ERV Standalone | Ventilation without ERV |  |  | CFM | TRM Version 5.0 | 2020-11-12 | 0 | 1.6 | 0 | -1.56 | 0 | 0 | 0 | 7.8 | 14 | Low-Income | 0 | 1 | 1
COM-ERV-SH-307-03 | Current |  | Commercial | Energy Recovery Ventilation | Multi-Residential, Health Care, Nursing Homes | New Construction/Retrofit | space heating | High Efficient 55% Energy Recovery Ventilation High Use Group (Multi-Residential, Health Care, Nursing Homes) | Ventilation with ERV Standalone | Ventilation without ERV |  |  | CFM | TRM Version 5.0 | 2020-11-12 | 0 | 4.52 | 0 | -4.39 | 0 | 0 | 0 | 7.8 | 14 | Low-Income | 0 | 1 | 1
COM-ERV-SH-309-03 | Current |  | Commercial | Energy Recovery Ventilation | Hotel | New Construction/Retrofit | space heating | High Efficient 55% Energy Recovery Ventilation Medium Use Group (Hotel, Restaurant, Retail) | Ventilation with ERV Standalone | Ventilation without ERV |  |  | CFM | TRM Version 5.0 | 2020-11-12 | 0 | 3.23 | 0 | -3.14 | 0 | 0 | 0 | 7.8 | 14 | Low-Income | 0 | 1 | 1
COM-ERV-SH-311-03 | Current |  | Commercial | Energy Recovery Ventilation | Restaurant | New Construction/Retrofit | space heating | High Efficient 55% Energy Recovery Ventilation Medium Use Group (Hotel, Restaurant, Retail) | Ventilation with ERV Standalone | Ventilation without ERV |  |  | CFM | TRM Version 5.0 | 2020-11-12 | 0 | 2.34 | 0 | -2.28 | 0 | 0 | 0 | 7.8 | 14 | Low-Income | 0 | 1 | 1
COM-ERV-SH-313-03 | Current |  | Commercial | Energy Recovery Ventilation | Retail | New Construction/Retrofit | space heating | High Efficient 55% Energy Recovery Ventilation Medium Use Group (Hotel, Restaurant, Retail) | Ventilation with ERV Standalone | Ventilation without ERV |  |  | CFM | TRM Version 5.0 | 2020-11-12 | 0 | 1.96 | 0 | -1.91 | 0 | 0 | 0 | 7.8 | 14 | Low-Income | 0 | 1 | 1
COM-ERV-SH-315-03 | Current |  | Commercial | Energy Recovery Ventilation | Office | New Construction/Retrofit | space heating | High Efficient 55% Energy Recovery Ventilation Low Use Group (Office, Warehouse, School) | Ventilation with ERV Standalone | Ventilation without ERV |  |  | CFM | TRM Version 5.0 | 2020-11-12 | 0 | 1.72 | 0 | -1.67 | 0 | 0 | 0 | 7.8 | 14 | Low-Income | 0 | 1 | 1
COM-ERV-SH-317-03 | Current |  | Commercial | Energy Recovery Ventilation | Warehouse | New Construction/Retrofit | space heating | High Efficient 55% Energy Recovery Ventilation Low Use Group (Office, Warehouse, School) | Ventilation with ERV Standalone | Ventilation without ERV |  |  | CFM | TRM Version 5.0 | 2020-11-12 | 0 | 1.64 | 0 | -1.6 | 0 | 0 | 0 | 7.8 | 14 | Low-Income | 0 | 1 | 1
COM-ERV-SH-319-03 | Current |  | Commercial | Energy Recovery Ventilation | School | New Construction/Retrofit | space heating | High Efficient 55% Energy Recovery Ventilation Low Use Group (Office, Warehouse, School) | Ventilation with ERV Standalone | Ventilation without ERV |  |  | CFM | TRM Version 5.0 | 2020-11-12 | 0 | 1.45 | 0 | -1.41 | 0 | 0 | 0 | 7.8 | 14 | Low-Income | 0 | 1 | 1
COM-ERV-SH-321-03 | Current |  | Commercial | Energy Recovery Ventilation | High Use Group | New Construction/Retrofit | space heating | High Efficient 65% Energy Recovery Ventilation High Use Group (Multi-Residential, Health Care, Nursing Homes) | Ventilation with ERV Standalone | Ventilation without ERV |  |  | CFM | TRM Version 5.0 | 2020-11-12 | 0 | 5.37 | 0 | -4.39 | 0 | 0 | 0 | 8.8 | 14 | Low-Income | 0 | 1 | 1
COM-ERV-SH-323-03 | Current |  | Commercial | Energy Recovery Ventilation | Medium Use Group | New Construction/Retrofit | space heating | High Efficient 65% Energy Recovery Ventilation Medium Use Group (Hotel, Restaurant, Retail) | Ventilation with ERV Standalone | Ventilation without ERV |  |  | CFM | TRM Version 5.0 | 2020-11-12 | 0 | 2.98 | 0 | -2.44 | 0 | 0 | 0 | 8.8 | 14 | Low-Income | 0 | 1 | 1
COM-ERV-SH-325-03 | Current |  | Commercial | Energy Recovery Ventilation | Low Use Group | New Construction/Retrofit | space heating | High Efficient 65% Energy Recovery Ventilation Low Use Group (Office, Warehouse, School) | Ventilation with ERV Standalone | Ventilation without ERV |  |  | CFM | TRM Version 5.0 | 2020-11-12 | 0 | 1.91 | 0 | -1.56 | 0 | 0 | 0 | 8.8 | 14 | Low-Income | 0 | 1 | 1
COM-ERV-SH-327-03 | Current |  | Commercial | Energy Recovery Ventilation | Multi-Residential, Health Care, Nursing Homes | New Construction/Retrofit | space heating | High Efficient 65% Energy Recovery Ventilation High Use Group (Multi-Residential, Health Care, Nursing Homes) | Ventilation with ERV Standalone | Ventilation without ERV |  |  | CFM | TRM Version 5.0 | 2020-11-12 | 0 | 5.37 | 0 | -4.39 | 0 | 0 | 0 | 8.8 | 14 | Low-Income | 0 | 1 | 1
COM-ERV-SH-329-03 | Current |  | Commercial | Energy Recovery Ventilation | Hotel | New Construction/Retrofit | space heating | High Efficient 65% Energy Recovery Ventilation Medium Use Group (Hotel, Restaurant, Retail) | Ventilation with ERV Standalone | Ventilation without ERV |  |  | CFM | TRM Version 5.0 | 2020-11-12 | 0 | 3.84 | 0 | -3.14 | 0 | 0 | 0 | 8.8 | 14 | Low-Income | 0 | 1 | 1
COM-ERV-SH-331-03 | Current |  | Commercial | Energy Recovery Ventilation | Restaurant | New Construction/Retrofit | space heating | High Efficient 65% Energy Recovery Ventilation Medium Use Group (Hotel, Restaurant, Retail) | Ventilation with ERV Standalone | Ventilation without ERV |  |  | CFM | TRM Version 5.0 | 2020-11-12 | 0 | 2.78 | 0 | -2.28 | 0 | 0 | 0 | 8.8 | 14 | Low-Income | 0 | 1 | 1
COM-ERV-SH-333-03 | Current |  | Commercial | Energy Recovery Ventilation | Retail | New Construction/Retrofit | space heating | High Efficient 65% Energy Recovery Ventilation Medium Use Group (Hotel, Restaurant, Retail) | Ventilation with ERV Standalone | Ventilation without ERV |  |  | CFM | TRM Version 5.0 | 2020-11-12 | 0 | 2.33 | 0 | -1.91 | 0 | 0 | 0 | 8.8 | 14 | Low-Income | 0 | 1 | 1
COM-ERV-SH-335-03 | Current |  | Commercial | Energy Recovery Ventilation | Office | New Construction/Retrofit | space heating | High Efficient 65% Energy Recovery Ventilation Low Use Group (Office, Warehouse, School) | Ventilation with ERV Standalone | Ventilation without ERV |  |  | CFM | TRM Version 5.0 | 2020-11-12 | 0 | 2.05 | 0 | -1.67 | 0 | 0 | 0 | 8.8 | 14 | Low-Income | 0 | 1 | 1
COM-ERV-SH-337-03 | Current |  | Commercial | Energy Recovery Ventilation | Warehouse | New Construction/Retrofit | space heating | High Efficient 65% Energy Recovery Ventilation Low Use Group (Office, Warehouse, School) | Ventilation with ERV Standalone | Ventilation without ERV |  |  | CFM | TRM Version 5.0 | 2020-11-12 | 0 | 1.95 | 0 | -1.6 | 0 | 0 | 0 | 8.8 | 14 | Low-Income | 0 | 1 | 1
COM-ERV-SH-339-03 | Current |  | Commercial | Energy Recovery Ventilation | School | New Construction/Retrofit | space heating | High Efficient 65% Energy Recovery Ventilation Low Use Group (Office, Warehouse, School) | Ventilation with ERV Standalone | Ventilation without ERV |  |  | CFM | TRM Version 5.0 | 2020-11-12 | 0 | 1.73 | 0 | -1.41 | 0 | 0 | 0 | 8.8 | 14 | Low-Income | 0 | 1 | 1
COM-ERV-SH-341-03 | Current |  | Commercial | Energy Recovery Ventilation | High Use Group | New Construction/Retrofit | space heating | High Efficient 75% Energy Recovery Ventilation High Use Group (Multi-Residential, Health Care, Nursing Homes) | Ventilation with ERV Standalone | Ventilation without ERV |  |  | CFM | TRM Version 5.0 | 2020-11-12 | 0 | 6.22 | 0 | -4.39 | 0 | 0 | 0 | 9.8 | 14 | Low-Income | 0 | 1 | 1
COM-ERV-SH-343-03 | Current |  | Commercial | Energy Recovery Ventilation | Medium Use Group | New Construction/Retrofit | space heating | High Efficient 75% Energy Recovery Ventilation Medium Use Group (Hotel, Restaurant, and Retail) | Ventilation with ERV Standalone | Ventilation without ERV |  |  | CFM | TRM Version 5.0 | 2020-11-12 | 0 | 3.45 | 0 | -2.44 | 0 | 0 | 0 | 9.8 | 14 | Low-Income | 0 | 1 | 1
COM-ERV-SH-345-03 | Current |  | Commercial | Energy Recovery Ventilation | Low Use Group | New Construction/Retrofit | space heating | High Efficient 75% Energy Recovery Ventilation Low Use Group (Office, Warehouse, School) | Ventilation with ERV Standalone | Ventilation without ERV |  |  | CFM | TRM Version 5.0 | 2020-11-12 | 0 | 2.21 | 0 | -1.56 | 0 | 0 | 0 | 9.8 | 14 | Low-Income | 0 | 1 | 1
COM-ERV-SH-347-03 | Current |  | Commercial | Energy Recovery Ventilation | Multi-Residential, Health Care, Nursing Homes | New Construction/Retrofit | space heating | High Efficient 75% Energy Recovery Ventilation High Use Group (Multi-Residential, Health Care, Nursing Homes) | Ventilation with ERV Standalone | Ventilation without ERV |  |  | CFM | TRM Version 5.0 | 2020-11-12 | 0 | 6.22 | 0 | -4.39 | 0 | 0 | 0 | 9.8 | 14 | Low-Income | 0 | 1 | 1
COM-ERV-SH-349-03 | Current |  | Commercial | Energy Recovery Ventilation | Hotel | New Construction/Retrofit | space heating | High Efficient 75% Energy Recovery Ventilation Medium Use Group (Hotel, Restaurant, and Retail) | Ventilation with ERV Standalone | Ventilation without ERV |  |  | CFM | TRM Version 5.0 | 2020-11-12 | 0 | 4.44 | 0 | -3.14 | 0 | 0 | 0 | 9.8 | 14 | Low-Income | 0 | 1 | 1
COM-ERV-SH-351-03 | Current |  | Commercial | Energy Recovery Ventilation | Restaurant | New Construction/Retrofit | space heating | High Efficient 75% Energy Recovery Ventilation Medium Use Group (Hotel, Restaurant, and Retail) | Ventilation with ERV Standalone | Ventilation without ERV |  |  | CFM | TRM Version 5.0 | 2020-11-12 | 0 | 3.22 | 0 | -2.28 | 0 | 0 | 0 | 9.8 | 14 | Low-Income | 0 | 1 | 1
COM-ERV-SH-353-03 | Current |  | Commercial | Energy Recovery Ventilation | Retail | New Construction/Retrofit | space heating | High Efficient 75% Energy Recovery Ventilation Medium Use Group (Hotel, Restaurant, and Retail) | Ventilation with ERV Standalone | Ventilation without ERV |  |  | CFM | TRM Version 5.0 | 2020-11-12 | 0 | 2.7 | 0 | -1.91 | 0 | 0 | 0 | 9.8 | 14 | Low-Income | 0 | 1 | 1
COM-ERV-SH-355-03 | Current |  | Commercial | Energy Recovery Ventilation | Office | New Construction/Retrofit | space heating | High Efficient 75% Energy Recovery Ventilation Low Use Group (Office, Warehouse, School) | Ventilation with ERV Standalone | Ventilation without ERV |  |  | CFM | TRM Version 5.0 | 2020-11-12 | 0 | 2.37 | 0 | -1.67 | 0 | 0 | 0 | 9.8 | 14 | Low-Income | 0 | 1 | 1
COM-ERV-SH-357-03 | Current |  | Commercial | Energy Recovery Ventilation | Warehouse | New Construction/Retrofit | space heating | High Efficient 75% Energy Recovery Ventilation Low Use Group (Office, Warehouse, School) | Ventilation with ERV Standalone | Ventilation without ERV |  |  | CFM | TRM Version 5.0 | 2020-11-12 | 0 | 2.26 | 0 | -1.6 | 0 | 0 | 0 | 9.8 | 14 | Low-Income | 0 | 1 | 1
COM-ERV-SH-359-03 | Current |  | Commercial | Energy Recovery Ventilation | School | New Construction/Retrofit | space heating | High Efficient 75% Energy Recovery Ventilation Low Use Group (Office, Warehouse, School) | Ventilation with ERV Standalone | Ventilation without ERV |  |  | CFM | TRM Version 5.0 | 2020-11-12 | 0 | 2 | 0 | -1.41 | 0 | 0 | 0 | 9.8 | 14 | Low-Income | 0 | 1 | 1
COM-ERV-SH-361-03 | Current |  | Commercial | Energy Recovery Ventilation | High Use Group | New Construction/Retrofit | space heating | High Efficient 85% Energy Recovery Ventilation High Use Group (Multi-Residential, Health Care, Nursing Homes) | Ventilation with ERV Standalone | Ventilation without ERV |  |  | CFM | TRM Version 5.0 | 2020-11-12 | 0 | 7.07 | 0 | -4.39 | 0 | 0 | 0 | 10.8 | 14 | Low-Income | 0 | 1 | 1
COM-ERV-SH-363-03 | Current |  | Commercial | Energy Recovery Ventilation | Medium Use Group | New Construction/Retrofit | space heating | High Efficient 85% Energy Recovery Ventilation Medium Use Group (Hotel, Restaurant, Retail) | Ventilation with ERV Standalone | Ventilation without ERV |  |  | CFM | TRM Version 5.0 | 2020-11-12 | 0 | 3.93 | 0 | -2.44 | 0 | 0 | 0 | 10.8 | 14 | Low-Income | 0 | 1 | 1
COM-ERV-SH-365-03 | Current |  | Commercial | Energy Recovery Ventilation | Low Use Group | New Construction/Retrofit | space heating | High Efficient 85% Energy Recovery Ventilation Low Use Group (Office, Warehouse, School) | Ventilation with ERV Standalone | Ventilation without ERV |  |  | CFM | TRM Version 5.0 | 2020-11-12 | 0 | 2.51 | 0 | -1.56 | 0 | 0 | 0 | 10.8 | 14 | Low-Income | 0 | 1 | 1
COM-ERV-SH-367-03 | Current |  | Commercial | Energy Recovery Ventilation | Multi-Residential, Health Care, Nursing Homes | New Construction/Retrofit | space heating | High Efficient 85% Energy Recovery Ventilation High Use Group (Multi-Residential, Health Care, Nursing Homes) | Ventilation with ERV Standalone | Ventilation without ERV |  |  | CFM | TRM Version 5.0 | 2020-11-12 | 0 | 7.07 | 0 | -4.39 | 0 | 0 | 0 | 10.8 | 14 | Low-Income | 0 | 1 | 1
COM-ERV-SH-369-03 | Current |  | Commercial | Energy Recovery Ventilation | Hotel | New Construction/Retrofit | space heating | High Efficient 85% Energy Recovery Ventilation Medium Use Group (Hotel, Restaurant, Retail) | Ventilation with ERV Standalone | Ventilation without ERV |  |  | CFM | TRM Version 5.0 | 2020-11-12 | 0 | 5.05 | 0 | -3.14 | 0 | 0 | 0 | 10.8 | 14 | Low-Income | 0 | 1 | 1
COM-ERV-SH-371-03 | Current |  | Commercial | Energy Recovery Ventilation | Restaurant | New Construction/Retrofit | space heating | High Efficient 85% Energy Recovery Ventilation Medium Use Group (Hotel, Restaurant, Retail) | Ventilation with ERV Standalone | Ventilation without ERV |  |  | CFM | TRM Version 5.0 | 2020-11-12 | 0 | 3.66 | 0 | -2.28 | 0 | 0 | 0 | 10.8 | 14 | Low-Income | 0 | 1 | 1
COM-ERV-SH-373-03 | Current |  | Commercial | Energy Recovery Ventilation | Retail | New Construction/Retrofit | space heating | High Efficient 85% Energy Recovery Ventilation Medium Use Group (Hotel, Restaurant, Retail) | Ventilation with ERV Standalone | Ventilation without ERV |  |  | CFM | TRM Version 5.0 | 2020-11-12 | 0 | 3.07 | 0 | -1.91 | 0 | 0 | 0 | 10.8 | 14 | Low-Income | 0 | 1 | 1
COM-ERV-SH-375-03 | Current |  | Commercial | Energy Recovery Ventilation | Office | New Construction/Retrofit | space heating | High Efficient 85% Energy Recovery Ventilation Low Use Group (Office, Warehouse, School) | Ventilation with ERV Standalone | Ventilation without ERV |  |  | CFM | TRM Version 5.0 | 2020-11-12 | 0 | 2.69 | 0 | -1.67 | 0 | 0 | 0 | 10.8 | 14 | Low-Income | 0 | 1 | 1
COM-ERV-SH-377-03 | Current |  | Commercial | Energy Recovery Ventilation | Warehouse | New Construction/Retrofit | space heating | High Efficient 85% Energy Recovery Ventilation Low Use Group (Office, Warehouse, School) | Ventilation with ERV Standalone | Ventilation without ERV |  |  | CFM | TRM Version 5.0 | 2020-11-12 | 0 | 2.57 | 0 | -1.6 | 0 | 0 | 0 | 10.8 | 14 | Low-Income | 0 | 1 | 1
COM-ERV-SH-379-03 | Current |  | Commercial | Energy Recovery Ventilation | School | New Construction/Retrofit | space heating | High Efficient 85% Energy Recovery Ventilation Low Use Group (Office, Warehouse, School) | Ventilation with ERV Standalone | Ventilation without ERV |  |  | CFM | TRM Version 5.0 | 2020-11-12 | 0 | 2.27 | 0 | -1.41 | 0 | 0 | 0 | 10.8 | 14 | Low-Income | 0 | 1 | 1
COM-HRV-SH-366-04 | Current |  | Commercial | Heat Recovery Ventialation | High Use | New Construction/Retrofit | space heating | High Efficient 55% Heat Recovery Ventilation High Use Group (Multi-Residential, Health Care, Nursing Homes) | Ventilation with HRV Integrated | Ventilation without HRV |  |  | CFM | TRM Version 5.0 | 2020-11-12 | 0 | 3.84 | 0 | 0 | 0 | 0 | 0 | 5.35 | 14 | Low-Income | 0 | 1 | 1
COM-HRV-SH-368-04 | Current |  | Commercial | Heat Recovery Ventialation | Low Use | New Construction/Retrofit | space heating | High Efficient 55% Heat Recovery Ventilation Low Use Group (Office, Warehouse, School) | Ventilation with HRV Integrated | Ventilation without HRV |  |  | CFM | TRM Version 5.0 | 2020-11-12 | 0 | 1.36 | 0 | 0 | 0 | 0 | 0 | 5.35 | 14 | Low-Income | 0 | 1 | 1
COM-HRV-SH-370-04 | Current |  | Commercial | Heat Recovery Ventialation | Medium Use | New Construction/Retrofit | space heating | High Efficient 55% Heat Recovery Ventilation Medium Use Group (Hotel, Restaurant, Retail) | Ventilation with HRV Integrated | Ventilation without HRV |  |  | CFM | TRM Version 5.0 | 2020-11-12 | 0 | 2.13 | 0 | 0 | 0 | 0 | 0 | 5.35 | 14 | Low-Income | 0 | 1 | 1
COM-HRV-SH-372-04 | Current |  | Commercial | Heat Recovery Ventialation | High Use | New Construction/Retrofit | space heating | High Efficient 65% Heat Recovery Ventilation High Use Group (Multi-Residential, Health Care, Nursing Homes) | Ventilation with HRV Integrated | Ventilation without HRV |  |  | CFM | TRM Version 5.0 | 2020-11-12 | 0 | 4.54 | 0 | 0 | 0 | 0 | 0 | 6.35 | 14 | Low-Income | 0 | 1 | 1
COM-HRV-SH-374-04 | Current |  | Commercial | Heat Recovery Ventialation | Low Use | New Construction/Retrofit | space heating | High Efficient 65% Heat Recovery Ventilation Low Use Group (Office, Warehouse, School) | Ventilation with HRV Integrated | Ventilation without HRV |  |  | CFM | TRM Version 5.0 | 2020-11-12 | 0 | 1.61 | 0 | 0 | 0 | 0 | 0 | 6.35 | 14 | Low-Income | 0 | 1 | 1
COM-HRV-SH-376-04 | Current |  | Commercial | Heat Recovery Ventialation | Medium Use | New Construction/Retrofit | space heating | High Efficient 65% Heat Recovery Ventilation Medium Use Group (Hotel, Restaurant, Retail) | Ventilation with HRV Integrated | Ventilation without HRV |  |  | CFM | TRM Version 5.0 | 2020-11-12 | 0 | 2.52 | 0 | 0 | 0 | 0 | 0 | 6.35 | 14 | Low-Income | 0 | 1 | 1
COM-HRV-SH-378-04 | Current |  | Commercial | Heat Recovery Ventialation | High Use | New Construction/Retrofit | space heating | High Efficient 75% Heat Recovery Ventilation High Use Group (Multi-Residential, Health Care, Nursing Homes) | Ventilation with HRV Integrated | Ventilation without HRV |  |  | CFM | TRM Version 5.0 | 2020-11-12 | 0 | 5.24 | 0 | 0 | 0 | 0 | 0 | 7.35 | 14 | Low-Income | 0 | 1 | 1
COM-HRV-SH-380-04 | Current |  | Commercial | Heat Recovery Ventialation | Low Use | New Construction/Retrofit | space heating | High Efficient 75% Heat Recovery Ventilation Low Use Group (Office, Warehouse, School) | Ventilation with HRV Integrated | Ventilation without HRV |  |  | CFM | TRM Version 5.0 | 2020-11-12 | 0 | 1.86 | 0 | 0 | 0 | 0 | 0 | 7.35 | 14 | Low-Income | 0 | 1 | 1
COM-HRV-SH-382-04 | Current |  | Commercial | Heat Recovery Ventialation | Medium Use | New Construction/Retrofit | space heating | High Efficient 75% Heat Recovery Ventilation Medium Use Group (Hotel, Restaurant, Retail) | Ventilation with HRV Integrated | Ventilation without HRV |  |  | CFM | TRM Version 5.0 | 2020-11-12 | 0 | 2.91 | 0 | 0 | 0 | 0 | 0 | 7.35 | 14 | Low-Income | 0 | 1 | 1
COM-HRV-SH-384-04 | Current |  | Commercial | Heat Recovery Ventialation | High Use | New Construction/Retrofit | space heating | High Efficient 85% Heat Recovery Ventilation High Use Group (Multi-Residential, Health Care, Nursing Homes) | Ventilation with HRV Integrated | Ventilation without HRV |  |  | CFM | TRM Version 5.0 | 2020-11-12 | 0 | 5.93 | 0 | 0 | 0 | 0 | 0 | 8.35 | 14 | Low-Income | 0 | 1 | 1
COM-HRV-SH-386-04 | Current |  | Commercial | Heat Recovery Ventialation | Low Use | New Construction/Retrofit | space heating | High Efficient 85% Heat Recovery Ventilation Low Use Group (Office, Warehouse, School) | Ventilation with HRV Integrated | Ventilation without HRV |  |  | CFM | TRM Version 5.0 | 2020-11-12 | 0 | 2.11 | 0 | 0 | 0 | 0 | 0 | 8.35 | 14 | Low-Income | 0 | 1 | 1
COM-HRV-SH-388-04 | Current |  | Commercial | Heat Recovery Ventialation | Medium Use | New Construction/Retrofit | space heating | High Efficient 85% Heat Recovery Ventilation Medium Use Group (Hotel, Restaurant, Retail) | Ventilation with HRV Integrated | Ventilation without HRV |  |  | CFM | TRM Version 5.0 | 2020-11-12 | 0 | 3.3 | 0 | 0 | 0 | 0 | 0 | 8.35 | 14 | Low-Income | 0 | 1 | 1
COM-HRV-SH-390-04 | Current |  | Commercial | Heat Recovery Ventialation | Multi-Family, Health Care and Nursing Homes | New Construction/Retrofit | space heating | High Efficient 55% Heat Recovery Ventilation High Use Group (Multi-Residential, Health Care, Nursing Homes) | Ventilation with HRV Integrated | Ventilation without HRV |  |  | CFM | TRM Version 5.0 | 2020-11-12 | 0 | 3.84 | 0 | 0 | 0 | 0 | 0 | 5.35 | 14 | Low-Income | 0 | 1 | 1
COM-HRV-SH-392-04 | Current |  | Commercial | Heat Recovery Ventialation | Hotels | New Construction/Retrofit | space heating | High Efficient 55% Heat Recovery Ventilation Medium Use Group (Hotel, Restaurant, Retail) | Ventilation with HRV Integrated | Ventilation without HRV |  |  | CFM | TRM Version 5.0 | 2020-11-12 | 0 | 2.74 | 0 | 0 | 0 | 0 | 0 | 5.35 | 14 | Low-Income | 0 | 1 | 1
COM-HRV-SH-394-04 | Current |  | Commercial | Heat Recovery Ventialation | Restaurant | New Construction/Retrofit | space heating | High Efficient 55% Heat Recovery Ventilation Medium Use Group (Hotel, Restaurant, Retail) | Ventilation with HRV Integrated | Ventilation without HRV |  |  | CFM | TRM Version 5.0 | 2020-11-12 | 0 | 1.99 | 0 | 0 | 0 | 0 | 0 | 5.35 | 14 | Low-Income | 0 | 1 | 1
COM-HRV-SH-396-04 | Current |  | Commercial | Heat Recovery Ventialation | Retail | New Construction/Retrofit | space heating | High Efficient 55% Heat Recovery Ventilation Medium Use Group (Hotel, Restaurant, Retail) | Ventilation with HRV Integrated | Ventilation without HRV |  |  | CFM | TRM Version 5.0 | 2020-11-12 | 0 | 1.67 | 0 | 0 | 0 | 0 | 0 | 5.35 | 14 | Low-Income | 0 | 1 | 1
COM-HRV-SH-398-04 | Current |  | Commercial | Heat Recovery Ventialation | Office | New Construction/Retrofit | space heating | High Efficient 55% Heat Recovery Ventilation Low Use Group (Office, Warehouse, School) | Ventilation with HRV Integrated | Ventilation without HRV |  |  | CFM | TRM Version 5.0 | 2020-11-12 | 0 | 1.46 | 0 | 0 | 0 | 0 | 0 | 5.35 | 14 | Low-Income | 0 | 1 | 1
COM-HRV-SH-400-04 | Current |  | Commercial | Heat Recovery Ventialation | Warehouse | New Construction/Retrofit | space heating | High Efficient 55% Heat Recovery Ventilation Low Use Group (Office, Warehouse, School) | Ventilation with HRV Integrated | Ventilation without HRV |  |  | CFM | TRM Version 5.0 | 2020-11-12 | 0 | 1.39 | 0 | 0 | 0 | 0 | 0 | 5.35 | 14 | Low-Income | 0 | 1 | 1
COM-HRV-SH-402-04 | Current |  | Commercial | Heat Recovery Ventialation | School | New Construction/Retrofit | space heating | High Efficient 55% Heat Recovery Ventilation Low Use Group (Office, Warehouse, School) | Ventilation with HRV Integrated | Ventilation without HRV |  |  | CFM | TRM Version 5.0 | 2020-11-12 | 0 | 1.23 | 0 | 0 | 0 | 0 | 0 | 5.35 | 14 | Low-Income | 0 | 1 | 1
COM-HRV-SH-404-04 | Current |  | Commercial | Heat Recovery Ventialation | Multi-Family, Health Care and Nursing Homes | New Construction/Retrofit | space heating | High Efficient 65% Heat Recovery Ventilation High Use Group (Multi-Residential, Health Care, Nursing Homes) | Ventilation with HRV Integrated | Ventilation without HRV |  |  | CFM | TRM Version 5.0 | 2020-11-12 | 0 | 4.54 | 0 | 0 | 0 | 0 | 0 | 6.35 | 14 | Low-Income | 0 | 1 | 1
COM-HRV-SH-406-04 | Current |  | Commercial | Heat Recovery Ventialation | Hotels | New Construction/Retrofit | space heating | High Efficient 65% Heat Recovery Ventilation Medium Use Group (Hotel, Restaurant, Retail) | Ventilation with HRV Integrated | Ventilation without HRV |  |  | CFM | TRM Version 5.0 | 2020-11-12 | 0 | 3.24 | 0 | 0 | 0 | 0 | 0 | 6.35 | 14 | Low-Income | 0 | 1 | 1
COM-HRV-SH-408-04 | Current |  | Commercial | Heat Recovery Ventialation | Restaurant | New Construction/Retrofit | space heating | High Efficient 65% Heat Recovery Ventilation Medium Use Group (Hotel, Restaurant, Retail) | Ventilation with HRV Integrated | Ventilation without HRV |  |  | CFM | TRM Version 5.0 | 2020-11-12 | 0 | 2.35 | 0 | 0 | 0 | 0 | 0 | 6.35 | 14 | Low-Income | 0 | 1 | 1
COM-HRV-SH-410-04 | Current |  | Commercial | Heat Recovery Ventialation | Retail | New Construction/Retrofit | space heating | High Efficient 65% Heat Recovery Ventilation Medium Use Group (Hotel, Restaurant, Retail) | Ventilation with HRV Integrated | Ventilation without HRV |  |  | CFM | TRM Version 5.0 | 2020-11-12 | 0 | 1.97 | 0 | 0 | 0 | 0 | 0 | 6.35 | 14 | Low-Income | 0 | 1 | 1
COM-HRV-SH-412-04 | Current |  | Commercial | Heat Recovery Ventialation | Office | New Construction/Retrofit | space heating | High Efficient 65% Heat Recovery Ventilation Low Use Group (Office, Warehouse, School) | Ventilation with HRV Integrated | Ventilation without HRV |  |  | CFM | TRM Version 5.0 | 2020-11-12 | 0 | 1.73 | 0 | 0 | 0 | 0 | 0 | 6.35 | 14 | Low-Income | 0 | 1 | 1
COM-HRV-SH-414-04 | Current |  | Commercial | Heat Recovery Ventialation | Warehouse | New Construction/Retrofit | space heating | High Efficient 65% Heat Recovery Ventilation Low Use Group (Office, Warehouse, School) | Ventilation with HRV Integrated | Ventilation without HRV |  |  | CFM | TRM Version 5.0 | 2020-11-12 | 0 | 1.65 | 0 | 0 | 0 | 0 | 0 | 6.35 | 14 | Low-Income | 0 | 1 | 1
COM-HRV-SH-416-04 | Current |  | Commercial | Heat Recovery Ventialation | School | New Construction/Retrofit | space heating | High Efficient 65% Heat Recovery Ventilation Low Use Group (Office, Warehouse, School) | Ventilation with HRV Integrated | Ventilation without HRV |  |  | CFM | TRM Version 5.0 | 2020-11-12 | 0 | 1.46 | 0 | 0 | 0 | 0 | 0 | 6.35 | 14 | Low-Income | 0 | 1 | 1
COM-HRV-SH-418-04 | Current |  | Commercial | Heat Recovery Ventialation | Multi-Family, Health Care and Nursing Homes | New Construction/Retrofit | space heating | High Efficient 75% Heat Recovery Ventilation High Use Group (Multi-Residential, Health Care, Nursing Homes) | Ventilation with HRV Integrated | Ventilation without HRV |  |  | CFM | TRM Version 5.0 | 2020-11-12 | 0 | 5.24 | 0 | 0 | 0 | 0 | 0 | 7.35 | 14 | Low-Income | 0 | 1 | 1
COM-HRV-SH-420-04 | Current |  | Commercial | Heat Recovery Ventialation | Hotels | New Construction/Retrofit | space heating | High Efficient 75% Heat Recovery Ventilation Medium Use Group (Hotel, Restaurant, Retail) | Ventilation with HRV Integrated | Ventilation without HRV |  |  | CFM | TRM Version 5.0 | 2020-11-12 | 0 | 3.74 | 0 | 0 | 0 | 0 | 0 | 7.35 | 14 | Low-Income | 0 | 1 | 1
COM-HRV-SH-422-04 | Current |  | Commercial | Heat Recovery Ventialation | Restaurant | New Construction/Retrofit | space heating | High Efficient 75% Heat Recovery Ventilation Medium Use Group (Hotel, Restaurant, Retail) | Ventilation with HRV Integrated | Ventilation without HRV |  |  | CFM | TRM Version 5.0 | 2020-11-12 | 0 | 2.71 | 0 | 0 | 0 | 0 | 0 | 7.35 | 14 | Low-Income | 0 | 1 | 1
COM-HRV-SH-424-04 | Current |  | Commercial | Heat Recovery Ventialation | Retail | New Construction/Retrofit | space heating | High Efficient 75% Heat Recovery Ventilation Medium Use Group (Hotel, Restaurant, Retail) | Ventilation with HRV Integrated | Ventilation without HRV |  |  | CFM | TRM Version 5.0 | 2020-11-12 | 0 | 2.28 | 0 | 0 | 0 | 0 | 0 | 7.35 | 14 | Low-Income | 0 | 1 | 1
COM-HRV-SH-426-04 | Current |  | Commercial | Heat Recovery Ventialation | Office | New Construction/Retrofit | space heating | High Efficient 75% Heat Recovery Ventilation Low Use Group (Office, Warehouse, School) | Ventilation with HRV Integrated | Ventilation without HRV |  |  | CFM | TRM Version 5.0 | 2020-11-12 | 0 | 1.99 | 0 | 0 | 0 | 0 | 0 | 7.35 | 14 | Low-Income | 0 | 1 | 1
COM-HRV-SH-428-04 | Current |  | Commercial | Heat Recovery Ventialation | Warehouse | New Construction/Retrofit | space heating | High Efficient 75% Heat Recovery Ventilation Low Use Group (Office, Warehouse, School) | Ventilation with HRV Integrated | Ventilation without HRV |  |  | CFM | TRM Version 5.0 | 2020-11-12 | 0 | 1.9 | 0 | 0 | 0 | 0 | 0 | 7.35 | 14 | Low-Income | 0 | 1 | 1
COM-HRV-SH-430-04 | Current |  | Commercial | Heat Recovery Ventialation | School | New Construction/Retrofit | space heating | High Efficient 75% Heat Recovery Ventilation Low Use Group (Office, Warehouse, School) | Ventilation with HRV Integrated | Ventilation without HRV |  |  | CFM | TRM Version 5.0 | 2020-11-12 | 0 | 1.68 | 0 | 0 | 0 | 0 | 0 | 7.35 | 14 | Low-Income | 0 | 1 | 1
COM-HRV-SH-432-04 | Current |  | Commercial | Heat Recovery Ventialation | Multi-Family, Health Care and Nursing Homes | New Construction/Retrofit | space heating | High Efficient 85% Heat Recovery Ventilation High Use Group (Multi-Residential, Health Care, Nursing Homes) | Ventilation with HRV Integrated | Ventilation without HRV |  |  | CFM | TRM Version 5.0 | 2020-11-12 | 0 | 5.93 | 0 | 0 | 0 | 0 | 0 | 8.35 | 14 | Low-Income | 0 | 1 | 1
COM-HRV-SH-434-04 | Current |  | Commercial | Heat Recovery Ventialation | Hotels | New Construction/Retrofit | space heating | High Efficient 85% Heat Recovery Ventilation Medium Use Group (Hotel, Restaurant, Retail) | Ventilation with HRV Integrated | Ventilation without HRV |  |  | CFM | TRM Version 5.0 | 2020-11-12 | 0 | 4.24 | 0 | 0 | 0 | 0 | 0 | 8.35 | 14 | Low-Income | 0 | 1 | 1
COM-HRV-SH-436-04 | Current |  | Commercial | Heat Recovery Ventialation | Restaurant | New Construction/Retrofit | space heating | High Efficient 85% Heat Recovery Ventilation Medium Use Group (Hotel, Restaurant, Retail) | Ventilation with HRV Integrated | Ventilation without HRV |  |  | CFM | TRM Version 5.0 | 2020-11-12 | 0 | 3.07 | 0 | 0 | 0 | 0 | 0 | 8.35 | 14 | Low-Income | 0 | 1 | 1
COM-HRV-SH-438-04 | Current |  | Commercial | Heat Recovery Ventialation | Retail | New Construction/Retrofit | space heating | High Efficient 85% Heat Recovery Ventilation Medium Use Group (Hotel, Restaurant, Retail) | Ventilation with HRV Integrated | Ventilation without HRV |  |  | CFM | TRM Version 5.0 | 2020-11-12 | 0 | 2.58 | 0 | 0 | 0 | 0 | 0 | 8.35 | 14 | Low-Income | 0 | 1 | 1
COM-HRV-SH-440-04 | Current |  | Commercial | Heat Recovery Ventialation | Office | New Construction/Retrofit | space heating | High Efficient 85% Heat Recovery Ventilation Low Use Group (Office, Warehouse, School) | Ventilation with HRV Integrated | Ventilation without HRV |  |  | CFM | TRM Version 5.0 | 2020-11-12 | 0 | 2.26 | 0 | 0 | 0 | 0 | 0 | 8.35 | 14 | Low-Income | 0 | 1 | 1
COM-HRV-SH-442-04 | Current |  | Commercial | Heat Recovery Ventialation | Warehouse | New Construction/Retrofit | space heating | High Efficient 85% Heat Recovery Ventilation Low Use Group (Office, Warehouse, School) | Ventilation with HRV Integrated | Ventilation without HRV |  |  | CFM | TRM Version 5.0 | 2020-11-12 | 0 | 2.15 | 0 | 0 | 0 | 0 | 0 | 8.35 | 14 | Low-Income | 0 | 1 | 1
COM-HRV-SH-444-04 | Current |  | Commercial | Heat Recovery Ventialation | School | New Construction/Retrofit | space heating | High Efficient 85% Heat Recovery Ventilation Low Use Group (Office, Warehouse, School) | Ventilation with HRV Integrated | Ventilation without HRV |  |  | CFM | TRM Version 5.0 | 2020-11-12 | 0 | 1.91 | 0 | 0 | 0 | 0 | 0 | 8.35 | 14 | Low-Income | 0 | 1 | 1
COM-HRV-SH-367-04 | Current |  | Commercial | Heat Recovery Ventialation | High Use | New Construction/Retrofit | space heating | High Efficient 55% Heat Recovery Ventilation High Use Group (Multi-Residential, Health Care, Nursing Homes) | Ventilation with HRV Standalone | Ventilation without HRV |  |  | CFM | TRM Version 5.0 | 2020-11-12 | 0 | 3.84 | 0 | -4.39 | 0 | 0 | 0 | 8.28 | 14 | Low-Income | 0 | 1 | 1
COM-HRV-SH-369-04 | Current |  | Commercial | Heat Recovery Ventialation | Low Use | New Construction/Retrofit | space heating | High Efficient 55% Heat Recovery Ventilation Low Use Group (Office, Warehouse, School) | Ventilation with HRV Standalone | Ventilation without HRV |  |  | CFM | TRM Version 5.0 | 2020-11-12 | 0 | 1.36 | 0 | -1.56 | 0 | 0 | 0 | 8.28 | 14 | Low-Income | 0 | 1 | 1
COM-HRV-SH-371-04 | Current |  | Commercial | Heat Recovery Ventialation | Medium Use | New Construction/Retrofit | space heating | High Efficient 55% Heat Recovery Ventilation Medium Use Group (Hotel, Restaurant, Retail) | Ventilation with HRV Standalone | Ventilation without HRV |  |  | CFM | TRM Version 5.0 | 2020-11-12 | 0 | 2.13 | 0 | -2.44 | 0 | 0 | 0 | 8.28 | 14 | Low-Income | 0 | 1 | 1
COM-HRV-SH-373-04 | Current |  | Commercial | Heat Recovery Ventialation | High Use | New Construction/Retrofit | space heating | High Efficient 65% Heat Recovery Ventilation High Use Group (Multi-Residential, Health Care, Nursing Homes) | Ventilation with HRV Standalone | Ventilation without HRV |  |  | CFM | TRM Version 5.0 | 2020-11-12 | 0 | 4.54 | 0 | -4.39 | 0 | 0 | 0 | 9.28 | 14 | Low-Income | 0 | 1 | 1
COM-HRV-SH-375-04 | Current |  | Commercial | Heat Recovery Ventialation | Low Use | New Construction/Retrofit | space heating | High Efficient 65% Heat Recovery Ventilation Low Use Group (Office, Warehouse, School) | Ventilation with HRV Standalone | Ventilation without HRV |  |  | CFM | TRM Version 5.0 | 2020-11-12 | 0 | 1.61 | 0 | -1.56 | 0 | 0 | 0 | 9.28 | 14 | Low-Income | 0 | 1 | 1
COM-HRV-SH-377-04 | Current |  | Commercial | Heat Recovery Ventialation | Medium Use | New Construction/Retrofit | space heating | High Efficient 65% Heat Recovery Ventilation Medium Use Group (Hotel, Restaurant, Retail) | Ventilation with HRV Standalone | Ventilation without HRV |  |  | CFM | TRM Version 5.0 | 2020-11-12 | 0 | 2.52 | 0 | -2.44 | 0 | 0 | 0 | 9.28 | 14 | Low-Income | 0 | 1 | 1
COM-HRV-SH-379-04 | Current |  | Commercial | Heat Recovery Ventialation | High Use | New Construction/Retrofit | space heating | High Efficient 75% Heat Recovery Ventilation High Use Group (Multi-Residential, Health Care, Nursing Homes) | Ventilation with HRV Standalone | Ventilation without HRV |  |  | CFM | TRM Version 5.0 | 2020-11-12 | 0 | 5.24 | 0 | -4.39 | 0 | 0 | 0 | 10.28 | 14 | Low-Income | 0 | 1 | 1
COM-HRV-SH-381-04 | Current |  | Commercial | Heat Recovery Ventialation | Low Use | New Construction/Retrofit | space heating | High Efficient 75% Heat Recovery Ventilation Low Use Group (Office, Warehouse, School) | Ventilation with HRV Standalone | Ventilation without HRV |  |  | CFM | TRM Version 5.0 | 2020-11-12 | 0 | 1.86 | 0 | -1.56 | 0 | 0 | 0 | 10.28 | 14 | Low-Income | 0 | 1 | 1
COM-HRV-SH-383-04 | Current |  | Commercial | Heat Recovery Ventialation | Medium Use | New Construction/Retrofit | space heating | High Efficient 75% Heat Recovery Ventilation Medium Use Group (Hotel, Restaurant, Retail) | Ventilation with HRV Standalone | Ventilation without HRV |  |  | CFM | TRM Version 5.0 | 2020-11-12 | 0 | 2.91 | 0 | -2.44 | 0 | 0 | 0 | 10.28 | 14 | Low-Income | 0 | 1 | 1
COM-HRV-SH-385-04 | Current |  | Commercial | Heat Recovery Ventialation | High Use | New Construction/Retrofit | space heating | High Efficient 85% Heat Recovery Ventilation High Use Group (Multi-Residential, Health Care, Nursing Homes) | Ventilation with HRV Standalone | Ventilation without HRV |  |  | CFM | TRM Version 5.0 | 2020-11-12 | 0 | 5.93 | 0 | -4.39 | 0 | 0 | 0 | 11.28 | 14 | Low-Income | 0 | 1 | 1
COM-HRV-SH-387-04 | Current |  | Commercial | Heat Recovery Ventialation | Low Use | New Construction/Retrofit | space heating | High Efficient 85% Heat Recovery Ventilation Low Use Group (Office, Warehouse, School) | Ventilation with HRV Standalone | Ventilation without HRV |  |  | CFM | TRM Version 5.0 | 2020-11-12 | 0 | 2.11 | 0 | -1.56 | 0 | 0 | 0 | 11.28 | 14 | Low-Income | 0 | 1 | 1
COM-HRV-SH-389-04 | Current |  | Commercial | Heat Recovery Ventialation | Medium Use | New Construction/Retrofit | space heating | High Efficient 85% Heat Recovery Ventilation Medium Use Group (Hotel, Restaurant, Retail) | Ventilation with HRV Standalone | Ventilation without HRV |  |  | CFM | TRM Version 5.0 | 2020-11-12 | 0 | 3.3 | 0 | -2.44 | 0 | 0 | 0 | 11.28 | 14 | Low-Income | 0 | 1 | 1
COM-HRV-SH-391-04 | Current |  | Commercial | Heat Recovery Ventialation | Multi-Family, Health Care and Nursing Homes | New Construction/Retrofit | space heating | High Efficient 55% Heat Recovery Ventilation High Use Group (Multi-Residential, Health Care, Nursing Homes) | Ventilation with HRV Standalone | Ventilation without HRV |  |  | CFM | TRM Version 5.0 | 2020-11-12 | 0 | 3.84 | 0 | -4.39 | 0 | 0 | 0 | 8.28 | 14 | Low-Income | 0 | 1 | 1
COM-HRV-SH-393-04 | Current |  | Commercial | Heat Recovery Ventialation | Hotels | New Construction/Retrofit | space heating | High Efficient 55% Heat Recovery Ventilation Medium Use Group (Hotel, Restaurant, Retail) | Ventilation with HRV Standalone | Ventilation without HRV |  |  | CFM | TRM Version 5.0 | 2020-11-12 | 0 | 2.74 | 0 | -3.14 | 0 | 0 | 0 | 8.28 | 14 | Low-Income | 0 | 1 | 1
COM-HRV-SH-395-04 | Current |  | Commercial | Heat Recovery Ventialation | Restaurant | New Construction/Retrofit | space heating | High Efficient 55% Heat Recovery Ventilation Medium Use Group (Hotel, Restaurant, Retail) | Ventilation with HRV Standalone | Ventilation without HRV |  |  | CFM | TRM Version 5.0 | 2020-11-12 | 0 | 1.99 | 0 | -2.28 | 0 | 0 | 0 | 8.28 | 14 | Low-Income | 0 | 1 | 1
COM-HRV-SH-397-04 | Current |  | Commercial | Heat Recovery Ventialation | Retail | New Construction/Retrofit | space heating | High Efficient 55% Heat Recovery Ventilation Medium Use Group (Hotel, Restaurant, Retail) | Ventilation with HRV Standalone | Ventilation without HRV |  |  | CFM | TRM Version 5.0 | 2020-11-12 | 0 | 1.67 | 0 | -1.91 | 0 | 0 | 0 | 8.28 | 14 | Low-Income | 0 | 1 | 1
COM-HRV-SH-399-04 | Current |  | Commercial | Heat Recovery Ventialation | Office | New Construction/Retrofit | space heating | High Efficient 55% Heat Recovery Ventilation Low Use Group (Office, Warehouse, School) | Ventilation with HRV Standalone | Ventilation without HRV |  |  | CFM | TRM Version 5.0 | 2020-11-12 | 0 | 1.46 | 0 | -1.67 | 0 | 0 | 0 | 8.28 | 14 | Low-Income | 0 | 1 | 1
COM-HRV-SH-401-04 | Current |  | Commercial | Heat Recovery Ventialation | Warehouse | New Construction/Retrofit | space heating | High Efficient 55% Heat Recovery Ventilation Low Use Group (Office, Warehouse, School) | Ventilation with HRV Standalone | Ventilation without HRV |  |  | CFM | TRM Version 5.0 | 2020-11-12 | 0 | 1.39 | 0 | -1.6 | 0 | 0 | 0 | 8.28 | 14 | Low-Income | 0 | 1 | 1
COM-HRV-SH-403-04 | Current |  | Commercial | Heat Recovery Ventialation | School | New Construction/Retrofit | space heating | High Efficient 55% Heat Recovery Ventilation Low Use Group (Office, Warehouse, School) | Ventilation with HRV Standalone | Ventilation without HRV |  |  | CFM | TRM Version 5.0 | 2020-11-12 | 0 | 1.23 | 0 | -1.41 | 0 | 0 | 0 | 8.28 | 14 | Low-Income | 0 | 1 | 1
COM-HRV-SH-405-04 | Current |  | Commercial | Heat Recovery Ventialation | Multi-Family, Health Care and Nursing Homes | New Construction/Retrofit | space heating | High Efficient 65% Heat Recovery Ventilation High Use Group (Multi-Residential, Health Care, Nursing Homes) | Ventilation with HRV Standalone | Ventilation without HRV |  |  | CFM | TRM Version 5.0 | 2020-11-12 | 0 | 4.54 | 0 | -4.39 | 0 | 0 | 0 | 9.28 | 14 | Low-Income | 0 | 1 | 1
COM-HRV-SH-407-04 | Current |  | Commercial | Heat Recovery Ventialation | Hotels | New Construction/Retrofit | space heating | High Efficient 65% Heat Recovery Ventilation Medium Use Group (Hotel, Restaurant, Retail) | Ventilation with HRV Standalone | Ventilation without HRV |  |  | CFM | TRM Version 5.0 | 2020-11-12 | 0 | 3.24 | 0 | -3.14 | 0 | 0 | 0 | 9.28 | 14 | Low-Income | 0 | 1 | 1
COM-HRV-SH-409-04 | Current |  | Commercial | Heat Recovery Ventialation | Restaurant | New Construction/Retrofit | space heating | High Efficient 65% Heat Recovery Ventilation Medium Use Group (Hotel, Restaurant, Retail) | Ventilation with HRV Standalone | Ventilation without HRV |  |  | CFM | TRM Version 5.0 | 2020-11-12 | 0 | 2.35 | 0 | -2.28 | 0 | 0 | 0 | 9.28 | 14 | Low-Income | 0 | 1 | 1
COM-HRV-SH-411-04 | Current |  | Commercial | Heat Recovery Ventialation | Retail | New Construction/Retrofit | space heating | High Efficient 65% Heat Recovery Ventilation Medium Use Group (Hotel, Restaurant, Retail) | Ventilation with HRV Standalone | Ventilation without HRV |  |  | CFM | TRM Version 5.0 | 2020-11-12 | 0 | 1.97 | 0 | -1.91 | 0 | 0 | 0 | 9.28 | 14 | Low-Income | 0 | 1 | 1
COM-HRV-SH-413-04 | Current |  | Commercial | Heat Recovery Ventialation | Office | New Construction/Retrofit | space heating | High Efficient 65% Heat Recovery Ventilation Low Use Group (Office, Warehouse, School) | Ventilation with HRV Standalone | Ventilation without HRV |  |  | CFM | TRM Version 5.0 | 2020-11-12 | 0 | 1.73 | 0 | -1.67 | 0 | 0 | 0 | 9.28 | 14 | Low-Income | 0 | 1 | 1
COM-HRV-SH-415-04 | Current |  | Commercial | Heat Recovery Ventialation | Warehouse | New Construction/Retrofit | space heating | High Efficient 65% Heat Recovery Ventilation Low Use Group (Office, Warehouse, School) | Ventilation with HRV Standalone | Ventilation without HRV |  |  | CFM | TRM Version 5.0 | 2020-11-12 | 0 | 1.65 | 0 | -1.6 | 0 | 0 | 0 | 9.28 | 14 | Low-Income | 0 | 1 | 1
COM-HRV-SH-417-04 | Current |  | Commercial | Heat Recovery Ventialation | School | New Construction/Retrofit | space heating | High Efficient 65% Heat Recovery Ventilation Low Use Group (Office, Warehouse, School) | Ventilation with HRV Standalone | Ventilation without HRV |  |  | CFM | TRM Version 5.0 | 2020-11-12 | 0 | 1.46 | 0 | -1.41 | 0 | 0 | 0 | 9.28 | 14 | Low-Income | 0 | 1 | 1
COM-HRV-SH-419-04 | Current |  | Commercial | Heat Recovery Ventialation | Multi-Family, Health Care and Nursing Homes | New Construction/Retrofit | space heating | High Efficient 75% Heat Recovery Ventilation High Use Group (Multi-Residential, Health Care, Nursing Homes) | Ventilation with HRV Standalone | Ventilation without HRV |  |  | CFM | TRM Version 5.0 | 2020-11-12 | 0 | 5.24 | 0 | -4.39 | 0 | 0 | 0 | 10.28 | 14 | Low-Income | 0 | 1 | 1
COM-HRV-SH-421-04 | Current |  | Commercial | Heat Recovery Ventialation | Hotels | New Construction/Retrofit | space heating | High Efficient 75% Heat Recovery Ventilation Medium Use Group (Hotel, Restaurant, Retail) | Ventilation with HRV Standalone | Ventilation without HRV |  |  | CFM | TRM Version 5.0 | 2020-11-12 | 0 | 3.74 | 0 | -3.14 | 0 | 0 | 0 | 10.28 | 14 | Low-Income | 0 | 1 | 1
COM-HRV-SH-423-04 | Current |  | Commercial | Heat Recovery Ventialation | Restaurant | New Construction/Retrofit | space heating | High Efficient 75% Heat Recovery Ventilation Medium Use Group (Hotel, Restaurant, Retail) | Ventilation with HRV Standalone | Ventilation without HRV |  |  | CFM | TRM Version 5.0 | 2020-11-12 | 0 | 2.71 | 0 | -2.28 | 0 | 0 | 0 | 10.28 | 14 | Low-Income | 0 | 1 | 1
COM-HRV-SH-425-04 | Current |  | Commercial | Heat Recovery Ventialation | Retail | New Construction/Retrofit | space heating | High Efficient 75% Heat Recovery Ventilation Medium Use Group (Hotel, Restaurant, Retail) | Ventilation with HRV Standalone | Ventilation without HRV |  |  | CFM | TRM Version 5.0 | 2020-11-12 | 0 | 2.28 | 0 | -1.91 | 0 | 0 | 0 | 10.28 | 14 | Low-Income | 0 | 1 | 1
COM-HRV-SH-427-04 | Current |  | Commercial | Heat Recovery Ventialation | Office | New Construction/Retrofit | space heating | High Efficient 75% Heat Recovery Ventilation Low Use Group (Office, Warehouse, School) | Ventilation with HRV Standalone | Ventilation without HRV |  |  | CFM | TRM Version 5.0 | 2020-11-12 | 0 | 1.99 | 0 | -1.67 | 0 | 0 | 0 | 10.28 | 14 | Low-Income | 0 | 1 | 1
COM-HRV-SH-429-04 | Current |  | Commercial | Heat Recovery Ventialation | Warehouse | New Construction/Retrofit | space heating | High Efficient 75% Heat Recovery Ventilation Low Use Group (Office, Warehouse, School) | Ventilation with HRV Standalone | Ventilation without HRV |  |  | CFM | TRM Version 5.0 | 2020-11-12 | 0 | 1.9 | 0 | -1.6 | 0 | 0 | 0 | 10.28 | 14 | Low-Income | 0 | 1 | 1
COM-HRV-SH-431-04 | Current |  | Commercial | Heat Recovery Ventialation | School | New Construction/Retrofit | space heating | High Efficient 75% Heat Recovery Ventilation Low Use Group (Office, Warehouse, School) | Ventilation with HRV Standalone | Ventilation without HRV |  |  | CFM | TRM Version 5.0 | 2020-11-12 | 0 | 1.68 | 0 | -1.41 | 0 | 0 | 0 | 10.28 | 14 | Low-Income | 0 | 1 | 1
COM-HRV-SH-433-04 | Current |  | Commercial | Heat Recovery Ventialation | Multi-Family, Health Care and Nursing Homes | New Construction/Retrofit | space heating | High Efficient 85% Heat Recovery Ventilation High Use Group (Multi-Residential, Health Care, Nursing Homes) | Ventilation with HRV Standalone | Ventilation without HRV |  |  | CFM | TRM Version 5.0 | 2020-11-12 | 0 | 5.93 | 0 | -4.39 | 0 | 0 | 0 | 11.28 | 14 | Low-Income | 0 | 1 | 1
COM-HRV-SH-435-04 | Current |  | Commercial | Heat Recovery Ventialation | Hotels | New Construction/Retrofit | space heating | High Efficient 85% Heat Recovery Ventilation Medium Use Group (Hotel, Restaurant, Retail) | Ventilation with HRV Standalone | Ventilation without HRV |  |  | CFM | TRM Version 5.0 | 2020-11-12 | 0 | 4.24 | 0 | -3.14 | 0 | 0 | 0 | 11.28 | 14 | Low-Income | 0 | 1 | 1
COM-HRV-SH-437-04 | Current |  | Commercial | Heat Recovery Ventialation | Restaurant | New Construction/Retrofit | space heating | High Efficient 85% Heat Recovery Ventilation Medium Use Group (Hotel, Restaurant, Retail) | Ventilation with HRV Standalone | Ventilation without HRV |  |  | CFM | TRM Version 5.0 | 2020-11-12 | 0 | 3.07 | 0 | -2.28 | 0 | 0 | 0 | 11.28 | 14 | Low-Income | 0 | 1 | 1
COM-HRV-SH-439-04 | Current |  | Commercial | Heat Recovery Ventialation | Retail | New Construction/Retrofit | space heating | High Efficient 85% Heat Recovery Ventilation Medium Use Group (Hotel, Restaurant, Retail) | Ventilation with HRV Standalone | Ventilation without HRV |  |  | CFM | TRM Version 5.0 | 2020-11-12 | 0 | 2.58 | 0 | -1.91 | 0 | 0 | 0 | 11.28 | 14 | Low-Income | 0 | 1 | 1
COM-HRV-SH-441-04 | Current |  | Commercial | Heat Recovery Ventialation | Office | New Construction/Retrofit | space heating | High Efficient 85% Heat Recovery Ventilation Low Use Group (Office, Warehouse, School) | Ventilation with HRV Standalone | Ventilation without HRV |  |  | CFM | TRM Version 5.0 | 2020-11-12 | 0 | 2.26 | 0 | -1.67 | 0 | 0 | 0 | 11.28 | 14 | Low-Income | 0 | 1 | 1
COM-HRV-SH-443-04 | Current |  | Commercial | Heat Recovery Ventialation | Warehouse | New Construction/Retrofit | space heating | High Efficient 85% Heat Recovery Ventilation Low Use Group (Office, Warehouse, School) | Ventilation with HRV Standalone | Ventilation without HRV |  |  | CFM | TRM Version 5.0 | 2020-11-12 | 0 | 2.15 | 0 | -1.6 | 0 | 0 | 0 | 11.28 | 14 | Low-Income | 0 | 1 | 1
COM-HRV-SH-445-04 | Current |  | Commercial | Heat Recovery Ventialation | School | New Construction/Retrofit | space heating | High Efficient 85% Heat Recovery Ventilation Low Use Group (Office, Warehouse, School) | Ventilation with HRV Standalone | Ventilation without HRV |  |  | CFM | TRM Version 5.0 | 2020-11-12 | 0 | 1.91 | 0 | -1.41 | 0 | 0 | 0 | 11.28 | 14 | Low-Income | 0 | 1 | 1
COM-CM-SH-498-04 | Current |  | Commercial | Condensing Make Up Air Unit | Commercial | New Construction/Natural Replacement | space heating | Condensing Make Up Air Unit (MUA) - Commercial | VFD | Conventional MUA | 80% Thermal Efficiency |  | CFM | TRM Version 5.0 | 2020-11-12 | 0 | 2.03 | 0 | 2.04 | 0 | 0 | 870 | 1.02 | 20 | Low-Income | 0 | 1 | 1
COM-CM-SH-501-04 | Current |  | Commercial | Condensing Make Up Air Unit | Multi-Residential and Long Term Care | New Construction/Natural Replacement | space heating | Condensing Make Up Air Unit (MUA) - Commercial | VFD | Conventional MUA | 80% Thermal Efficiency |  | CFM | TRM Version 5.0 | 2020-11-12 | 0 | 3 | 0 | 2.3 | 0 | 0 | 870 | 1.02 | 20 | Low-Income | 0 | 1 | 1
MRS-SH-WH-569-02 | Current |  | Commercial | Showerhead | Multi-residential | New Construction | water heating | Low-flow showerhead | 1.25 GPM |  | 2.0 GPM | unit |  | TRM Version 6.0 | 2021-12-16 | 23.2 | 0 | 0 | 0 | 7775 | 0 | actual cost |  | 10 | Low-Income | 0 | 0.8576 | 1
MRS-SH-WH-571-02 | Current |  | Commercial | Showerhead | Multi-residential | Retrofit | water heating | Low-flow showerhead | 1.25 GPM | Average existing stock | 2.5 GPM | unit |  | TRM Version 6.0 | 2021-12-16 | 38.7 | 0 | 0 | 0 | 11734 | 0 | actual cost |  | 10 | Low-Income | 0 | 0.8576 | 1
MRS-SH-WH-570-02 | Current |  | Commercial | Showerhead | Multi-residential | New Construction | water heating | Low-flow showerhead | 1.50 GPM |  | 2.0 GPM | unit |  | TRM Version 6.0 | 2021-12-16 | 15.5 | 0 | 0 | 0 | 4107 | 0 | actual cost |  | 10 | Low-Income | 0 | 0.8576 | 1
MRS-SH-WH-572-02 | Current |  | Commercial | Showerhead | Multi-residential | Retrofit | water heating | Low-flow showerhead | 1.50 GPM | Average existing stock | 2.5 GPM | unit |  | TRM Version 6.0 | 2021-12-16 | 31 | 0 | 0 | 0 | 8068 | 0 | actual cost |  | 10 | Low-Income | 0 | 0.8576 | 1
COM-CMB-FS-621-04 | Current |  | Commercial | Combination Oven |  | New Construction/Natural Replacement | food service | Energy Star Combination Oven | Energy Star Rated Combiniation Oven, 15-28 pan | Conventional combination oven |  | unit |  | TRM Version 6.0 | 2021-12-16 | 1295 | 0 | 4747 | 0 | 51684 | 0 | 5007 | 0 | 12 | Low-Income | 0 | 1 | 1
COM-CMB-FS-622-04 | Current |  | Commercial | Combination Oven |  | New Construction/Natural Replacement | food service | Energy Star Combination Oven | Energy Star Rated Combiniation Oven, 29+ pan | Conventional combination oven |  | unit |  | TRM Version 6.0 | 2021-12-16 | 1048 | 0 | 485 | 0 | 599459 | 0 | 8507 | 0 | 12 | Low-Income | 0 | 1 | 1
COM-CMB-FS-623-04 | Current |  | Commercial | Combination Oven |  | New Construction/Natural Replacement | food service | Energy Star Combination Oven | Energy Star Rated Combiniation Oven, average | Conventional combination oven |  | unit |  | TRM Version 6.0 | 2021-12-16 | 1186 | 0 | 2088 | 0 | 145120 | 0 | 4440 | 0 | 12 | Low-Income | 0 | 1 | 1
COM-CO-FS-520-04 | Current |  | Commercial | Convection Ovens |  | New Construction/Natural Replacement | food service | Energy Star Convection Ovens | Energy Star Rated Convection Oven (Full Size) | Conventional Convection Oven (Full Size) |  | unit |  | TRM Version 6.0 | 2021-12-16 | 954 | 0 | 44.2 | 0 | 0 | 0 | 1200 | 0 | 12 | Low-Income | 0 | 1 | 1
COM-RO-FS-651-04 | Current |  | Commercial | Rack Oven |  | New Construction/Natural Replacement | food service | ENERGY STAR Rack Oven | Energy Star Rated Rack Oven, Double | Conventiona rack oven |  | unit |  | TRM Version 6.0 | 2021-12-16 | 1187 | 0 | 1858 | 0 | 0 | 0 | 2591 | 0 | 12 | Low-Income | 0 | 1 | 1
COM-RO-FS-650-04 | Current |  | Commercial | Rack Oven |  | New Construction/Natural Replacement | food service | ENERGY STAR Rack Oven | Energy Star Rated Rack Oven, Single | Conventiona rack oven |  | unit |  | TRM Version 6.0 | 2021-12-16 | 915 | 0 | 826 | 0 | 0 | 0 | 1544 | 0 | 12 | Low-Income | 0 | 1 | 1
COM-OL-WH-329-04 | Current |  | Commercial | Ozone Laundry |  | New Construction/Retrofit | water heating | Commercial Ozone Laundry Treatment | Ozone Treatment Tunnel Washer <= 120 lbs | Commercial laundry with no ozone treatment system |  |  | lbs/yr | TRM Version 7.0 | 2022-11-30 | 0 | 0.0295 | 0 | 0.0015 | 0 | 1.29 | 71429 | 0 | 15 | Low-Income | 0 | 1 | 1
COM-OL-WH-331-04 | Current |  | Commercial | Ozone Laundry |  | New Construction/Retrofit | water heating | Commercial Ozone Laundry Treatment | Ozone Treatment Tunnel Washer=> 500 lbs | Commercial laundry with no ozone treatment system |  |  | lbs/yr | TRM Version 7.0 | 2022-11-30 | 0 | 0.0295 | 0 | 0.0015 | 0 | 1.29 | 228571 | 0 | 15 | Low-Income | 0 | 1 | 1
COM-OL-WH-330-04 | Current |  | Commercial | Ozone Laundry |  | New Construction/Retrofit | water heating | Commercial Ozone Laundry Treatment | Ozone Treatment Tunnel Washer 121 lbs to 499 lbs | Commercial laundry with no ozone treatment system |  |  | lbs/yr | TRM Version 7.0 | 2022-11-30 | 0 | 0.0295 | 0 | 0.0015 | 0 | 1.29 | 150000 | 0 | 15 | Low-Income | 0 | 1 | 1
COM-OL-WH-326-04 | Current |  | Commercial | Ozone Laundry |  | New Construction/Retrofit | water heating | Commercial Ozone Laundry Treatment | Ozone Treatment Washer extractor =< 60 lbs | Commercial laundry with no ozone treatment system |  |  | lbs/yr | TRM Version 7.0 | 2022-11-30 | 0 | 0.0376 | 0 | 0.00211 | 0 | 2.1 | 15714 | 0 | 15 | Low-Income | 0 | 1 | 1
COM-OL-WH-327-04 | Current |  | Commercial | Ozone Laundry |  | New Construction/Retrofit | water heating | Commercial Ozone Laundry Treatment | Ozone Treatment Washer extractor 61 lbs to 499 lbs | Commercial laundry with no ozone treatment system |  |  | lbs/yr | TRM Version 7.0 | 2022-11-30 | 0 | 0.0376 | 0 | 0.00211 | 0 | 2.1 | 35714 | 0 | 15 | Low-Income | 0 | 1 | 1
COM-OL-WH-328-04 | Current |  | Commercial | Ozone Laundry |  | New Construction/Retrofit | water heating | Commercial Ozone Laundry Treatment | Ozone Treatment Washer extractor=> 500 lbs | Commercial laundry with no ozone treatment system |  |  | lbs/yr | TRM Version 7.0 | 2022-11-30 | 0 | 0.0376 | 0 | 0.00211 | 0 | 2.1 | 44286 | 0 | 15 | Low-Income | 0 | 1 | 1
COM-CMB-FS-620-04 | Current |  | Commercial | Combination Oven |  | New Construction/Natural Replacement | food service | Energy Star Combination Oven | Energy Star Rated Combination Oven, 6-14 pan | Conventional combination oven |  | unit |  | TRM Version 6.0 | 2021-12-16 | 1104 | 0 | 72 | 0 | 209664 | 0 | 3941 | 0 | 12 | Low-Income | 0 | 1 | 1
COM-GR-FS-800-01 | Current |  | Commercial | Griddles |  | New Construction/Natural Replacement | food service | Energy Star Griddle | ENERGY STAR Certified Griddle | Non-ENERGY STAR Griddle |  |  | ft | TRM Version 7.0 | 2022-11-30 | 0 | 439 | 0 | 0 | 0 | 0 | 0 | 1096 | 12 | Low-Income | 0 | 1 | 1
COM-GR-FS-801-01 | Current |  | Commercial | Griddles |  | New Construction/Natural Replacement | food service | Energy Star Griddle | ENERGY STAR Certified Griddle | Non-ENERGY STAR Griddle |  | unit |  | TRM Version 7.0 | 2022-11-30 | 1974 | 0 | 0 | 0 | 0 | 0 | 4581 | 0 | 12 | Low-Income | 0 | 1 | 1
COM-FR-FS-325-04 | Current | Split measure into two Vat sizes | Commercial | Fryer |  | New Construction/Natural Replacement | food service | Energy Star Fryer, Standard Vat | Energy Star Rated Fryer | Non-Energy Star rated Fryer |  | unit |  | TRM Version 7.0 | 2022-11-30 | 1466 | 0 | 0 | 0 | 0 | 0 | 2657 | 0 | 12 | Low-Income | 0 | 1 | 1
COM-FR-FS-326-04 | Current | Split measure into two Vat sizes | Commercial | Fryer |  | New Construction/Natural Replacement | food service | Energy Star Fryer, Large Vat | Energy Star Rated Fryer | Non-Energy Star rated Fryer |  | unit |  | TRM Version 7.0 | 2022-11-30 | 1709 | 0 | 0 | 0 | 0 | 0 | 3113 | 0 | 12 | Low-Income | 0 | 1 | 1
COM-SC-FS-325-04 | Current |  | Commercial | Steam Cookers |  | New Construction/Natural Replacement | food service | Energy Star Steam Cookers | Energy Star Rated Steam Cooker | Boiler-based steam cooker |  | unit |  | TRM Version 7.0 | 2022-11-30 | 8461 | 0 | 0 | 0 | 1109458 | 0 | 3045 | 0 | 12 | Low-Income | 0 | 1 | 1
COM-CNB-FS-810-01 | Current | New measure in TRM V7.0 | Commercial | Conveyor Broiler |  | New Construction/Natural Replacement | food service | Energy-Efficient Conveyor Broiler, <22" width | high-efficiency conveyor broiler with a catalyst and an idle input rate less than the rates listed below or a dual stage or modulating gas valve with a capability of throttling the input rate below the idle rates <40,000 Btu/h | Conventional Conveyor Broiler |  | unit |  | TRM Version 7.0 | 2022-11-30 | 1954 | 0 | 2443 | 0 | 0 | 0 | 3154 | 0 | 12 | Low-Income | 0.05 | 1 | 1
COM-CNB-FS-811-01 | Current | New measure in TRM V7.0 | Commercial | Conveyor Broiler |  | New Construction/Natural Replacement | food service | Energy-Efficient Conveyor Broiler, 22" - 26" width | high-efficiency conveyor broiler with a catalyst and an idle input rate less than the rates listed below or a dual stage or modulating gas valve with a capability of throttling the input rate below the idle rates <60,000 Btu/h | Conventional Conveyor Broiler |  | unit |  | TRM Version 7.0 | 2022-11-30 | 3070 | 0 | 3839 | 0 | 0 | 0 | 3933 | 0 | 12 | Low-Income | 0.05 | 1 | 1
COM-CNB-FS-812-01 | Current | New measure in TRM V7.0 | Commercial | Conveyor Broiler |  | New Construction/Natural Replacement | food service | Energy-Efficient Conveyor Broiler, > 26" width | high-efficiency conveyor broiler with a catalyst and an idle input rate less than the rates listed below or a dual stage or modulating gas valve with a capability of throttling the input rate below the idle rates <70,000 Btu/h | Conventional Conveyor Broiler |  | unit |  | TRM Version 7.0 | 2022-11-30 | 3768 | 0 | 4712 | 0 | 0 | 0 | 4586 | 0 | 12 | Low-Income | 0.05 | 1 | 1
COM-CNO-FS-806-01 | Current | New measure in TRM V7.0 | Commercial | Conveyor Oven |  | New Construction/Natural Replacement | food service | Energy-Efficient Conveyor Oven, large ≥ 1520 sq in | Large Conveyor Oven Chamber Area ≥ 1520 sq in, 45% cooking efficiency | Conventional Conveyor Oven |  | unit |  | TRM Version 7.0 | 2022-11-30 | 1519 | 0 | 2601 | 0 | 0 | 0 | 1994 | 0 | 12 | Low-Income | 0.05 | 1 | 1
COM-UB-FS-332-04 | Current |  | Commercial | Under-Fired Broilers |  | New Construction/Natural Replacement | food service | High Efficiency Under-Fired Broilers - 3 foot | low idle energy rate (≤22,000 Btu/hr per linear foot) | Conventional Efficiency Under-Fired Broiler | conventional underfired broiler | unit |  | TRM Version 7.0 | 2022-11-30 | 2636 | 0 | 0 | 0 | 0 | 0 | 1868 | 0 | 12 | Low-Income | 0 | 1 | 1
COM-UB-FS-333-04 | Current |  | Commercial | Under-Fired Broilers |  | New Construction/Natural Replacement | food service | High Efficiency Under-Fired Broilers - 4 foot | low idle energy rate (≤22,000 Btu/hr per linear foot) | Conventional Efficiency Under-Fired Broiler | conventional underfired broiler | unit |  | TRM Version 7.0 | 2022-11-30 | 3515 | 0 | 0 | 0 | 0 | 0 | 2948 | 0 | 12 | Low-Income | 0 | 1 | 1
COM-UB-FS-334-04 | Current |  | Commercial | Under-Fired Broilers |  | New Construction/Natural Replacement | food service | High Efficiency Under-Fired Broilers - 5 foot | low idle energy rate (≤22,000 Btu/hr per linear foot) | Conventional Efficiency Under-Fired Broiler | conventional underfired broiler | unit |  | TRM Version 7.0 | 2022-11-30 | 4393 | 0 | 0 | 0 | 0 | 0 | 3820 | 0 | 12 | Low-Income | 0 | 1 | 1
COM-UB-FS-335-04 | Current |  | Commercial | Under-Fired Broilers |  | New Construction/Natural Replacement | food service | High Efficiency Under-Fired Broilers - 6 foot | low idle energy rate (≤22,000 Btu/hr per linear foot) | Conventional Efficiency Under-Fired Broiler | conventional underfired broiler | unit |  | TRM Version 7.0 | 2022-11-30 | 5272 | 0 | 0 | 0 | 0 | 0 | 4134 | 0 | 12 | Low-Income | 0 | 1 | 1
COM-UB-FS-336-04 | Current |  | Commercial | Under-Fired Broilers |  | New Construction/Natural Replacement | food service | High Efficiency Under-Fired Broilers - 2 foot | low idle energy rate (≤22,000 Btu/hr per linear foot) | Conventional Efficiency Under-Fired Broiler | conventional underfired broiler | unit |  | TRM Version 7.0 | 2022-11-30 | 1757 | 0 | 0 | 0 | 0 | 0 | 1264 | 0 | 12 | Low-Income | 0 | 1 | 1
COM-DW-WH-555-02 | Current | revised from TRM Version 5.0: natural gas, electric savings, and water savings | Commercial | Dishwasher |  | New Construction/Natural Replacement | water heating | Energy Star Dishwasher | Multi Tank Conveyor - High Temperature | Non-Energy Star Dishwasher |  | unit |  | TRM Version 7.0 | 2022-11-30 | 2970 | 0 | 14386 | 0 | 437533 | 0 | 1216 | 0 | 20 | Low-Income | 0 | 1 | 1
COM-DW-WH-556-02 | Current | revised from TRM Version 5.0: natural gas, electric savings, and water savings | Commercial | Dishwasher |  | New Construction/Natural Replacement | water heating | Energy Star Dishwasher | Multi Tank Conveyor - Low Temperature | Non-Energy Star Dishwasher |  | unit |  | TRM Version 7.0 | 2022-11-30 | 3447 | 0 | 3375 | 0 | 507851 | 0 | 1216 | 0 | 20 | Low-Income | 0 | 1 | 1
COM-DW-WH-553-02 | Current | revised from TRM Version 5.0: natural gas, electric savings, and water savings | Commercial | Dishwasher |  | New Construction/Natural Replacement | water heating | Energy Star Dishwasher | Single Tank Conveyor – High Temperature | Non-Energy Star Dishwasher |  | unit |  | TRM Version 7.0 | 2022-11-30 | 1167 | 0 | 7599 | 0 | 171888 | 0 | 2570 | 0 | 20 | Low-Income | 0 | 1 | 1
COM-DW-WH-554-02 | Current | revised from TRM Version 5.0: natural gas, electric savings, and water savings | Commercial | Dishwasher |  | New Construction/Natural Replacement | water heating | Energy Star Dishwasher | Single Tank Conveyor - Low Temperature | Non-Energy Star Dishwasher |  | unit |  | TRM Version 7.0 | 2022-11-30 | 2546 | 0 | 3474 | 0 | 375028 | 0 | 0 | 0 | 20 | Low-Income | 0 | 1 | 1
COM-CNO-FS-805-01 | Current | New measure in TRM V7.0 | Commercial | Conveyor Oven |  | New Construction/Natural Replacement | food service | Energy-Efficient Conveyor Oven, small < 1520 sq in | Small Conveyor Oven Chamber Area <1520 sq in, 37% cooking efficiency | Conventional Conveyor Oven |  | unit |  | TRM Version 7.0 | 2022-11-30 | 562 | 0 | 619 | 0 | 0 | 0 | 859 | 0 | 12 | Low-Income | 0.05 | 1 | 1
COM-DW-WH-551-02 | Current | revised from TRM Version 5.0: natural gas, electric savings, and water savings | Commercial | Dishwasher |  | New Construction/Natural Replacement | water heating | Energy Star Dishwasher | Stationary Single Tank Door – High Temperature | Non-Energy Star Dishwasher |  | unit |  | TRM Version 7.0 | 2022-11-30 | 1262 | 0 | 6032 | 0 | 185951 | 0 | 1247 | 0 | 15 | Low-Income | 0 | 1 | 1
COM-DW-WH-552-02 | Current | revised from TRM Version 5.0: natural gas, electric savings, and water savings | Commercial | Dishwasher |  | New Construction/Natural Replacement | water heating | Energy Star Dishwasher | Stationary Single Tank Door – Low Temperature | Non-Energy Star Dishwasher |  | unit |  | TRM Version 7.0 | 2022-11-30 | 2846 | 0 | 946 | 0 | 419302 | 0 | 830 | 0 | 15 | Low-Income | 0 | 1 | 1
COM-DW-WH-549-02 | Current | revised from TRM Version 5.0: natural gas, electric savings, and water savings | Commercial | Dishwasher |  | New Construction/Natural Replacement | water heating | Energy Star Dishwasher | Undercounter – High Temperature | Non-Energy Star Dishwasher |  | unit |  | TRM Version 7.0 | 2022-11-30 | 285 | 0 | 2767 | 0 | 41995 | 0 | 2538 | 0 | 10 | Low-Income | 0 | 1 | 1
COM-DW-WH-550-02 | Current | revised from TRM Version 5.0: natural gas, electric savings, and water savings | Commercial | Dishwasher |  | New Construction/Natural Replacement | water heating | Energy Star Dishwasher | Undercounter – Low Temperature | Non-Energy Star Dishwasher |  | unit |  | TRM Version 7.0 | 2022-11-30 | 438 | 0 | 1405 | 0 | 64458 | 0 | 293 | 0 | 10 | Low-Income | 0 | 1 | 1
COM-DK-SH-524-02 | Current | Updated savings values | Commercial | Demand Control Kitchen Ventilation |  | New Construction/Natural Replacement | space heating | Demand Control Kitchen Ventilation | 0 - 5,000 CFM | Constant Volume Kitchen Ventilation |  | unit |  | TRM Version 8.0 | 2024-04-30 | 4307 | 0 | 15865 | 0 | 0 | 0 | 5490 | 0 | 15 | Low-Income | 0 | 1 | 1
COM-DK-SH-526-02 | Current | Updated savings values | Commercial | Demand Control Kitchen Ventilation |  | New Construction/Natural Replacement | space heating | Demand Control Kitchen Ventilation | 10,001 - 15,000 CFM | Constant Volume Kitchen Ventilation |  | unit |  | TRM Version 8.0 | 2024-04-30 | 17947 | 0 | 29586 | 0 | 0 | 0 | 22875 | 0 | 15 | Low-Income | 0 | 1 | 1
COM-DK-SH-525-02 | Current | Updated savings values | Commercial | Demand Control Kitchen Ventilation |  | New Construction/Natural Replacement | space heating | Demand Control Kitchen Ventilation | 5,001 - 10,000 CFM | Constant Volume Kitchen Ventilation |  | unit |  | TRM Version 8.0 | 2024-04-30 | 10768 | 0 | 22364 | 0 | 0 | 0 | 13725 | 0 | 15 | Low-Income | 0 | 1 | 1
COM-CU-SH-515-04 | Current | Updated size descriptions in eTRM to match TRM, entered energy savings that appear to be new from last TRM | Commercial | Condensing Unit Heater |  | Natural Replacement | space heating | Condensing Unit Heater | 125-225 kBtu/hr 90% Thermal Efficiency, 89% Annual Efficiency | Non-Condensing Unit Heater | 80% Thermal Efficiency, 78% Annual Efficiency |  | kBtu/hr input capacity | TRM Version 8.0 | 2024-04-30 | 0 | 6.52 | -438 | 0 | 0 | 0 | 0 | 16.07 | 18 | Low-Income | 0 | 1 | 1
COM-CU-SH-516-04 | Current | Entered energy savings that appear to be new from last TRM | Commercial | Condensing Unit Heater |  | Natural Replacement | space heating | Condensing Unit Heater | 225-300 kBtu/hr 90% Thermal Efficiency, 89% Annual Efficiency | Non-Condensing Unit Heater | 80% Thermal Efficiency, 78% Annual Efficiency |  | kBtu/hr input capacity | TRM Version 8.0 | 2024-04-30 | 0 | 6.52 | -451 | 0 | 0 | 0 | 0 | 16.07 | 18 | Low-Income | 0 | 1 | 1
COM-CU-SH-514-04 | Current | Updated size descriptions in eTRM to match TRM, entered energy savings that appear to be new from last TRM | Commercial | Condensing Unit Heater |  | Natural Replacement | space heating | Condensing Unit Heater | 30-125 kBtu/hr - 90% Thermal Efficiency, 89% Annual Efficiency | Non-Condensing Unit Heater | 80% Thermal Efficiency, 78% Annual Efficiency |  | kBtu/hr input capacity | TRM Version 8.0 | 2024-04-30 | 0 | 6.52 | -244 | 0 | 0 | 0 | 0 | 16.07 | 18 | Low-Income | 0 | 1 | 1
COM-CU-SH-518-04 | Current | Updated size descriptions in eTRM to match TRM, entered energy savings that appear to be new from last TRM | Commercial | Condensing Unit Heater |  | New Construction | space heating | Condensing Unit Heater | 125-225 kBtu/hr 90% Thermal Efficiency, 89% Annual Efficiency | Non-Condensing Unit Heater | 80% Thermal Efficiency, 78% Annual Efficiency |  | kBtu/hr input capacity | TRM Version 8.0 | 2024-04-30 | 0 | 4.62 | -310 | 0 | 0 | 0 | 0 | 16.07 | 18 | Low-Income | 0 | 1 | 1
COM-CU-SH-519-04 | Current | Entered energy savings that appear to be new from last TRM | Commercial | Condensing Unit Heater |  | New Construction | space heating | Condensing Unit Heater | 225-300 kBtu/hr 90% Thermal Efficiency, 89% Annual Efficiency | Non-Condensing Unit Heater | 80% Thermal Efficiency, 78% Annual Efficiency |  | kBtu/hr input capacity | TRM Version 8.0 | 2024-04-30 | 0 | 4.62 | -320 | 0 | 0 | 0 | 0 | 16.07 | 18 | Low-Income | 0 | 1 | 1
COM-CU-SH-517-04 | Current | Updated size descriptions in eTRM to match TRM, entered energy savings that appear to be new from last TRM | Commercial | Condensing Unit Heater |  | New Construction | space heating | Condensing Unit Heater | 30-125 kBtu/hr - 90% Thermal Efficiency, 89% Annual Efficiency | Non-Condensing Unit Heater | 80% Thermal Efficiency, 78% Annual Efficiency |  | kBtu/hr input capacity | TRM Version 8.0 | 2024-04-30 | 0 | 4.62 | -173 | 0 | 0 | 0 | 0 | 16.07 | 18 | Low-Income | 0 | 1 | 1
COM-CT-WH-533-15 | Current | Updated size descriptions in eTRM to match TRM. Split New Construction and Natural Replacement to effectively represent baseline. Updated technology descriptions. Updated energy savings. | Commercial | Condensing Tankless Water Heater | High Utilization | Natural Replacement | water heating | Condensing Tankless Water Heater - High Utilization | <200 kBtu/hr UEF >= 0.90 Stand-by Loss = negligible | Non-Condensing Storage Water Heater | Storage Water Heater 75 kBtu/hr. and greater Uniform Energy Factor (UEF)=0.6597-0.00024Vs | unit | kBtu/hr input capacity | TRM Version 8.0 | 2024-04-30 | 212 | 4.349 | 0 | 0 | 0 | 0 | 3030 | 0 | 20 | Low-Income | 0 | 1 | 1
COM-CT-WH-533-16 | Current | Split New Construction and Natural Replacement to effectively represent baseline. Updated technology descriptions. Updated energy savings. | Commercial | Condensing Tankless Water Heater | High Utilization | Natural Replacement | water heating | Condensing Tankless Water Heater - High Utilization | >=200 kBtu/hr Thermal efficiency >= 94% Stand-by Loss = negligible | Non-Condensing Storage Water Heater | Storage Water Heater 75 kBtu/hr. and greater Thermal efficiency = 80% Stand-by Loss Q/800 +110√V0 Btu/hr | unit | kBtu/hr input capacity | TRM Version 8.0 | 2024-04-30 | 351 | 1.954 | 0 | 0 | 0 | 0 | 3030 | 0 | 20 | Low-Income | 0 | 1 | 1
COM-CT-WH-533-17 | Current | Updated size descriptions in eTRM to match TRM. Split New Construction and Natural Replacement to effectively represent baseline. Updated technology descriptions. Updated energy savings. | Commercial | Condensing Tankless Water Heater | High Utilization | Natural Replacement | water heating | Condensing Tankless Water Heater - High Utilization | <200 kBtu/hr UEF >= 0.95 Stand-by Loss = negligible | Non-Condensing Storage Water Heater | Storage Water Heater 75 kBtu/hr. and greater Uniform Energy Factor (UEF)=0.6597-0.00024Vs | unit | kBtu/hr input capacity | TRM Version 8.0 | 2024-04-30 | 212 | 5.211 | 0 | 0 | 0 | 0 | 3030 | 0 | 20 | Low-Income | 0 | 1 | 1
COM-CT-WH-533-18 | Current | Split New Construction and Natural Replacement to effectively represent baseline. Updated technology descriptions. Updated energy savings. | Commercial | Condensing Tankless Water Heater | High Utilization | Natural Replacement | water heating | Condensing Tankless Water Heater - High Utilization | >=200 kBtu/hr Thermal efficiency >= 96% Stand-by Loss = negligible | Non-Condensing Storage Water Heater | Storage Water Heater 75 kBtu/hr. and greater Thermal efficiency = 80% Stand-by Loss Q/800 +110√V0 Btu/hr | unit | kBtu/hr input capacity | TRM Version 8.0 | 2024-04-30 | 521 | 2.233 | 0 | 0 | 0 | 0 | 3030 | 0 | 20 | Low-Income | 0 | 1 | 1
COM-CT-WH-533-19 | Current | Split New Construction and Natural Replacement to effectively represent baseline. Updated technology descriptions. Updated energy savings. | Commercial | Condensing Tankless Water Heater | High Utilization | Natural Replacement | water heating | Condensing Tankless Water Heater - High Utilization | >=200 kBtu/hr Thermal efficiency >= 98% Stand-by Loss = negligible | Non-Condensing Storage Water Heater | Storage Water Heater 75 kBtu/hr. and greater Thermal efficiency = 80% Stand-by Loss Q/800 +110√V0 Btu/hr | unit | kBtu/hr input capacity | TRM Version 8.0 | 2024-04-30 | 867 | 2.512 | 0 | 0 | 0 | 0 | 3030 | 0 | 20 | Low-Income | 0 | 1 | 1
COM-CT-WH-534-12 | Current | Updated size descriptions in eTRM to match TRM. Split New Construction and Natural Replacement to effectively represent baseline. Updated technology descriptions. Updated energy savings. | Commercial | Condensing Tankless Water Heater | High Utilization | New Construction | water heating | Condensing Tankless Water Heater - High Utilization | <200 kBtu/hr UEF >= 0.95 Stand-by Loss = negligible | Non-Condensing Storage Water Heater | Storage Water Heater 75 kBtu/hr. and greater Uniform Energy Factor (UEF)=0.8107-0.00021Vs | unit | kBtu/hr input capacity | TRM Version 8.0 | 2024-04-30 | 178 | 2.09 | 0 | 0 | 0 | 0 | 1030 | 0 | 20 | Low-Income | 0 | 1 | 1
COM-CT-WH-534-13 | Current | Split New Construction and Natural Replacement to effectively represent baseline. Updated technology descriptions. Updated energy savings. | Commercial | Condensing Tankless Water Heater | High Utilization | New Construction | water heating | Condensing Tankless Water Heater - High Utilization | >=200 kBtu/hr Thermal efficiency >= 96% Stand-by Loss = negligible | Non-Condensing Storage Water Heater | Storage Water Heater 75 kBtu/hr. and greater Thermal efficiency = 90% Stand-by Loss 0.84(Q/800 +110√V0)Btu/hr | unit | kBtu/hr input capacity | TRM Version 8.0 | 2024-04-30 | 295 | 0.744 | 0 | 0 | 0 | 0 | 1030 | 0 | 20 | Low-Income | 0 | 1 | 1
COM-CT-WH-534-14 | Current | Split New Construction and Natural Replacement to effectively represent baseline. Updated technology descriptions. Updated energy savings. | Commercial | Condensing Tankless Water Heater | High Utilization | New Construction | water heating | Condensing Tankless Water Heater - High Utilization | >=1000 < 2500 kBtu/hr Thermal efficiency >= 98% Stand-by Loss = negligible | Non-Condensing Storage Water Heater | Storage Water Heater 75 kBtu/hr. and greater Thermal efficiency = 80% Stand-by Loss Q/800 +110√V0 Btu/hr | unit | kBtu/hr input capacity | TRM Version 8.0 | 2024-04-30 | 438 | 0.992 | 0 | 0 | 0 | 0 | 1030 | 0 | 20 | Low-Income | 0 | 1 | 1
COM-CT-WH-534-15 | Current | Split New Construction and Natural Replacement to effectively represent baseline. Updated technology descriptions. Updated energy savings. | Commercial | Condensing Tankless Water Heater | High Utilization | New Construction | water heating | Condensing Tankless Water Heater - High Utilization | >=2500 kBtu/hr Thermal efficiency >= 98% Stand-by Loss = negligible | Non-Condensing Storage Water Heater | Storage Water Heater 75 kBtu/hr. and greater Thermal efficiency = 80% Stand-by Loss Q/800 +110√V0 Btu/hr | unit | kBtu/hr input capacity | TRM Version 8.0 | 2024-04-30 | 728 | 0.992 | 0 | 0 | 0 | 0 | 1030 | 0 | 20 | Low-Income | 0 | 1 | 1
COM-CT-WH-535-15 | Current | Updated size descriptions in eTRM to match TRM. Split New Construction and Natural Replacement to effectively represent baseline. Updated technology descriptions. Updated energy savings. | Commercial | Condensing Tankless Water Heater | Low Utilization | Natural Replacement | water heating | Condensing Tankless Water Heater - Low Utilization | <200 kBtu/hr UEF >= 0.90 Stand-by Loss = negligible | Non-Condensing Storage Water Heater | Storage Water Heater 75 kBtu/hr. and greater Uniform Energy Factor (UEF)=0.6597-0.00024Vs | unit | kBtu/hr input capacity | TRM Version 8.0 | 2024-04-30 | 212 | 1.918 | 0 | 0 | 0 | 0 | 3030 | 0 | 20 | Low-Income | 0 | 1 | 1
COM-CS-WH-502-03 | Replaced | Replaced in TRM Version 8.0 | Commercial | Condensing Storage Water Heater | Low Utilization | New Construction/Natural Replacement | water heating | Condensing Storage Water Heater - Low Utilization | > 75 kBtu/hr and <=250 kBtu/hr. inputEstimated overall efficiency of units shipped = 94.5% | Non-condensing storage water heater | Non-condensing storage water heaterGreater than 75 kBtu/hr. inputEstimated overall efficiency of units shipped = 80.1% |  | kBtu/hr input capacity | TRM Version 5.0 | 2020-11-12 | 0 | 1.36 | 0 | 0 | 0 | 0 | 2591 | 0 | 15 | Midstream | 0.05 | 1 | 1
COM-CS-WH-503-03 | Replaced | Replaced in TRM Version 8.0 | Commercial | Condensing Storage Water Heater | Medium Utilization | New Construction/Natural Replacement | water heating | Condensing Storage Water Heater - Medium Utilization | > 75 kBtu/hr and <=250 kBtu/hr. inputEstimated overall efficiency of units shipped = 94.5% | Non-condensing storage water heater | Greater than 75 kBtu/hr. inputEstimated overall efficiency of units shipped = 80.1% |  | kBtu/hr input capacity | TRM Version 5.0 | 2020-11-12 | 0 | 2.22 | 0 | 0 | 0 | 0 | 2591 | 0 | 15 | Midstream | 0.05 | 1 | 1
COM-CS-WH-504-03 | Replaced | Replaced in TRM Version 8.0 | Commercial | Condensing Storage Water Heater | High Utilization | New Construction/Natural Replacement | water heating | Condensing Storage Water Heater - High Utilization | > 75 kBtu/hr and <=250 kBtu/hr. inputEstimated overall efficiency of units shipped = 94.5% | Non-condensing storage water heater | Greater than 75 kBtu/hr. inputEstimated overall efficiency of units shipped = 80.1% |  | kBtu/hr input capacity | TRM Version 5.0 | 2020-11-12 | 0 | 3.09 | 0 | 0 | 0 | 0 | 2591 | 0 | 15 | Midstream | 0.05 | 1 | 1
COM-CT-WH-511-03 | Replaced | Replaced in TRM Version 8.0 | Commercial | Condensing Tankless Water Heater | Low Utilization | New Construction/Natural Replacement | water heating | Condensing Tankless Water Heater - Low Utilization | >=200 kBtu/hrThermal efficiency = 92.9%Stand-by Loss = negligible | Non-Condensing Storage Water Heater | 75 kBtu/hr. and greaterThermal efficiency of units shipped = 80.1%Stand-by Loss Q/0.8 +110√V0 | unit | kBtu/hr input capacity | TRM Version 5.0 | 2020-11-12 | 326 | 0.79 | 0 | 0 | 0 | 0 | 2227 | 0 | 20 | Midstream | 0.02 | 1 | 1
COM-CT-WH-512-03 | Replaced | Replaced in TRM Version 8.0 | Commercial | Condensing Tankless Water Heater | Medium Utilization | New Construction/Natural Replacement | water heating | Condensing Tankless Water Heater - Medium Utilization | >=200 kBtu/hrThermal efficiency = 92.9%Stand-by Loss = negligible | Non-Condensing Storage Water Heater | 75 kBtu/hr. and greaterThermal efficiency of units shipped = 80.1%Stand-by Loss Q/0.8 +110√V0 | unit | kBtu/hr input capacity | TRM Version 5.0 | 2020-11-12 | 326 | 1.29 | 0 | 0 | 0 | 0 | 2227 | 0 | 20 | Midstream | 0.02 | 1 | 1
COM-CT-WH-513-03 | Replaced | Replaced in TRM Version 8.0 | Commercial | Condensing Tankless Water Heater | High Utilization | New Construction/Natural Replacement | water heating | Condensing Tankless Water Heater - High Utilization | >=200 kBtu/hrThermal efficiency = 92.9%Stand-by Loss = negligible | Non-Condensing Storage Water Heater | 75 kBtu/hr. and greaterThermal efficiency of units shipped = 80.1%Stand-by Loss Q/0.8 +110√V0 | unit | kBtu/hr input capacity | TRM Version 5.0 | 2020-11-12 | 326 | 1.79 | 0 | 0 | 0 | 0 | 2227 | 0 | 20 | Midstream | 0.02 | 1 | 1
COM-CS-WH-505-03 | Replaced | Replaced in TRM Version 8.0 | Commercial | Condensing Storage Water Heater | Low Utilization | New Construction/Natural Replacement | water heating | Condensing Storage Water Heater - Low Utilization | >250 kBtu/hr. inputEstimated overall efficiency of units shipped = 94.5% | Non-condensing storage water heater | Greater than 75 kBtu/hr. inputEstimated overall efficiency of units shipped = 80.1% |  | kBtu/hr input capacity | TRM Version 5.0 | 2020-11-12 | 0 | 1.36 | 0 | 0 | 0 | 0 | 4464 | 0 | 15 | Midstream | 0.05 | 1 | 1
COM-CS-WH-506-03 | Replaced | Replaced in TRM Version 8.0 | Commercial | Condensing Storage Water Heater | Medium Utilization | New Construction/Natural Replacement | water heating | Condensing Storage Water Heater - Medium Utilization | >250 kBtu/hr. inputEstimated overall efficiency of units shipped = 94.5% | Non-condensing storage water heater | Greater than 75 kBtu/hr. inputEstimated overall efficiency of units shipped = 80.1% |  | kBtu/hr input capacity | TRM Version 5.0 | 2020-11-12 | 0 | 2.22 | 0 | 0 | 0 | 0 | 4464 | 0 | 15 | Midstream | 0.05 | 1 | 1
COM-CS-WH-507-03 | Replaced | Replaced in TRM Version 8.0 | Commercial | Condensing Storage Water Heater | High Utilization | New Construction/Natural Replacement | water heating | Condensing Storage Water Heater - High Utilization | >250 kBtu/hr. inputEstimated overall efficiency of units shipped = 94.5% | Non-condensing storage water heater | Greater than 75 kBtu/hr. inputEstimated overall efficiency of units shipped = 80.1% |  | kBtu/hr input capacity | TRM Version 5.0 | 2020-11-12 | 0 | 3.09 | 0 | 0 | 0 | 0 | 4464 | 0 | 15 | Midstream | 0.05 | 1 | 1
COM-CT-WH-508-03 | Replaced | Replaced in TRM Version 8.0 | Commercial | Condensing Tankless Water Heater | Low Utilization | New Construction/Natural Replacement | water heating | Condensing Tankless Water Heater - Low Utilization | >75 and <200 kBtu/hrThermal efficiency = 92.9%Stand-by Loss = negligible | Non-Condensing Storage Water Heater | 75 kBtu/hr. and greaterThermal efficiency of units shipped = 80.1%Stand-by Loss Q/0.8 +110√V0 | unit | kBtu/hr input capacity | TRM Version 5.0 | 2020-11-12 | 212 | 0.79 | 0 | 0 | 0 | 0 | 2227 | 0 | 20 | Midstream | 0.02 | 1 | 1
COM-CT-WH-509-03 | Replaced | Replaced in TRM Version 8.0 | Commercial | Condensing Tankless Water Heater | Medium Utilization | New Construction/Natural Replacement | water heating | Condensing Tankless Water Heater - Medium Utilization | >75 and <200 kBtu/hrThermal efficiency = 92.9%Stand-by Loss = negligible | Non-Condensing Storage Water Heater | 75 kBtu/hr. and greaterThermal efficiency of units shipped = 80.1%Stand-by Loss Q/0.8 +110√V0 | unit | kBtu/hr input capacity | TRM Version 5.0 | 2020-11-12 | 212 | 1.29 | 0 | 0 | 0 | 0 | 2227 | 0 | 20 | Midstream | 0.02 | 1 | 1
COM-CT-WH-510-03 | Replaced | Replaced in TRM Version 8.0 | Commercial | Condensing Tankless Water Heater | High Utilization | New Construction/Natural Replacement | water heating | Condensing Tankless Water Heater - High Utilization | >75 and <200 kBtu/hrThermal efficiency = 92.9%Stand-by Loss = negligible | Non-Condensing Storage Water Heater | 75 kBtu/hr. and greaterThermal efficiency of units shipped = 80.1%Stand-by Loss Q/0.8 +110√V0 | unit | kBtu/hr input capacity | TRM Version 5.0 | 2020-11-12 | 212 | 1.79 | 0 | 0 | 0 | 0 | 2227 | 0 | 20 | Midstream | 0.02 | 1 | 1
COM-DK-SH-521-04 | Replaced | Updated in TRM V8.0 | Commercial | Demand Control Kitchen Ventilation |  | Retrofit | space heating | Demand Control Kitchen Ventilation | 0 - 5,000 CFM | Constant Volume Kitchen Ventilation |  | unit |  | TRM Version 5.0 | 2020-11-12 | 4207 | 0 | 4940 | 0 | 0 | 0 | 4766 | 0 | 15 | Midstream | 0.05 | 1 | 1
COM-DK-SH-524-04 | Replaced | Updated in TRM V8.0 | Commercial | Demand Control Kitchen Ventilation |  | New Construction/Natural Replacement | space heating | Demand Control Kitchen Ventilation | 0 - 5,000 CFM | Constant Volume Kitchen Ventilation |  | unit |  | TRM Version 5.0 | 2020-11-12 | 4207 | 0 | 4940 | 0 | 0 | 0 | 2383 | 0 | 15 | Midstream | 0.05 | 1 | 1
COM-DK-SH-523-04 | Replaced | Updated in TRM V8.0 | Commercial | Demand Control Kitchen Ventilation |  | Retrofit | space heating | Demand Control Kitchen Ventilation | 10,001 - 15,000 CFM | Constant Volume Kitchen Ventilation |  | unit |  | TRM Version 5.0 | 2020-11-12 | 17529 | 0 | 28929 | 0 | 0 | 0 | 19859 | 0 | 15 | Midstream | 0.05 | 1 | 1
COM-DK-SH-526-04 | Replaced | Updated in TRM V8.0 | Commercial | Demand Control Kitchen Ventilation |  | New Construction/Natural Replacement | space heating | Demand Control Kitchen Ventilation | 10,001 - 15,000 CFM | Constant Volume Kitchen Ventilation |  | unit |  | TRM Version 5.0 | 2020-11-12 | 17529 | 0 | 28929 | 0 | 0 | 0 | 9929 | 0 | 15 | Midstream | 0.05 | 1 | 1
COM-CU-SH-515-03 | Replaced | Updated in TRM Version 6.0 with new incremental cost and negative, not positive electric savings. | Commercial | Condensing Unit Heater |  | Natural Replacement | space heating | Condensing Unit Heater | 125-200 kBtu/hr 90% Thermal Efficiency, 89% Annual Efficiency | Non-Condensing Unit Heater | 80% Thermal Efficiency, 78% Annual Efficiency |  | kBtu/hr input capacity | TRM Version 5.0 | 2020-11-12 | 0 | 7.89 | -530 | 0 | 0 | 0 | 0 | 12.9 | 18 | Midstream | 0 | 1 | 1
COM-CU-SH-518-03 | Replaced | Updated in TRM Version 6.0 with new incremental cost and negative, not positive electric savings. | Commercial | Condensing Unit Heater |  | New Construction | space heating | Condensing Unit Heater | 125-200 kBtu/hr 90% Thermal Efficiency, 89% Annual Efficiency | Non-Condensing Unit Heater | 80% Thermal Efficiency, 78% Annual Efficiency |  | kBtu/hr input capacity | TRM Version 5.0 | 2020-11-12 | 0 | 5.92 | -398 | 0 | 0 | 0 | 0 | 12.9 | 18 | Midstream | 0 | 1 | 1
COM-CU-SH-516-03 | Replaced | Updated in TRM Version 6.0 with new incremental cost and negative, not positive electric savings. | Commercial | Condensing Unit Heater |  | Natural Replacement | space heating | Condensing Unit Heater | 225-300 kBtu/hr 90% Thermal Efficiency, 89% Annual Efficiency | Non-Condensing Unit Heater | 80% Thermal Efficiency, 78% Annual Efficiency |  | kBtu/hr input capacity | TRM Version 5.0 | 2020-11-12 | 0 | 7.89 | -546 | 0 | 0 | 0 | 0 | 12.9 | 18 | Midstream | 0 | 1 | 1
COM-CU-SH-519-03 | Replaced | Updated in TRM Version 6.0 with new incremental cost and negative, not positive electric savings. | Commercial | Condensing Unit Heater |  | New Construction | space heating | Condensing Unit Heater | 225-300 kBtu/hr 90% Thermal Efficiency, 89% Annual Efficiency | Non-Condensing Unit Heater | 80% Thermal Efficiency, 78% Annual Efficiency |  | kBtu/hr input capacity | TRM Version 5.0 | 2020-11-12 | 0 | 5.92 | -410 | 0 | 0 | 0 | 0 | 12.9 | 18 | Midstream | 0 | 1 | 1
COM-CU-SH-514-03 | Replaced | Updated in TRM Version 6.0 with new incremental cost and negative, not positive electric savings. | Commercial | Condensing Unit Heater |  | Natural Replacement | space heating | Condensing Unit Heater | 30-100 kBtu/hr - 90% Thermal Efficiency, 89% Annual Efficiency | Non-Condensing Unit Heater | 80% Thermal Efficiency, 78% Annual Efficiency |  | kBtu/hr input capacity | TRM Version 5.0 | 2020-11-12 | 0 | 7.89 | -296 | 0 | 0 | 0 | 0 | 12.9 | 18 | Midstream | 0 | 1 | 1
COM-CU-SH-517-03 | Replaced | Updated in TRM Version 6.0 with new incremental cost and negative, not positive electric savings. | Commercial | Condensing Unit Heater |  | New Construction | space heating | Condensing Unit Heater | 30-100 kBtu/hr - 90% Thermal Efficiency, 89% Annual Efficiency | Non-Condensing Unit Heater | 80% Thermal Efficiency, 78% Annual Efficiency |  | kBtu/hr input capacity | TRM Version 5.0 | 2020-11-12 | 0 | 5.92 | -222 | 0 | 0 | 0 | 0 | 12.9 | 18 | Midstream | 0 | 1 | 1
COM-DK-SH-522-04 | Replaced | Updated in TRM V8.0 | Commercial | Demand Control Kitchen Ventilation |  | Retrofit | space heating | Demand Control Kitchen Ventilation | 5,001 - 10,000 CFM | Constant Volume Kitchen Ventilation |  | unit |  | TRM Version 5.0 | 2020-11-12 | 10517 | 0 | 16294 | 0 | 0 | 0 | 11915 | 0 | 15 | Midstream | 0.05 | 1 | 1
COM-DK-SH-525-04 | Replaced | Updated in TRM V8.0 | Commercial | Demand Control Kitchen Ventilation |  | New Construction/Natural Replacement | space heating | Demand Control Kitchen Ventilation | 5,001 - 10,000 CFM | Constant Volume Kitchen Ventilation |  | unit |  | TRM Version 5.0 | 2020-11-12 | 10517 | 0 | 16294 | 0 | 0 | 0 | 5958 | 0 | 15 | Midstream | 0.05 | 1 | 1
COM-CO-FS-520-03 | Replaced | Updated in TRM Version 6.0 | Commercial | Convection Ovens |  | New Construction/Natural Replacement | food service | Energy Star Convection Ovens | Energy Star Rated Convection Oven (Full Size) | Conventional Convection Oven (Full Size) |  | unit |  | TRM Version 5.0 | 2020-11-12 | 865 | 0 | 40.1 | 0 | 0 | 0 | 1200 | 0 | 12 | Midstream | 0.2 | 1 | 1
COM-FR-FS-324-03 | Replaced | Updated in TRM Version 7.0 | Commercial | Fryer |  | New Construction/Natural Replacement | food service | Energy Star Fryer | Energy Star Rated Fryer | Non-Energy Star rated Fryer |  | unit |  | TRM Version 5.0 | 2020-11-12 | 1408 | 0 | 0 | 0 | 0 | 0 | 2476 | 0 | 12 | Midstream | 0.2 | 1 | 1
COM-CT-WH-535-16 | Current | Split New Construction and Natural Replacement to effectively represent baseline. Updated technology descriptions. Updated energy savings. | Commercial | Condensing Tankless Water Heater | Low Utilization | Natural Replacement | water heating | Condensing Tankless Water Heater - Low Utilization | >=200 kBtu/hr Thermal efficiency >= 94% Stand-by Loss = negligible | Non-Condensing Storage Water Heater | Storage Water Heater 75 kBtu/hr. and greater Thermal efficiency = 80% Stand-by Loss Q/800 +110√V0 Btu/hr | unit | kBtu/hr input capacity | TRM Version 8.0 | 2024-04-30 | 351 | 0.862 | 0 | 0 | 0 | 0 | 3030 | 0 | 20 | Low-Income | 0 | 1 | 1
COM-CT-WH-535-17 | Current | Updated size descriptions in eTRM to match TRM. Split New Construction and Natural Replacement to effectively represent baseline. Updated technology descriptions. Updated energy savings. | Commercial | Condensing Tankless Water Heater | Low Utilization | Natural Replacement | water heating | Condensing Tankless Water Heater - Low Utilization | <200 kBtu/hr UEF >= 0.95 Stand-by Loss = negligible | Non-Condensing Storage Water Heater | Storage Water Heater 75 kBtu/hr. and greater Uniform Energy Factor (UEF)=0.6597-0.00024Vs | unit | kBtu/hr input capacity | TRM Version 8.0 | 2024-04-30 | 212 | 2.299 | 0 | 0 | 0 | 0 | 3030 | 0 | 20 | Low-Income | 0 | 1 | 1
COM-CT-WH-535-18 | Current | Split New Construction and Natural Replacement to effectively represent baseline. Updated technology descriptions. Updated energy savings. | Commercial | Condensing Tankless Water Heater | Low Utilization | Natural Replacement | water heating | Condensing Tankless Water Heater - Low Utilization | >=200 kBtu/hr Thermal efficiency >= 96% Stand-by Loss = negligible | Non-Condensing Storage Water Heater | Storage Water Heater 75 kBtu/hr. and greater Thermal efficiency = 80% Stand-by Loss Q/800 +110√V0 Btu/hr | unit | kBtu/hr input capacity | TRM Version 8.0 | 2024-04-30 | 521 | 0.985 | 0 | 0 | 0 | 0 | 3030 | 0 | 20 | Low-Income | 0 | 1 | 1
COM-CT-WH-535-19 | Current | Split New Construction and Natural Replacement to effectively represent baseline. Updated technology descriptions. Updated energy savings. | Commercial | Condensing Tankless Water Heater | Low Utilization | Natural Replacement | water heating | Condensing Tankless Water Heater - Low Utilization | >=200 kBtu/hr Thermal efficiency >= 98% Stand-by Loss = negligible | Non-Condensing Storage Water Heater | Storage Water Heater 75 kBtu/hr. and greater Thermal efficiency = 80% Stand-by Loss Q/800 +110√V0 Btu/hr | unit | kBtu/hr input capacity | TRM Version 8.0 | 2024-04-30 | 867 | 1.108 | 0 | 0 | 0 | 0 | 3030 | 0 | 20 | Low-Income | 0 | 1 | 1
COM-CT-WH-536-12 | Current | Updated size descriptions in eTRM to match TRM. Split New Construction and Natural Replacement to effectively represent baseline. Updated technology descriptions. Updated energy savings. | Commercial | Condensing Tankless Water Heater | Low Utilization | New Construction | water heating | Condensing Tankless Water Heater - Low Utilization | <200 kBtu/hr UEF >= 0.95 Stand-by Loss = negligible | Non-Condensing Storage Water Heater | Storage Water Heater 75 kBtu/hr. and greater Uniform Energy Factor (UEF)=0.8107-0.00021Vs | unit | kBtu/hr input capacity | TRM Version 8.0 | 2024-04-30 | 178 | 0.922 | 0 | 0 | 0 | 0 | 1030 | 0 | 20 | Low-Income | 0 | 1 | 1
COM-CT-WH-536-13 | Current | Split New Construction and Natural Replacement to effectively represent baseline. Updated technology descriptions. Updated energy savings. | Commercial | Condensing Tankless Water Heater | Low Utilization | New Construction | water heating | Condensing Tankless Water Heater - Low Utilization | >=200 kBtu/hr Thermal efficiency >= 96% Stand-by Loss = negligible | Non-Condensing Storage Water Heater | Storage Water Heater 75 kBtu/hr. and greater Thermal efficiency = 90% Stand-by Loss 0.84(Q/800 +110√V0)Btu/hr | unit | kBtu/hr input capacity | TRM Version 8.0 | 2024-04-30 | 295 | 0.328 | 0 | 0 | 0 | 0 | 1030 | 0 | 20 | Low-Income | 0 | 1 | 1
COM-CT-WH-536-14 | Current | Split New Construction and Natural Replacement to effectively represent baseline. Updated technology descriptions. Updated energy savings. | Commercial | Condensing Tankless Water Heater | Low Utilization | New Construction | water heating | Condensing Tankless Water Heater - Low Utilization | >=1000 < 2500 kBtu/hr Thermal efficiency >= 98% Stand-by Loss = negligible | Non-Condensing Storage Water Heater | Storage Water Heater 75 kBtu/hr. and greater Thermal efficiency = 80% Stand-by Loss Q/800 +110√V0 Btu/hr | unit | kBtu/hr input capacity | TRM Version 8.0 | 2024-04-30 | 438 | 0.438 | 0 | 0 | 0 | 0 | 1030 | 0 | 20 | Low-Income | 0 | 1 | 1
COM-CT-WH-536-15 | Current | Split New Construction and Natural Replacement to effectively represent baseline. Updated technology descriptions. Updated energy savings. | Commercial | Condensing Tankless Water Heater | Low Utilization | New Construction | water heating | Condensing Tankless Water Heater - Low Utilization | >=2500 kBtu/hr Thermal efficiency >= 98% Stand-by Loss = negligible | Non-Condensing Storage Water Heater | Storage Water Heater 75 kBtu/hr. and greater Thermal efficiency = 80% Stand-by Loss Q/800 +110√V0 Btu/hr | unit | kBtu/hr input capacity | TRM Version 8.0 | 2024-04-30 | 728 | 0.438 | 0 | 0 | 0 | 0 | 1030 | 0 | 20 | Low-Income | 0 | 1 | 1
COM-CT-WH-537-15 | Current | Updated size descriptions in eTRM to match TRM. Split New Construction and Natural Replacement to effectively represent baseline. Updated technology descriptions. Updated energy savings. | Commercial | Condensing Tankless Water Heater | Medium Utilization | Natural Replacement | water heating | Condensing Tankless Water Heater - Medium Utilization | <200 kBtu/hr UEF >= 0.90 Stand-by Loss = negligible | Non-Condensing Storage Water Heater | Storage Water Heater 75 kBtu/hr. and greater Uniform Energy Factor (UEF)=0.6597-0.00024Vs | unit | kBtu/hr input capacity | TRM Version 8.0 | 2024-04-30 | 212 | 3.128 | 0 | 0 | 0 | 0 | 3030 | 0 | 20 | Low-Income | 0 | 1 | 1
COM-CT-WH-537-16 | Current | Split New Construction and Natural Replacement to effectively represent baseline. Updated technology descriptions. Updated energy savings. | Commercial | Condensing Tankless Water Heater | Medium Utilization | Natural Replacement | water heating | Condensing Tankless Water Heater - Medium Utilization | >=200 kBtu/hr Thermal efficiency >= 94% Stand-by Loss = negligible | Non-Condensing Storage Water Heater | Storage Water Heater 75 kBtu/hr. and greater Thermal efficiency = 80% Stand-by Loss Q/800 +110√V0 Btu/hr | unit | kBtu/hr input capacity | TRM Version 8.0 | 2024-04-30 | 351 | 1.405 | 0 | 0 | 0 | 0 | 3030 | 0 | 20 | Low-Income | 0 | 1 | 1
COM-CT-WH-537-17 | Current | Updated size descriptions in eTRM to match TRM. Split New Construction and Natural Replacement to effectively represent baseline. Updated technology descriptions. Updated energy savings. | Commercial | Condensing Tankless Water Heater | Medium Utilization | Natural Replacement | water heating | Condensing Tankless Water Heater - Medium Utilization | <200 kBtu/hr UEF >= 0.95 Stand-by Loss = negligible | Non-Condensing Storage Water Heater | Storage Water Heater 75 kBtu/hr. and greater Uniform Energy Factor (UEF)=0.6597-0.00024Vs | unit | kBtu/hr input capacity | TRM Version 8.0 | 2024-04-30 | 212 | 3.748 | 0 | 0 | 0 | 0 | 3030 | 0 | 20 | Low-Income | 0 | 1 | 1
COM-CT-WH-537-18 | Current | Split New Construction and Natural Replacement to effectively represent baseline. Updated technology descriptions. Updated energy savings. | Commercial | Condensing Tankless Water Heater | Medium Utilization | Natural Replacement | water heating | Condensing Tankless Water Heater - Medium Utilization | >=200 kBtu/hr Thermal efficiency >= 96% Stand-by Loss = negligible | Non-Condensing Storage Water Heater | Storage Water Heater 75 kBtu/hr. and greater Thermal efficiency = 80% Stand-by Loss Q/800 +110√V0 Btu/hr | unit | kBtu/hr input capacity | TRM Version 8.0 | 2024-04-30 | 521 | 1.606 | 0 | 0 | 0 | 0 | 3030 | 0 | 20 | Low-Income | 0 | 1 | 1
COM-CT-WH-537-19 | Current | Split New Construction and Natural Replacement to effectively represent baseline. Updated technology descriptions. Updated energy savings. | Commercial | Condensing Tankless Water Heater | Medium Utilization | Natural Replacement | water heating | Condensing Tankless Water Heater - Medium Utilization | >=200 kBtu/hr Thermal efficiency >= 98% Stand-by Loss = negligible | Non-Condensing Storage Water Heater | Storage Water Heater 75 kBtu/hr. and greater Thermal efficiency = 80% Stand-by Loss Q/800 +110√V0 Btu/hr | unit | kBtu/hr input capacity | TRM Version 8.0 | 2024-04-30 | 867 | 1.807 | 0 | 0 | 0 | 0 | 3030 | 0 | 20 | Low-Income | 0 | 1 | 1
COM-CT-WH-538-12 | Current | Updated size descriptions in eTRM to match TRM. Split New Construction and Natural Replacement to effectively represent baseline. Updated technology descriptions. Updated energy savings. | Commercial | Condensing Tankless Water Heater | Medium Utilization | New Construction | water heating | Condensing Tankless Water Heater - Medium Utilization | <200 kBtu/hr UEF >= 0.95 Stand-by Loss = negligible | Non-Condensing Storage Water Heater | Storage Water Heater 75 kBtu/hr. and greater Uniform Energy Factor (UEF)=0.8107-0.00021Vs | unit | kBtu/hr input capacity | TRM Version 8.0 | 2024-04-30 | 178 | 1.503 | 0 | 0 | 0 | 0 | 1030 | 0 | 20 | Low-Income | 0 | 1 | 1
COM-CT-WH-538-13 | Current | Split New Construction and Natural Replacement to effectively represent baseline. Updated technology descriptions. Updated energy savings. | Commercial | Condensing Tankless Water Heater | Medium Utilization | New Construction | water heating | Condensing Tankless Water Heater - Medium Utilization | >=200 kBtu/hr Thermal efficiency >= 96% Stand-by Loss = negligible | Non-Condensing Storage Water Heater | Storage Water Heater 75 kBtu/hr. and greater Thermal efficiency = 90% Stand-by Loss 0.84(Q/800 +110√V0)Btu/hr | unit | kBtu/hr input capacity | TRM Version 8.0 | 2024-04-30 | 295 | 0.535 | 0 | 0 | 0 | 0 | 1030 | 0 | 20 | Low-Income | 0 | 1 | 1
COM-CT-WH-538-14 | Current | Split New Construction and Natural Replacement to effectively represent baseline. Updated technology descriptions. Updated energy savings. | Commercial | Condensing Tankless Water Heater | Medium Utilization | New Construction | water heating | Condensing Tankless Water Heater - Medium Utilization | >=1000 < 2500 kBtu/hr Thermal efficiency >= 98% Stand-by Loss = negligible | Non-Condensing Storage Water Heater | Storage Water Heater 75 kBtu/hr. and greater Thermal efficiency = 80% Stand-by Loss Q/800 +110√V0 Btu/hr | unit | kBtu/hr input capacity | TRM Version 8.0 | 2024-04-30 | 438 | 0.714 | 0 | 0 | 0 | 0 | 1030 | 0 | 20 | Low-Income | 0 | 1 | 1
COM-CT-WH-538-15 | Current | Split New Construction and Natural Replacement to effectively represent baseline. Updated technology descriptions. Updated energy savings. | Commercial | Condensing Tankless Water Heater | Medium Utilization | New Construction | water heating | Condensing Tankless Water Heater - Medium Utilization | >=2500 kBtu/hr Thermal efficiency >= 98% Stand-by Loss = negligible | Non-Condensing Storage Water Heater | Storage Water Heater 75 kBtu/hr. and greater Thermal efficiency = 80% Stand-by Loss Q/800 +110√V0 Btu/hr | unit | kBtu/hr input capacity | TRM Version 8.0 | 2024-04-30 | 728 | 0.714 | 0 | 0 | 0 | 0 | 1030 | 0 | 20 | Low-Income | 0 | 1 | 1
COM-CS-WH-527-24 | Current | Split New Construction and Natural Replacement to effectively represent baseline and efficient efficiencies. Updated savings. | Commercial | Condensing Storage Water Heater | High Utilization | Natural Replacement | water heating | Condensing storage water heater | > 75 kBTU/hr and <= 105 kBTU/hr, rated nominal volume <= 120 US gallon, single-phase power, water temp <180 deg f, UEF >= 0.86 < 0.89 | Non-condensing storage water heater | > 75 kBTU/hr and <= 105 kBTU/hr, rated nominal volume <= 120 US gallon, single-phase power, water temp <180 deg f, UEF = 0.6597 - 0.00024Vs |  | kBtu/hr input capacity | TRM Version 8.0 | 2024-04-30 | 0 | 5.699 | 0 | 0 | 0 | 0 | 2591 | 0 | 15 | Low-Income | 0 | 1 | 1
COM-CS-WH-527-25 | Current | Split New Construction and Natural Replacement to effectively represent baseline and efficient efficiencies. Updated savings. | Commercial | Condensing Storage Water Heater | High Utilization | Natural Replacement | water heating | Condensing storage water heater | > 75 kBTU/hr and <= 105 kBTU/hr, rated nominal volume <= 120 US gallon, single-phase power, water temp <180 deg f, UEF >= 0.89 | Non-condensing storage water heater | > 75 kBTU/hr and <= 105 kBTU/hr, rated nominal volume <= 120 US gallon, single-phase power, water temp <180 deg f, UEF = 0.6597 - 0.00024Vs |  | kBtu/hr input capacity | TRM Version 8.0 | 2024-04-30 | 0 | 6.497 | 0 | 0 | 0 | 0 | 2591 | 0 | 15 | Low-Income | 0 | 1 | 1
COM-CS-WH-527-26 | Current | Split New Construction and Natural Replacement to effectively represent baseline and efficient efficiencies. Updated savings. | Commercial | Condensing Storage Water Heater | High Utilization | Natural Replacement | water heating | Condensing storage water heater | All water heaters not described by UEF baseline definition with thermal efficiency >= 92% < 95%, <= 250 kBTU/hr | Non-condensing storage water heater | All water heaters not described by UEF baseline definition with thermal efficiency >= 80% |  | kBtu/hr input capacity | TRM Version 8.0 | 2024-04-30 | 0 | 2.577 | 0 | 0 | 0 | 0 | 2591 | 0 | 15 | Low-Income | 0 | 1 | 1
COM-CS-WH-527-27 | Current | Split New Construction and Natural Replacement to effectively represent baseline and efficient efficiencies. Updated savings. | Commercial | Condensing Storage Water Heater | High Utilization | Natural Replacement | water heating | Condensing storage water heater | All water heaters not described by UEF baseline definition with thermal efficiency >= 95% < 97%, <= 250 kBTU/hr | Non-condensing storage water heater | All water heaters not described by UEF baseline definition with thermal efficiency >= 80% |  | kBtu/hr input capacity | TRM Version 8.0 | 2024-04-30 | 0 | 3.221 | 0 | 0 | 0 | 0 | 2591 | 0 | 15 | Low-Income | 0 | 1 | 1
COM-CS-WH-527-28 | Current | Split New Construction and Natural Replacement to effectively represent baseline and efficient efficiencies. Updated savings. | Commercial | Condensing Storage Water Heater | High Utilization | Natural Replacement | water heating | Condensing storage water heater | All water heaters not described by UEF baseline definition with thermal efficiency >= 97%, <= 250 kBTU/hr | Non-condensing storage water heater | All water heaters not described by UEF baseline definition with thermal efficiency >= 80% |  | kBtu/hr input capacity | TRM Version 8.0 | 2024-04-30 | 0 | 3.651 | 0 | 0 | 0 | 0 | 2591 | 0 | 15 | Low-Income | 0 | 1 | 1
COM-CS-WH-527-29 | Current | Split New Construction and Natural Replacement to effectively represent baseline and efficient efficiencies. Updated savings. | Commercial | Condensing Storage Water Heater | High Utilization | Natural Replacement | water heating | Condensing storage water heater | All water heaters not described by UEF baseline definition with thermal efficiency >= 92% < 95%, > 250 kBTU/hr | Non-condensing storage water heater | All water heaters not described by UEF baseline definition with thermal efficiency >= 80% |  | kBtu/hr input capacity | TRM Version 8.0 | 2024-04-30 | 0 | 2.577 | 0 | 0 | 0 | 0 | 4464 | 0 | 15 | Low-Income | 0 | 1 | 1
COM-CS-WH-527-30 | Current | Split New Construction and Natural Replacement to effectively represent baseline and efficient efficiencies. Updated savings. | Commercial | Condensing Storage Water Heater | High Utilization | Natural Replacement | water heating | Condensing storage water heater | All water heaters not described by UEF baseline definition with thermal efficiency >= 95% < 97%, > 250 kBTU/hr | Non-condensing storage water heater | All water heaters not described by UEF baseline definition with thermal efficiency >= 80% |  | kBtu/hr input capacity | TRM Version 8.0 | 2024-04-30 | 0 | 3.221 | 0 | 0 | 0 | 0 | 4464 | 0 | 15 | Low-Income | 0 | 1 | 1
COM-CS-WH-527-31 | Current | Split New Construction and Natural Replacement to effectively represent baseline and efficient efficiencies. Updated savings. | Commercial | Condensing Storage Water Heater | High Utilization | Natural Replacement | water heating | Condensing storage water heater | All water heaters not described by UEF baseline definition with thermal efficiency >= 97%, > 250 kBTU/hr | Non-condensing storage water heater | All water heaters not described by UEF baseline definition with thermal efficiency >= 80% |  | kBtu/hr input capacity | TRM Version 8.0 | 2024-04-30 | 0 | 3.651 | 0 | 0 | 0 | 0 | 4464 | 0 | 15 | Low-Income | 0 | 1 | 1
COM-CS-WH-528-18 | Current | Split New Construction and Natural Replacement to effectively represent baseline and efficient efficiencies. Updated savings. | Commercial | Condensing Storage Water Heater | High Utilization | New Construction | water heating | Condensing storage water heater | > 75 kBTU/hr and <= 105 kBTU/hr, rated nominal volume <= 120 US gallon, single-phase power, water temp <180 deg f, UEF >= 0.86 < 0.89 | Non-condensing storage water heater | > 75 kBTU/hr and <= 105 kBTU/hr, rated nominal volume <= 120 US gallon, single-phase power, water temp <180 deg f, UEF = 0.8107 - 0.00021Vs |  | kBtu/hr input capacity | TRM Version 8.0 | 2024-04-30 | 0 | 1.323 | 0 | 0 | 0 | 0 | 2591 | 0 | 15 | Low-Income | 0 | 1 | 1
COM-CS-WH-528-19 | Current | Split New Construction and Natural Replacement to effectively represent baseline and efficient efficiencies. Updated savings. | Commercial | Condensing Storage Water Heater | High Utilization | New Construction | water heating | Condensing storage water heater | > 75 kBTU/hr and <= 105 kBTU/hr, rated nominal volume <= 120 US gallon, single-phase power, water temp <180 deg f, UEF >= 0.89 | Non-condensing storage water heater | > 75 kBTU/hr and <= 105 kBTU/hr, rated nominal volume <= 120 US gallon, single-phase power, water temp <180 deg f, UEF = 0.8107 - 0.00021Vs |  | kBtu/hr input capacity | TRM Version 8.0 | 2024-04-30 | 0 | 1.968 | 0 | 0 | 0 | 0 | 2591 | 0 | 15 | Low-Income | 0 | 1 | 1
COM-CS-WH-528-20 | Current | Split New Construction and Natural Replacement to effectively represent baseline and efficient efficiencies. Updated savings. | Commercial | Condensing Storage Water Heater | High Utilization | New Construction | water heating | Condensing storage water heater | All water heaters not described by UEF baseline definition with thermal efficiency >= 95 < 97%, <= 250 kBTU/hr | Non-condensing storage water heater | All water heaters not described by UEF baseline definition with thermal efficiency = 90% |  | kBtu/hr input capacity | TRM Version 8.0 | 2024-04-30 | 0 | 0.954 | 0 | 0 | 0 | 0 | 2591 | 0 | 15 | Low-Income | 0 | 1 | 1
COM-CS-WH-528-21 | Current | Split New Construction and Natural Replacement to effectively represent baseline and efficient efficiencies. Updated savings. | Commercial | Condensing Storage Water Heater | High Utilization | New Construction | water heating | Condensing storage water heater | All water heaters not described by UEF baseline definition with thermal efficiency >= 97%, <= 250 kBTU/hr | Non-condensing storage water heater | All water heaters not described by UEF baseline definition with thermal efficiency = 90% |  | kBtu/hr input capacity | TRM Version 8.0 | 2024-04-30 | 0 | 1.336 | 0 | 0 | 0 | 0 | 2591 | 0 | 15 | Low-Income | 0 | 1 | 1
COM-CS-WH-528-22 | Current | Split New Construction and Natural Replacement to effectively represent baseline and efficient efficiencies. Updated savings. | Commercial | Condensing Storage Water Heater | High Utilization | New Construction | water heating | Condensing storage water heater | All water heaters not described by UEF baseline definition with thermal efficiency >= 95 < 97%, > 250 kBTU/hr | Non-condensing storage water heater | All water heaters not described by UEF baseline definition with thermal efficiency = 90% |  | kBtu/hr input capacity | TRM Version 8.0 | 2024-04-30 | 0 | 0.954 | 0 | 0 | 0 | 0 | 4464 | 0 | 15 | Low-Income | 0 | 1 | 1
COM-CS-WH-528-23 | Current | Split New Construction and Natural Replacement to effectively represent baseline and efficient efficiencies. Updated savings. | Commercial | Condensing Storage Water Heater | High Utilization | New Construction | water heating | Condensing storage water heater | All water heaters not described by UEF baseline definition with thermal efficiency >= 97%, > 250 kBTU/hr | Non-condensing storage water heater | All water heaters not described by UEF baseline definition with thermal efficiency = 90% |  | kBtu/hr input capacity | TRM Version 8.0 | 2024-04-30 | 0 | 1.336 | 0 | 0 | 0 | 0 | 4464 | 0 | 15 | Low-Income | 0 | 1 | 1
COM-CS-WH-529-24 | Current | Split New Construction and Natural Replacement to effectively represent baseline and efficient efficiencies. Updated savings. | Commercial | Condensing Storage Water Heater | Low Utilization | Natural Replacement | water heating | Condensing storage water heater | > 75 kBTU/hr and <= 105 kBTU/hr, rated nominal volume <= 120 US gallon, single-phase power, water temp <180 deg f, UEF >= 0.86 < 0.89 | Non-condensing storage water heater | > 75 kBTU/hr and <= 105 kBTU/hr, rated nominal volume <= 120 US gallon, single-phase power, water temp <180 deg f, UEF = 0.6597 - 0.00024Vs |  | kBtu/hr input capacity | TRM Version 8.0 | 2024-04-30 | 0 | 2.515 | 0 | 0 | 0 | 0 | 2591 | 0 | 15 | Low-Income | 0 | 1 | 1
COM-CS-WH-529-25 | Current | Split New Construction and Natural Replacement to effectively represent baseline and efficient efficiencies. Updated savings. | Commercial | Condensing Storage Water Heater | Low Utilization | Natural Replacement | water heating | Condensing storage water heater | > 75 kBTU/hr and <= 105 kBTU/hr, rated nominal volume <= 120 US gallon, single-phase power, water temp <180 deg f, UEF >= 0.89 | Non-condensing storage water heater | > 75 kBTU/hr and <= 105 kBTU/hr, rated nominal volume <= 120 US gallon, single-phase power, water temp <180 deg f, UEF = 0.6597 - 0.00024Vs |  | kBtu/hr input capacity | TRM Version 8.0 | 2024-04-30 | 0 | 2.868 | 0 | 0 | 0 | 0 | 2591 | 0 | 15 | Low-Income | 0 | 1 | 1
COM-CS-WH-529-26 | Current | Split New Construction and Natural Replacement to effectively represent baseline and efficient efficiencies. Updated savings. | Commercial | Condensing Storage Water Heater | Low Utilization | Natural Replacement | water heating | Condensing storage water heater | All water heaters not described by UEF baseline definition with thermal efficiency >= 92% < 95%, <= 250 kBTU/hr | Non-condensing storage water heater | All water heaters not described by UEF baseline definition with thermal efficiency >= 80% |  | kBtu/hr input capacity | TRM Version 8.0 | 2024-04-30 | 0 | 1.137 | 0 | 0 | 0 | 0 | 2591 | 0 | 15 | Low-Income | 0 | 1 | 1
COM-CS-WH-529-27 | Current | Split New Construction and Natural Replacement to effectively represent baseline and efficient efficiencies. Updated savings. | Commercial | Condensing Storage Water Heater | Low Utilization | Natural Replacement | water heating | Condensing storage water heater | All water heaters not described by UEF baseline definition with thermal efficiency >= 95% < 97%, <= 250 kBTU/hr | Non-condensing storage water heater | All water heaters not described by UEF baseline definition with thermal efficiency >= 80% |  | kBtu/hr input capacity | TRM Version 8.0 | 2024-04-30 | 0 | 1.422 | 0 | 0 | 0 | 0 | 2591 | 0 | 15 | Low-Income | 0 | 1 | 1
COM-CS-WH-529-28 | Current | Split New Construction and Natural Replacement to effectively represent baseline and efficient efficiencies. Updated savings. | Commercial | Condensing Storage Water Heater | Low Utilization | Natural Replacement | water heating | Condensing storage water heater | All water heaters not described by UEF baseline definition with thermal efficiency >= 97%, <= 250 kBTU/hr | Non-condensing storage water heater | All water heaters not described by UEF baseline definition with thermal efficiency >= 80% |  | kBtu/hr input capacity | TRM Version 8.0 | 2024-04-30 | 0 | 1.611 | 0 | 0 | 0 | 0 | 2591 | 0 | 15 | Low-Income | 0 | 1 | 1
COM-CS-WH-529-29 | Current | Split New Construction and Natural Replacement to effectively represent baseline and efficient efficiencies. Updated savings. | Commercial | Condensing Storage Water Heater | Low Utilization | Natural Replacement | water heating | Condensing storage water heater | All water heaters not described by UEF baseline definition with thermal efficiency >= 92% < 95%, > 250 kBTU/hr | Non-condensing storage water heater | All water heaters not described by UEF baseline definition with thermal efficiency >= 80% |  | kBtu/hr input capacity | TRM Version 8.0 | 2024-04-30 | 0 | 1.137 | 0 | 0 | 0 | 0 | 4464 | 0 | 15 | Low-Income | 0 | 1 | 1
COM-CS-WH-529-30 | Current | Split New Construction and Natural Replacement to effectively represent baseline and efficient efficiencies. Updated savings. | Commercial | Condensing Storage Water Heater | Low Utilization | Natural Replacement | water heating | Condensing storage water heater | All water heaters not described by UEF baseline definition with thermal efficiency >= 95% < 97%, > 250 kBTU/hr | Non-condensing storage water heater | All water heaters not described by UEF baseline definition with thermal efficiency >= 80% |  | kBtu/hr input capacity | TRM Version 8.0 | 2024-04-30 | 0 | 1.422 | 0 | 0 | 0 | 0 | 4464 | 0 | 15 | Low-Income | 0 | 1 | 1
COM-CS-WH-529-31 | Current | Split New Construction and Natural Replacement to effectively represent baseline and efficient efficiencies. Updated savings. | Commercial | Condensing Storage Water Heater | Low Utilization | Natural Replacement | water heating | Condensing storage water heater | All water heaters not described by UEF baseline definition with thermal efficiency >= 97%, > 250 kBTU/hr | Non-condensing storage water heater | All water heaters not described by UEF baseline definition with thermal efficiency >= 80% |  | kBtu/hr input capacity | TRM Version 8.0 | 2024-04-30 | 0 | 1.611 | 0 | 0 | 0 | 0 | 4464 | 0 | 15 | Low-Income | 0 | 1 | 1
COM-CS-WH-530-18 | Current | Split New Construction and Natural Replacement to effectively represent baseline and efficient efficiencies. Updated savings. | Commercial | Condensing Storage Water Heater | Low Utilization | New Construction | water heating | Condensing storage water heater | > 75 kBTU/hr and <= 105 kBTU/hr, rated nominal volume <= 120 US gallon, single-phase power, water temp <180 deg f, UEF >= 0.86 < 0.89 | Non-condensing storage water heater | > 75 kBTU/hr and <= 105 kBTU/hr, rated nominal volume <= 120 US gallon, single-phase power, water temp <180 deg f, UEF = 0.8107 - 0.00021Vs |  | kBtu/hr input capacity | TRM Version 8.0 | 2024-04-30 | 0 | 0.584 | 0 | 0 | 0 | 0 | 2591 | 0 | 15 | Low-Income | 0 | 1 | 1
COM-CS-WH-530-19 | Current | Split New Construction and Natural Replacement to effectively represent baseline and efficient efficiencies. Updated savings. | Commercial | Condensing Storage Water Heater | Low Utilization | New Construction | water heating | Condensing storage water heater | > 75 kBTU/hr and <= 105 kBTU/hr, rated nominal volume <= 120 US gallon, single-phase power, water temp <180 deg f, UEF >= 0.89 | Non-condensing storage water heater | > 75 kBTU/hr and <= 105 kBTU/hr, rated nominal volume <= 120 US gallon, single-phase power, water temp <180 deg f, UEF = 0.8107 - 0.00021Vs |  | kBtu/hr input capacity | TRM Version 8.0 | 2024-04-30 | 0 | 0.869 | 0 | 0 | 0 | 0 | 2591 | 0 | 15 | Low-Income | 0 | 1 | 1
COM-CS-WH-530-20 | Current | Split New Construction and Natural Replacement to effectively represent baseline and efficient efficiencies. Updated savings. | Commercial | Condensing Storage Water Heater | Low Utilization | New Construction | water heating | Condensing storage water heater | All water heaters not described by UEF baseline definition with thermal efficiency >= 95 < 97%, <= 250 kBTU/hr | Non-condensing storage water heater | All water heaters not described by UEF baseline definition with thermal efficiency = 90% |  | kBtu/hr input capacity | TRM Version 8.0 | 2024-04-30 | 0 | 0.421 | 0 | 0 | 0 | 0 | 2591 | 0 | 15 | Low-Income | 0 | 1 | 1
COM-CS-WH-530-21 | Current | Split New Construction and Natural Replacement to effectively represent baseline and efficient efficiencies. Updated savings. | Commercial | Condensing Storage Water Heater | Low Utilization | New Construction | water heating | Condensing storage water heater | All water heaters not described by UEF baseline definition with thermal efficiency >= 97%, <= 250 kBTU/hr | Non-condensing storage water heater | All water heaters not described by UEF baseline definition with thermal efficiency = 90% |  | kBtu/hr input capacity | TRM Version 8.0 | 2024-04-30 | 0 | 0.59 | 0 | 0 | 0 | 0 | 2591 | 0 | 15 | Low-Income | 0 | 1 | 1
COM-CS-WH-530-22 | Current | Split New Construction and Natural Replacement to effectively represent baseline and efficient efficiencies. Updated savings. | Commercial | Condensing Storage Water Heater | Low Utilization | New Construction | water heating | Condensing storage water heater | All water heaters not described by UEF baseline definition with thermal efficiency >= 95 < 97%, > 250 kBTU/hr | Non-condensing storage water heater | All water heaters not described by UEF baseline definition with thermal efficiency = 90% |  | kBtu/hr input capacity | TRM Version 8.0 | 2024-04-30 | 0 | 0.421 | 0 | 0 | 0 | 0 | 4464 | 0 | 15 | Low-Income | 0 | 1 | 1
COM-CS-WH-530-23 | Current | Split New Construction and Natural Replacement to effectively represent baseline and efficient efficiencies. Updated savings. | Commercial | Condensing Storage Water Heater | Low Utilization | New Construction | water heating | Condensing storage water heater | All water heaters not described by UEF baseline definition with thermal efficiency >= 97%, > 250 kBTU/hr | Non-condensing storage water heater | All water heaters not described by UEF baseline definition with thermal efficiency = 90% |  | kBtu/hr input capacity | TRM Version 8.0 | 2024-04-30 | 0 | 0.59 | 0 | 0 | 0 | 0 | 4464 | 0 | 15 | Low-Income | 0 | 1 | 1
COM-CS-WH-531-24 | Current | Split New Construction and Natural Replacement to effectively represent baseline and efficient efficiencies. Updated savings. | Commercial | Condensing Storage Water Heater | Medium Utilization | Natural Replacement | water heating | Condensing storage water heater | > 75 kBTU/hr and <= 105 kBTU/hr, rated nominal volume <= 120 US gallon, single-phase power, water temp <180 deg f, UEF >= 0.86 < 0.89 | Non-condensing storage water heater | > 75 kBTU/hr and <= 105 kBTU/hr, rated nominal volume <= 120 US gallon, single-phase power, water temp <180 deg f, UEF = 0.6597 - 0.00024Vs |  | kBtu/hr input capacity | TRM Version 8.0 | 2024-04-30 | 0 | 4.103 | 0 | 0 | 0 | 0 | 2591 | 0 | 15 | Low-Income | 0 | 1 | 1
COM-CS-WH-531-25 | Current | Split New Construction and Natural Replacement to effectively represent baseline and efficient efficiencies. Updated savings. | Commercial | Condensing Storage Water Heater | Medium Utilization | Natural Replacement | water heating | Condensing storage water heater | > 75 kBTU/hr and <= 105 kBTU/hr, rated nominal volume <= 120 US gallon, single-phase power, water temp <180 deg f, UEF >= 0.89 | Non-condensing storage water heater | > 75 kBTU/hr and <= 105 kBTU/hr, rated nominal volume <= 120 US gallon, single-phase power, water temp <180 deg f, UEF = 0.6597 - 0.00024Vs |  | kBtu/hr input capacity | TRM Version 8.0 | 2024-04-30 | 0 | 4.677 | 0 | 0 | 0 | 0 | 2591 | 0 | 15 | Low-Income | 0 | 1 | 1
COM-CS-WH-531-26 | Current | Split New Construction and Natural Replacement to effectively represent baseline and efficient efficiencies. Updated savings. | Commercial | Condensing Storage Water Heater | Medium Utilization | Natural Replacement | water heating | Condensing storage water heater | All water heaters not described by UEF baseline definition with thermal efficiency >= 92% < 95%, <= 250 kBTU/hr | Non-condensing storage water heater | All water heaters not described by UEF baseline definition with thermal efficiency >= 80% |  | kBtu/hr input capacity | TRM Version 8.0 | 2024-04-30 | 0 | 1.855 | 0 | 0 | 0 | 0 | 2591 | 0 | 15 | Low-Income | 0 | 1 | 1
COM-RO-FS-651-02 | Replaced | Updated in V6.0 | Commercial | Rack Oven |  | New Construction/Natural Replacement | food service | ENERGY STAR Rack Oven | Energy Star Rated Rack Oven, Double | Conventiona rack oven |  | unit |  | TRM Version 5.0 | 2020-11-12 | 1076 | 0 | 1685 | 0 | 0 | 0 | 2591 | 0 | 12 | Midstream | 0.2 | 1 | 1
COM-RO-FS-650-02 | Replaced | Updated in V6.0 | Commercial | Rack Oven |  | New Construction/Natural Replacement | food service | ENERGY STAR Rack Oven | Energy Star Rated Rack Oven, Single | Conventiona rack oven |  | unit |  | TRM Version 5.0 | 2020-11-12 | 830 | 0 | 749 | 0 | 0 | 0 | 1544 | 0 | 12 | Midstream | 0.2 | 1 | 1
COM-SC-FS-325-03 | Replaced | Updated in TRM Version 7.0 | Commercial | Steam Cookers |  | New Construction/Natural Replacement | food service | Energy Star Steam Cookers | Energy Star Rated Steam Cooker | Boiler-based steam cooker |  | unit |  | TRM Version 5.0 | 2020-11-12 | 8889 | 0 | 0 | 0 | 340142 | 0 | 3880 | 0 | 12 | Midstream | 0.2 | 1 | 1
COM-DW-WH-555-04 | Replaced | Updated in TRM Version 6.0 | Commercial | Dishwasher |  | New Construction/Natural Replacement | water heating | Energy Star Dishwasher | Multi Tank Conveyor - High Temperature | Non-Energy Star Dishwasher |  | unit |  | TRM Version 5.0 | 2020-11-12 | 2260 | 0 | 9680 | 0 | 304677 | 0 | 1386 | 0 | 20 | Midstream | 0.27 | 1 | 1
COM-DW-WH-556-04 | Replaced | Updated in TRM Version 6.0 | Commercial | Dishwasher |  | New Construction/Natural Replacement | water heating | Energy Star Dishwasher | Multi Tank Conveyor - Low Temperature | Non-Energy Star Dishwasher |  | unit |  | TRM Version 5.0 | 2020-11-12 | 2383 | 0 | 0 | 0 | 354276 | 0 | 1386 | 0 | 20 | Midstream | 0.27 | 1 | 1
COM-OL-WH-329-03 | Replaced | Updated in TRM Version 6.0 | Commercial | Ozone Laundry |  | New Construction/Retrofit | water heating | Commercial Ozone Laundry Treatment | Ozone Treatment Tunnel Washer <= 120 lbs | Commercial laundry with no ozone treatment system |  |  | lbs/yr | TRM Version 5.0 | 2020-11-12 | 0 | 0.0305 | 0 | 0.0015 | 0 | 1.27 | 71429 | 0 | 15 | Midstream | 0.08 | 1 | 1
COM-OL-WH-331-03 | Replaced | Updated in TRM Version 6.0 | Commercial | Ozone Laundry |  | New Construction/Retrofit | water heating | Commercial Ozone Laundry Treatment | Ozone Treatment Tunnel Washer=> 500 lbs | Commercial laundry with no ozone treatment system |  |  | lbs/yr | TRM Version 5.0 | 2020-11-12 | 0 | 0.0305 | 0 | 0.0015 | 0 | 1.27 | 228571 | 0 | 15 | Midstream | 0.08 | 1 | 1
COM-OL-WH-330-03 | Replaced | Updated in TRM Version 6.0 | Commercial | Ozone Laundry |  | New Construction/Retrofit | water heating | Commercial Ozone Laundry Treatment | Ozone Treatment Tunnel Washer121 lbs to 499 lbs | Commercial laundry with no ozone treatment system |  |  | lbs/yr | TRM Version 5.0 | 2020-11-12 | 0 | 0.0305 | 0 | 0.0015 | 0 | 1.27 | 150000 | 0 | 15 | Midstream | 0.08 | 1 | 1
COM-OL-WH-326-03 | Replaced | Updated in TRM Version 6.0 | Commercial | Ozone Laundry |  | New Construction/Retrofit | water heating | Commercial Ozone Laundry Treatment | Ozone Treatment Washer extractor =< 60 lbs | Commercial laundry with no ozone treatment system |  |  | lbs/yr | TRM Version 5.0 | 2020-11-12 | 0 | 0.0383 | 0 | 0.00213 | 0 | 2.08 | 15714 | 0 | 15 | Midstream | 0.08 | 1 | 1
COM-OL-WH-327-03 | Replaced | Updated in TRM Version 6.0 | Commercial | Ozone Laundry |  | New Construction/Retrofit | water heating | Commercial Ozone Laundry Treatment | Ozone Treatment Washer extractor 61 lbs to 499 lbs | Commercial laundry with no ozone treatment system |  |  | lbs/yr | TRM Version 5.0 | 2020-11-12 | 0 | 0.0383 | 0 | 0.00213 | 0 | 2.08 | 35714 | 0 | 15 | Midstream | 0.08 | 1 | 1
COM-OL-WH-328-03 | Replaced | Updated in TRM Version 6.0 | Commercial | Ozone Laundry |  | New Construction/Retrofit | water heating | Commercial Ozone Laundry Treatment | Ozone Treatment Washer extractor=> 500 lbs | Commercial laundry with no ozone treatment system |  |  | lbs/yr | TRM Version 5.0 | 2020-11-12 | 0 | 0.0383 | 0 | 0.00213 | 0 | 2.08 | 44286 | 0 | 15 | Midstream | 0.08 | 1 | 1
COM-UB-FS-332-03 | Replaced | Updated in TRM Version 7.0 | Commercial | Under-Fired Broilers |  | New Construction/Natural Replacement | food service | High Efficiency Under-Fired Broilers - 3 foot | pre-heat =< 40,500 Btu and cooking energy rate =< 72,000 Btu/hr | Conventional Efficiency Under-Fired Broiler | pre-heat =< 48,000 Btu and cooking energy rate =< 96,000 Btu/hr | unit |  | TRM Version 5.0 | 2020-11-12 | 2511 | 0 | 0 | 0 | 0 | 0 | 1900 | 0 | 12 | Midstream | 0.2 | 1 | 1
COM-UB-FS-333-03 | Replaced | Updated in TRM Version 7.0 | Commercial | Under-Fired Broilers |  | New Construction/Natural Replacement | food service | High Efficiency Under-Fired Broilers - 4 foot | pre-heat 40,501 to 54,000 Btu and a cooking energy rate 72,001 to 96,000 Btu/hr | Conventional Efficiency Under-Fired Broiler | pre-heat 48,001 to 64,000 Btu and a cooking energy rate 96,000 to 128,000 Btu/hr | unit |  | TRM Version 5.0 | 2020-11-12 | 3347 | 0 | 0 | 0 | 0 | 0 | 1900 | 0 | 12 | Midstream | 0.2 | 1 | 1
COM-UB-FS-334-03 | Replaced | Updated in TRM Version 7.0 | Commercial | Under-Fired Broilers |  | New Construction/Natural Replacement | food service | High Efficiency Under-Fired Broilers - 5 foot | pre-heat 54,001 to 67,500 Btu and cooking energy rate 96,001 to 120,000 Btu/hr | Conventional Efficiency Under-Fired Broiler | pre-heat 64,001 to 80,000 Btu and cooking energy rate 128,001 to 160,000 Btu/hr | unit |  | TRM Version 5.0 | 2020-11-12 | 4184 | 0 | 0 | 0 | 0 | 0 | 1900 | 0 | 12 | Midstream | 0.2 | 1 | 1
COM-UB-FS-335-03 | Replaced | Updated in TRM Version 7.0 | Commercial | Under-Fired Broilers |  | New Construction/Natural Replacement | food service | High Efficiency Under-Fired Broilers - 6 foot | pre-heat 67,501 to 81,000 Btu and cooking energy rate 120,001 to 144,000 Btu/hr | Conventional Efficiency Under-Fired Broiler | pre-heat 80,001 to 96,000 Btu and cooking energy rate 160,001 to 192,000 Btu/hr | unit |  | TRM Version 5.0 | 2020-11-12 | 5021 | 0 | 0 | 0 | 0 | 0 | 1900 | 0 | 12 | Midstream | 0.2 | 1 | 1
COM-DW-WH-553-04 | Replaced | Updated in TRM Version 6.0 | Commercial | Dishwasher |  | New Construction/Natural Replacement | water heating | Energy Star Dishwasher | Single Tank Conveyor – High Temperature | Non-Energy Star Dishwasher |  | unit |  | TRM Version 5.0 | 2020-11-12 | 540 | 0 | 4251 | 0 | 80303 | 0 | 2929 | 0 | 20 | Midstream | 0.27 | 1 | 1
COM-CS-WH-531-27 | Current | Split New Construction and Natural Replacement to effectively represent baseline and efficient efficiencies. Updated savings. | Commercial | Condensing Storage Water Heater | Medium Utilization | Natural Replacement | water heating | Condensing storage water heater | All water heaters not described by UEF baseline definition with thermal efficiency >= 95% < 97%, <= 250 kBTU/hr | Non-condensing storage water heater | All water heaters not described by UEF baseline definition with thermal efficiency >= 80% |  | kBtu/hr input capacity | TRM Version 8.0 | 2024-04-30 | 0 | 2.319 | 0 | 0 | 0 | 0 | 2591 | 0 | 15 | Low-Income | 0 | 1 | 1
COM-CS-WH-531-28 | Current | Split New Construction and Natural Replacement to effectively represent baseline and efficient efficiencies. Updated savings. | Commercial | Condensing Storage Water Heater | Medium Utilization | Natural Replacement | water heating | Condensing storage water heater | All water heaters not described by UEF baseline definition with thermal efficiency >= 97%, <= 250 kBTU/hr | Non-condensing storage water heater | All water heaters not described by UEF baseline definition with thermal efficiency >= 80% |  | kBtu/hr input capacity | TRM Version 8.0 | 2024-04-30 | 0 | 2.628 | 0 | 0 | 0 | 0 | 2591 | 0 | 15 | Low-Income | 0 | 1 | 1
COM-CS-WH-531-29 | Current | Split New Construction and Natural Replacement to effectively represent baseline and efficient efficiencies. Updated savings. | Commercial | Condensing Storage Water Heater | Medium Utilization | Natural Replacement | water heating | Condensing storage water heater | All water heaters not described by UEF baseline definition with thermal efficiency >= 92% < 95%, > 250 kBTU/hr | Non-condensing storage water heater | All water heaters not described by UEF baseline definition with thermal efficiency >= 80% |  | kBtu/hr input capacity | TRM Version 8.0 | 2024-04-30 | 0 | 1.855 | 0 | 0 | 0 | 0 | 4464 | 0 | 15 | Low-Income | 0 | 1 | 1
COM-CS-WH-531-30 | Current | Split New Construction and Natural Replacement to effectively represent baseline and efficient efficiencies. Updated savings. | Commercial | Condensing Storage Water Heater | Medium Utilization | Natural Replacement | water heating | Condensing storage water heater | All water heaters not described by UEF baseline definition with thermal efficiency >= 95% < 97%, > 250 kBTU/hr | Non-condensing storage water heater | All water heaters not described by UEF baseline definition with thermal efficiency >= 80% |  | kBtu/hr input capacity | TRM Version 8.0 | 2024-04-30 | 0 | 2.319 | 0 | 0 | 0 | 0 | 4464 | 0 | 15 | Low-Income | 0 | 1 | 1
COM-CS-WH-531-31 | Current | Split New Construction and Natural Replacement to effectively represent baseline and efficient efficiencies. Updated savings. | Commercial | Condensing Storage Water Heater | Medium Utilization | Natural Replacement | water heating | Condensing storage water heater | All water heaters not described by UEF baseline definition with thermal efficiency >= 97%, > 250 kBTU/hr | Non-condensing storage water heater | All water heaters not described by UEF baseline definition with thermal efficiency >= 80% |  | kBtu/hr input capacity | TRM Version 8.0 | 2024-04-30 | 0 | 2.628 | 0 | 0 | 0 | 0 | 4464 | 0 | 15 | Low-Income | 0 | 1 | 1
COM-CS-WH-532-18 | Current | Split New Construction and Natural Replacement to effectively represent baseline and efficient efficiencies. Updated savings. | Commercial | Condensing Storage Water Heater | Medium Utilization | New Construction | water heating | Condensing storage water heater | > 75 kBTU/hr and <= 105 kBTU/hr, rated nominal volume <= 120 US gallon, single-phase power, water temp <180 deg f, UEF >= 0.86 < 0.89 | Non-condensing storage water heater | > 75 kBTU/hr and <= 105 kBTU/hr, rated nominal volume <= 120 US gallon, single-phase power, water temp <180 deg f, UEF = 0.8107 - 0.00021Vs |  | kBtu/hr input capacity | TRM Version 8.0 | 2024-04-30 | 0 | 0.952 | 0 | 0 | 0 | 0 | 2591 | 0 | 15 | Low-Income | 0 | 1 | 1
COM-CS-WH-532-19 | Current | Split New Construction and Natural Replacement to effectively represent baseline and efficient efficiencies. Updated savings. | Commercial | Condensing Storage Water Heater | Medium Utilization | New Construction | water heating | Condensing storage water heater | > 75 kBTU/hr and <= 105 kBTU/hr, rated nominal volume <= 120 US gallon, single-phase power, water temp <180 deg f, UEF >= 0.89 | Non-condensing storage water heater | > 75 kBTU/hr and <= 105 kBTU/hr, rated nominal volume <= 120 US gallon, single-phase power, water temp <180 deg f, UEF = 0.8107 - 0.00021Vs |  | kBtu/hr input capacity | TRM Version 8.0 | 2024-04-30 | 0 | 1.417 | 0 | 0 | 0 | 0 | 2591 | 0 | 15 | Low-Income | 0 | 1 | 1
COM-CS-WH-532-20 | Current | Split New Construction and Natural Replacement to effectively represent baseline and efficient efficiencies. Updated savings. | Commercial | Condensing Storage Water Heater | Medium Utilization | New Construction | water heating | Condensing storage water heater | All water heaters not described by UEF baseline definition with thermal efficiency >= 95 < 97%, <= 250 kBTU/hr | Non-condensing storage water heater | All water heaters not described by UEF baseline definition with thermal efficiency = 90% |  | kBtu/hr input capacity | TRM Version 8.0 | 2024-04-30 | 0 | 0.687 | 0 | 0 | 0 | 0 | 2591 | 0 | 15 | Low-Income | 0 | 1 | 1
COM-CS-WH-532-21 | Current | Split New Construction and Natural Replacement to effectively represent baseline and efficient efficiencies. Updated savings. | Commercial | Condensing Storage Water Heater | Medium Utilization | New Construction | water heating | Condensing storage water heater | All water heaters not described by UEF baseline definition with thermal efficiency >= 97%, <= 250 kBTU/hr | Non-condensing storage water heater | All water heaters not described by UEF baseline definition with thermal efficiency = 90% |  | kBtu/hr input capacity | TRM Version 8.0 | 2024-04-30 | 0 | 0.962 | 0 | 0 | 0 | 0 | 2591 | 0 | 15 | Low-Income | 0 | 1 | 1
COM-CS-WH-532-22 | Current | Split New Construction and Natural Replacement to effectively represent baseline and efficient efficiencies. Updated savings. | Commercial | Condensing Storage Water Heater | Medium Utilization | New Construction | water heating | Condensing storage water heater | All water heaters not described by UEF baseline definition with thermal efficiency >= 95 < 97%, > 250 kBTU/hr | Non-condensing storage water heater | All water heaters not described by UEF baseline definition with thermal efficiency = 90% |  | kBtu/hr input capacity | TRM Version 8.0 | 2024-04-30 | 0 | 0.687 | 0 | 0 | 0 | 0 | 4464 | 0 | 15 | Low-Income | 0 | 1 | 1
COM-CS-WH-532-23 | Current | Split New Construction and Natural Replacement to effectively represent baseline and efficient efficiencies. Updated savings. | Commercial | Condensing Storage Water Heater | Medium Utilization | New Construction | water heating | Condensing storage water heater | All water heaters not described by UEF baseline definition with thermal efficiency >= 97%, > 250 kBTU/hr | Non-condensing storage water heater | All water heaters not described by UEF baseline definition with thermal efficiency = 90% |  | kBtu/hr input capacity | TRM Version 8.0 | 2024-04-30 | 0 | 0.962 | 0 | 0 | 0 | 0 | 4464 | 0 | 15 | Low-Income | 0 | 1 | 1
COM-DW-WH-554-04 | Replaced | Updated in TRM Version 6.0 | Commercial | Dishwasher |  | New Construction/Natural Replacement | water heating | Energy Star Dishwasher | Single Tank Conveyor - Low Temperature | Non-Energy Star Dishwasher |  | unit |  | TRM Version 5.0 | 2020-11-12 | 1652 | 0 | 0 | 0 | 245631 | 0 | 0 | 0 | 20 | Midstream | 0.27 | 1 | 1
COM-DW-WH-551-04 | Replaced | Updated in TRM Version 6.0 | Commercial | Dishwasher |  | New Construction/Natural Replacement | water heating | Energy Star Dishwasher | Stationary Single Tank Door – High Temperature | Non-Energy Star Dishwasher |  | unit |  | TRM Version 5.0 | 2020-11-12 | 890 | 0 | 4173 | 0 | 132263 | 0 | 1100 | 0 | 15 | Midstream | 0.2 | 1 | 1
COM-DW-WH-552-04 | Replaced | Updated in TRM Version 6.0 | Commercial | Dishwasher |  | New Construction/Natural Replacement | water heating | Energy Star Dishwasher | Stationary Single Tank Door – Low Temperature | Non-Energy Star Dishwasher |  | unit |  | TRM Version 5.0 | 2020-11-12 | 2256 | 0 | 0 | 0 | 304205 | 0 | 0 | 0 | 15 | Midstream | 0.2 | 1 | 1
COM-DW-WH-549-04 | Replaced | Updated in TRM Version 6.0 | Commercial | Dishwasher |  | New Construction/Natural Replacement | water heating | Energy Star Dishwasher | Undercounter – High Temperature | Non-Energy Star Dishwasher |  | unit |  | TRM Version 5.0 | 2020-11-12 | 137 | 0 | 1791 | 0 | 20371 | 0 | 171 | 0 | 10 | Midstream | 0.4 | 1 | 1
COM-DW-WH-550-04 | Replaced | Updated in TRM Version 6.0 | Commercial | Dishwasher |  | New Construction/Natural Replacement | water heating | Energy Star Dishwasher | Undercounter – Low Temperature | Non-Energy Star Dishwasher |  | unit |  | TRM Version 5.0 | 2020-11-12 | 322 | 0 | 0 | 0 | 47827 | 0 | 71 | 0 | 10 | Midstream | 0.4 | 1 | 1
COM-CU-SH-515-03 | Replaced | Updated in TRM Version 8.0 | Commercial | Condensing Unit Heater |  | Natural Replacement | space heating | Condensing Unit Heater | 125-200 kBtu/hr 90% Thermal Efficiency, 89% Annual Efficiency | Non-Condensing Unit Heater | 80% Thermal Efficiency, 78% Annual Efficiency |  | kBtu/hr input capacity | TRM Version 6.0 | 2021-12-16 | 0 | 7.89 | -530 | 0 | 0 | 0 | 0 | 16.08 | 18 | Midstream | 0 | 1 | 1
COM-CU-SH-518-03 | Replaced | Updated in TRM Version 8.0 | Commercial | Condensing Unit Heater |  | New Construction | space heating | Condensing Unit Heater | 125-200 kBtu/hr 90% Thermal Efficiency, 89% Annual Efficiency | Non-Condensing Unit Heater | 80% Thermal Efficiency, 78% Annual Efficiency |  | kBtu/hr input capacity | TRM Version 6.0 | 2021-12-16 | 0 | 5.92 | -398 | 0 | 0 | 0 | 0 | 16.08 | 18 | Midstream | 0 | 1 | 1
COM-CU-SH-516-03 | Replaced | Updated in TRM Version 8.0 | Commercial | Condensing Unit Heater |  | Natural Replacement | space heating | Condensing Unit Heater | 225-300 kBtu/hr 90% Thermal Efficiency, 89% Annual Efficiency | Non-Condensing Unit Heater | 80% Thermal Efficiency, 78% Annual Efficiency |  | kBtu/hr input capacity | TRM Version 6.0 | 2021-12-16 | 0 | 7.89 | -546 | 0 | 0 | 0 | 0 | 16.08 | 18 | Midstream | 0 | 1 | 1
COM-CU-SH-519-03 | Replaced | Updated in TRM Version 8.0 | Commercial | Condensing Unit Heater |  | New Construction | space heating | Condensing Unit Heater | 225-300 kBtu/hr 90% Thermal Efficiency, 89% Annual Efficiency | Non-Condensing Unit Heater | 80% Thermal Efficiency, 78% Annual Efficiency |  | kBtu/hr input capacity | TRM Version 6.0 | 2021-12-16 | 0 | 5.92 | -410 | 0 | 0 | 0 | 0 | 16.08 | 18 | Midstream | 0 | 1 | 1
COM-CU-SH-514-03 | Replaced | Updated in TRM Version 8.0 | Commercial | Condensing Unit Heater |  | Natural Replacement | space heating | Condensing Unit Heater | 30-100 kBtu/hr - 90% Thermal Efficiency, 89% Annual Efficiency | Non-Condensing Unit Heater | 80% Thermal Efficiency, 78% Annual Efficiency |  | kBtu/hr input capacity | TRM Version 6.0 | 2021-12-16 | 0 | 7.89 | -296 | 0 | 0 | 0 | 0 | 16.08 | 18 | Midstream | 0 | 1 | 1
COM-CU-SH-517-03 | Replaced | Updated in TRM Version 8.0 | Commercial | Condensing Unit Heater |  | New Construction | space heating | Condensing Unit Heater | 30-100 kBtu/hr - 90% Thermal Efficiency, 89% Annual Efficiency | Non-Condensing Unit Heater | 80% Thermal Efficiency, 78% Annual Efficiency |  | kBtu/hr input capacity | TRM Version 6.0 | 2021-12-16 | 0 | 5.92 | -222 | 0 | 0 | 0 | 0 | 16.08 | 18 | Midstream | 0 | 1 | 1
COM-DW-WH-555-04 | Replaced | Updated in TRM Version 7.0; revised from TRM Version 5.0: natural gas, electric savings, and water savings | Commercial | Dishwasher |  | New Construction/Natural Replacement | water heating | Energy Star Dishwasher | Multi Tank Conveyor - High Temperature | Non-Energy Star Dishwasher |  | unit |  | TRM Version 6.0 | 2021-12-16 | 2260 | 0 | 10673 | 0 | 335926 | 0 | 1386 | 0 | 20 | Midstream | 0.27 | 1 | 1
COM-DW-WH-556-04 | Replaced | Updated in TRM Version 7.0; revised from TRM Version 5.0: natural gas, electric savings, and water savings | Commercial | Dishwasher |  | New Construction/Natural Replacement | water heating | Energy Star Dishwasher | Multi Tank Conveyor - Low Temperature | Non-Energy Star Dishwasher |  | unit |  | TRM Version 6.0 | 2021-12-16 | 2628 | 0 | 0 | 0 | 390612 | 0 | 1386 | 0 | 20 | Midstream | 0.27 | 1 | 1
COM-DW-WH-553-04 | Replaced | Updated in TRM Version 7.0; revised from TRM Version 5.0: natural gas, electric savings, and water savings | Commercial | Dishwasher |  | New Construction/Natural Replacement | water heating | Energy Star Dishwasher | Single Tank Conveyor – High Temperature | Non-Energy Star Dishwasher |  | unit |  | TRM Version 6.0 | 2021-12-16 | 596 | 0 | 4686 | 0 | 88539 | 0 | 2929 | 0 | 20 | Midstream | 0.27 | 1 | 1
COM-DW-WH-554-04 | Replaced | Updated in TRM Version 7.0; revised from TRM Version 5.0: natural gas, electric savings, and water savings | Commercial | Dishwasher |  | New Construction/Natural Replacement | water heating | Energy Star Dishwasher | Single Tank Conveyor - Low Temperature | Non-Energy Star Dishwasher |  | unit |  | TRM Version 6.0 | 2021-12-16 | 1822 | 0 | 0 | 0 | 270824 | 0 | 0 | 0 | 20 | Midstream | 0.27 | 1 | 1
COM-DW-WH-551-04 | Replaced | Updated in TRM Version 7.0; revised from TRM Version 5.0: natural gas, electric savings, and water savings | Commercial | Dishwasher |  | New Construction/Natural Replacement | water heating | Energy Star Dishwasher | Stationary Single Tank Door – High Temperature | Non-Energy Star Dishwasher |  | unit |  | TRM Version 6.0 | 2021-12-16 | 981 | 0 | 4601 | 0 | 145828 | 0 | 1100 | 0 | 15 | Midstream | 0.2 | 1 | 1
COM-DW-WH-552-04 | Replaced | Updated in TRM Version 7.0; revised from TRM Version 5.0: natural gas, electric savings, and water savings | Commercial | Dishwasher |  | New Construction/Natural Replacement | water heating | Energy Star Dishwasher | Stationary Single Tank Door – Low Temperature | Non-Energy Star Dishwasher |  | unit |  | TRM Version 6.0 | 2021-12-16 | 2256 | 0 | 0 | 0 | 335406 | 0 | 0 | 0 | 15 | Midstream | 0.2 | 1 | 1
COM-DW-WH-549-04 | Replaced | Updated in TRM Version 7.0; revised from TRM Version 5.0: natural gas, electric savings, and water savings | Commercial | Dishwasher |  | New Construction/Natural Replacement | water heating | Energy Star Dishwasher | Undercounter – High Temperature | Non-Energy Star Dishwasher |  | unit |  | TRM Version 6.0 | 2021-12-16 | 151 | 0 | 1975 | 0 | 22460 | 0 | 171 | 0 | 10 | Midstream | 0.4 | 1 | 1
COM-DW-WH-550-04 | Replaced | Updated in TRM Version 7.0; revised from TRM Version 5.0: natural gas, electric savings, and water savings | Commercial | Dishwasher |  | New Construction/Natural Replacement | water heating | Energy Star Dishwasher | Undercounter – Low Temperature | Non-Energy Star Dishwasher |  | unit |  | TRM Version 6.0 | 2021-12-16 | 355 | 0 | 0 | 0 | 52733 | 0 | 71 | 0 | 10 | Midstream | 0.4 | 1 | 1
COM-CF-SH-494-03 | Current |  | Commercial | Condensing Furnace |  | New Construction | space heating | High Efficiency Condensing Furnace | >=97% AFUE | Condensing Furnace | 95% AFUE |  | kBtu/hr | TRM Version 5.0 | 2020-11-12 | 0 | 0.884 | 0 | 0 | 0 | 0 | 188 | 0 | 18 | Midstream | 0.175 | 1 | 1
COM-CF-SH-495-03 | Current |  | Commercial | Condensing Furnace |  | Natural Replacement | space heating | High Efficiency Condensing Furnace | >=97% AFUE | Condensing Furnace | 95% AFUE |  | kBtu/hr | TRM Version 5.0 | 2020-11-12 | 0 | 1.178 | 0 | 0 | 0 | 0 | 188 | 0 | 18 | Midstream | 0.175 | 1 | 1
COM-DS-SH-560-04 | Current |  | Commercial | Dock Door Seals |  | Retrofit | space heating | Dock Door Seals | 10' x 10' | Dock door with deteriorated seals |  | unit |  | TRM Version 5.0 | 2020-11-12 | 1736 | 0 | 433 | 0 | 0 | 0 | 2968 | 0 | 10 | Midstream | 0.05 | 1 | 1
COM-DS-SH-564-04 | Current |  | Commercial | Dock Door Seals |  | Retrofit | space heating | Dock Door Seals | 10' x 10' | Dock door without seals |  | unit |  | TRM Version 5.0 | 2020-11-12 | 4501 | 0 | 1123 | 0 | 0 | 0 | 2615 | 0 | 10 | Midstream | 0.05 | 1 | 1
COM-CM-SH-497-03 | Current |  | Commercial | Condensing Make Up Air Unit | Commercial | New Construction/Natural Replacement | space heating | Condensing Make Up Air Unit (MUA) - Commercial | 2 Speed | Conventional MUA | 80% Thermal Efficiency |  | CFM | TRM Version 5.0 | 2020-11-12 | 0 | 1.22 | 0 | 1.24 | 0 | 0 | 870 | 1.01 | 20 | Midstream | 0.05 | 1 | 1
COM-CM-SH-500-03 | Current |  | Commercial | Condensing Make Up Air Unit | Multi-Residential and Long Term Care | New Construction/Natural Replacement | space heating | Condensing Make Up Air Unit (MUA) - Commercial | 2 Speed | Conventional MUA | 80% Thermal Efficiency |  | CFM | TRM Version 5.0 | 2020-11-12 | 0 | 2.45 | 0 | 1.61 | 0 | 0 | 870 | 1.01 | 20 | Midstream | 0.05 | 1 | 1
COM-DF-SH-545-04 | Current |  | Commercial | Destratification Fans |  | New Construction | space heating | HVLS (High Volume Low Speed) Destratification Fans | 20 ft fan diameter | No destratification fans |  | fan |  | TRM Version 5.0 | 2020-11-12 | 1472 | 0 | 0 | 0 | 0 | 0 | 7961 | 0 | 15 | Midstream | 0.1 | 1 | 1
COM-DF-SH-546-04 | Current |  | Commercial | Destratification Fans |  | Retrofit | space heating | HVLS (High Volume Low Speed) Destratification Fans | 20 ft fan diameter | No destratification fans |  | fan |  | TRM Version 5.0 | 2020-11-12 | 2029 | 0 | 0 | 0 | 0 | 0 | 7961 | 0 | 15 | Midstream | 0.1 | 1 | 1
COM-DF-SH-547-04 | Current |  | Commercial | Destratification Fans |  | New Construction | space heating | HVLS (High Volume Low Speed) Destratification Fans | 24 ft fan diameter | No destratification fans |  | fan |  | TRM Version 5.0 | 2020-11-12 | 2120 | 0 | 0 | 0 | 0 | 0 | 7961 | 0 | 15 | Midstream | 0.1 | 1 | 1
COM-DF-SH-548-04 | Current |  | Commercial | Destratification Fans |  | Retrofit | space heating | HVLS (High Volume Low Speed) Destratification Fans | 24 ft fan diameter | No destratification fans |  | fan |  | TRM Version 5.0 | 2020-11-12 | 2922 | 0 | 0 | 0 | 0 | 0 | 7961 | 0 | 15 | Midstream | 0.1 | 1 | 1
COM-DS-SH-559-04 | Current |  | Commercial | Dock Door Seals |  | Retrofit | space heating | Dock Door Seals | 8' x 10' | Dock door with deteriorated seals |  | unit |  | TRM Version 5.0 | 2020-11-12 | 2041 | 0 | 509 | 0 | 0 | 0 | 1617 | 0 | 10 | Midstream | 0.05 | 1 | 1
COM-DS-SH-563-04 | Current |  | Commercial | Dock Door Seals |  | Retrofit | space heating | Dock Door Seals | 8' x 10' | Dock door without seals |  | unit |  | TRM Version 5.0 | 2020-11-12 | 5087 | 0 | 1269 | 0 | 0 | 0 | 1455 | 0 | 10 | Midstream | 0.05 | 1 | 1
COM-DS-SH-557-04 | Current |  | Commercial | Dock Door Seals |  | Retrofit | space heating | Dock Door Seals | 8' x 8' | Dock door with deteriorated seals |  | unit |  | TRM Version 5.0 | 2020-11-12 | 1897 | 0 | 451 | 0 | 0 | 0 | 1425 | 0 | 10 | Midstream | 0.05 | 1 | 1
COM-DS-SH-561-04 | Current |  | Commercial | Dock Door Seals |  | Retrofit | space heating | Dock Door Seals | 8' x 8' | Dock door without seals |  | unit |  | TRM Version 5.0 | 2020-11-12 | 4853 | 0 | 1155 | 0 | 0 | 0 | 1263 | 0 | 10 | Midstream | 0.05 | 1 | 1
COM-DS-SH-558-04 | Current |  | Commercial | Dock Door Seals |  | Retrofit | space heating | Dock Door Seals | 8' x 9' | Dock door with deteriorated seals |  | unit |  | TRM Version 5.0 | 2020-11-12 | 1977 | 0 | 481 | 0 | 0 | 0 | 1580 | 0 | 10 | Midstream | 0.05 | 1 | 1
COM-DS-SH-562-04 | Current |  | Commercial | Dock Door Seals |  | Retrofit | space heating | Dock Door Seals | 8' x 9' | Dock door without seals |  | unit |  | TRM Version 5.0 | 2020-11-12 | 4988 | 0 | 1214 | 0 | 0 | 0 | 1417 | 0 | 10 | Midstream | 0.05 | 1 | 1
RES-AT-SH-321-02 | Current |  | Residential | Adaptive Thermostat |  | New Construction | space heating | Adaptive Thermostats | Adaptive Thermostat | Programmable Thermostat |  | unit |  | TRM Version 5.0 | 2020-11-12 | 105 | 0 | 206 | 0 | 0 | 0 | 200 | 0 | 15 | Midstream | 0.04 | 1 | 1
RES-AT-SH-322-02 | Current |  | Residential | Adaptive Thermostat |  | Retrofit | space heating | Adaptive Thermostats - Retail Purchase | Adaptive Thermostat | Blended value. Non Programmable and programmable Thermostat |  | unit |  | TRM Version 5.0 | 2020-11-12 | 185 | 0 | 176 | 0 | 0 | 0 | 300 | 0 | 15 | Midstream | 0.04 | 1 | 1
MRS-FA-WH-461-09 | Current |  | Commercial | Faucet Aerator | Multi-residential | Retrofit | water heating | Faucet Aerator | Bathroom, 1.0 GPM | Standard flow bathroom aerator (code compliant) | 2.2 GPM | unit |  | TRM Version 7.0 | 2022-11-30 | 6.65 | 0 | 0 | 0 | 2501 | 0 | 0.6 | 0 | 10 | Midstream | 0.1 | 1 | 1
MRS-FA-WH-460-09 | Current |  | Commercial | Faucet Aerator | Multi-residential | Retrofit | water heating | Faucet Aerator | Bathroom, 1.5 GPM | Standard flow bathroom aerator (code compliant) | 2.2 GPM | unit |  | TRM Version 7.0 | 2022-11-30 | 3.88 | 0 | 0 | 0 | 1459 | 0 | 0.6 | 0 | 10 | Midstream | 0.1 | 1 | 1
COM-CM-SH-496-03 | Current |  | Commercial | Condensing Make Up Air Unit | Commercial | New Construction/Natural Replacement | space heating | Condensing Make Up Air Unit (MUA) - Commercial | Constant Speed | Conventional MUA | 80% Thermal Efficiency |  | CFM | TRM Version 5.0 | 2020-11-12 | 0 | 0.407 | 0 | 0 | 0 | 0 | 870 | 0.66 | 20 | Midstream | 0.05 | 1 | 1
COM-CM-SH-499-03 | Current |  | Commercial | Condensing Make Up Air Unit | Multi-Residential and Long Term Care | New Construction/Natural Replacement | space heating | Condensing Make Up Air Unit (MUA) - Commercial | Constant Speed | Conventional MUA | 80% Thermal Efficiency |  | CFM | TRM Version 5.0 | 2020-11-12 | 0 | 0.919 | 0 | 0 | 0 | 0 | 870 | 0.66 | 20 | Midstream | 0.05 | 1 | 1
COM-HRV-SH-336-03 | Current |  | Commercial | Heat Recovery Ventialation | High Use | New Construction/Natural Replacement | space heating | High Efficient 65% Heat Recovery Ventilation High Use Group (Multi-Residential, Health Care, Nursing Homes) | HRV with Minimum 65% Sensible Heat Recovery Effectiveness at 32°F | HRV with Minimum 55% Sensible Heat Recovery Effectiveness as per Ontario Building Code 2017 |  |  | CFM | TRM Version 5.0 | 2020-11-12 | 0 | 0.7 | 0 | 0 | 0 | 0 | 0 | 1 | 14 | Midstream | 0.05 | 1 | 1
COM-HRV-SH-337-03 | Current |  | Commercial | Heat Recovery Ventialation | Low Use | New Construction/Natural Replacement | space heating | High Efficient 65% Heat Recovery Ventilation Low Use Group (Office, Warehouse, School) | HRV with Minimum 65% Sensible Heat Recovery Effectiveness at 32°F | HRV with Minimum 55% Sensible Heat Recovery Effectiveness as per Ontario Building Code 2017 |  |  | CFM | TRM Version 5.0 | 2020-11-12 | 0 | 0.25 | 0 | 0 | 0 | 0 | 0 | 1 | 14 | Midstream | 0.05 | 1 | 1
COM-HRV-SH-338-03 | Current |  | Commercial | Heat Recovery Ventialation | Medium Use | New Construction/Natural Replacement | space heating | High Efficient 65% Heat Recovery Ventilation Medium Use Group (Hotel, Restaurant, Retail) | HRV with Minimum 65% Sensible Heat Recovery Effectiveness at 32°F | HRV with Minimum 55% Sensible Heat Recovery Effectiveness as per Ontario Building Code 2017 |  |  | CFM | TRM Version 5.0 | 2020-11-12 | 0 | 0.39 | 0 | 0 | 0 | 0 | 0 | 1 | 14 | Midstream | 0.05 | 1 | 1
COM-HRV-SH-345-03 | Current |  | Commercial | Heat Recovery Ventialation | Multi-Family, Health Care and Nursing Homes | New Construction/Natural Replacement | space heating | High Efficient 65% Heat Recovery Ventilation High Use Group (Multi-Residential, Health Care, Nursing Homes) | HRV with Minimum 65% Sensible Heat Recovery Effectiveness at 32°F | HRV with Minimum 55% Sensible Heat Recovery Effectiveness as per Ontario Building Code 2017 |  |  | CFM | TRM Version 5.0 | 2020-11-12 | 0 | 0.7 | 0 | 0 | 0 | 0 | 0 | 1 | 14 | Midstream | 0.05 | 1 | 1
COM-HRV-SH-346-03 | Current |  | Commercial | Heat Recovery Ventialation | Hotels | New Construction/Natural Replacement | space heating | High Efficient 65% Heat Recovery Ventilation Medium Use Group (Hotel, Restaurant, Retail) | HRV with Minimum 65% Sensible Heat Recovery Effectiveness at 32°F | HRV with Minimum 55% Sensible Heat Recovery Effectiveness as per Ontario Building Code 2017 |  |  | CFM | TRM Version 5.0 | 2020-11-12 | 0 | 0.5 | 0 | 0 | 0 | 0 | 0 | 1 | 14 | Midstream | 0.05 | 1 | 1
COM-HRV-SH-347-03 | Current |  | Commercial | Heat Recovery Ventialation | Restaurant | New Construction/Natural Replacement | space heating | High Efficient 65% Heat Recovery Ventilation Medium Use Group (Hotel, Restaurant, Retail) | HRV with Minimum 65% Sensible Heat Recovery Effectiveness at 32°F | HRV with Minimum 55% Sensible Heat Recovery Effectiveness as per Ontario Building Code 2017 |  |  | CFM | TRM Version 5.0 | 2020-11-12 | 0 | 0.36 | 0 | 0 | 0 | 0 | 0 | 1 | 14 | Midstream | 0.05 | 1 | 1
COM-HRV-SH-348-03 | Current |  | Commercial | Heat Recovery Ventialation | Retail | New Construction/Natural Replacement | space heating | High Efficient 65% Heat Recovery Ventilation Medium Use Group (Hotel, Restaurant, Retail) | HRV with Minimum 65% Sensible Heat Recovery Effectiveness at 32°F | HRV with Minimum 55% Sensible Heat Recovery Effectiveness as per Ontario Building Code 2017 |  |  | CFM | TRM Version 5.0 | 2020-11-12 | 0 | 0.3 | 0 | 0 | 0 | 0 | 0 | 1 | 14 | Midstream | 0.05 | 1 | 1
COM-HRV-SH-349-03 | Current |  | Commercial | Heat Recovery Ventialation | Office | New Construction/Natural Replacement | space heating | High Efficient 65% Heat Recovery Ventilation Low Use Group (Office, Warehouse, School) | HRV with Minimum 65% Sensible Heat Recovery Effectiveness at 32°F | HRV with Minimum 55% Sensible Heat Recovery Effectiveness as per Ontario Building Code 2017 |  |  | CFM | TRM Version 5.0 | 2020-11-12 | 0 | 0.27 | 0 | 0 | 0 | 0 | 0 | 1 | 14 | Midstream | 0.05 | 1 | 1
COM-HRV-SH-350-03 | Current |  | Commercial | Heat Recovery Ventialation | Warehouse | New Construction/Natural Replacement | space heating | High Efficient 65% Heat Recovery Ventilation Low Use Group (Office, Warehouse, School) | HRV with Minimum 65% Sensible Heat Recovery Effectiveness at 32°F | HRV with Minimum 55% Sensible Heat Recovery Effectiveness as per Ontario Building Code 2017 |  |  | CFM | TRM Version 5.0 | 2020-11-12 | 0 | 0.25 | 0 | 0 | 0 | 0 | 0 | 1 | 14 | Midstream | 0.05 | 1 | 1
COM-HRV-SH-351-03 | Current |  | Commercial | Heat Recovery Ventialation | School | New Construction/Natural Replacement | space heating | High Efficient 65% Heat Recovery Ventilation Low Use Group (Office, Warehouse, School) | HRV with Minimum 65% Sensible Heat Recovery Effectiveness at 32°F | HRV with Minimum 55% Sensible Heat Recovery Effectiveness as per Ontario Building Code 2017 |  |  | CFM | TRM Version 5.0 | 2020-11-12 | 0 | 0.22 | 0 | 0 | 0 | 0 | 0 | 1 | 14 | Midstream | 0.05 | 1 | 1
COM-HRV-SH-339-03 | Current |  | Commercial | Heat Recovery Ventialation | High Use | New Construction/Natural Replacement | space heating | High Efficient 75% Heat Recovery Ventilation High Use Group (Multi-Residential, Health Care, Nursing Homes) | HRV with Minimum 75% Sensible Heat Recovery Effectiveness at 32°F | HRV with Minimum 55% Sensible Heat Recovery Effectiveness as per Ontario Building Code 2017 |  |  | CFM | TRM Version 5.0 | 2020-11-12 | 0 | 1.39 | 0 | 0 | 0 | 0 | 0 | 2 | 14 | Midstream | 0.05 | 1 | 1
COM-HRV-SH-340-03 | Current |  | Commercial | Heat Recovery Ventialation | Low Use | New Construction/Natural Replacement | space heating | High Efficient 75% Heat Recovery Ventilation Low Use Group (Office, Warehouse, School) | HRV with Minimum 75% Sensible Heat Recovery Effectiveness at 32°F | HRV with Minimum 55% Sensible Heat Recovery Effectiveness as per Ontario Building Code 2017 |  |  | CFM | TRM Version 5.0 | 2020-11-12 | 0 | 0.5 | 0 | 0 | 0 | 0 | 0 | 2 | 14 | Midstream | 0.05 | 1 | 1
COM-HRV-SH-341-03 | Current |  | Commercial | Heat Recovery Ventialation | Medium Use | New Construction/Natural Replacement | space heating | High Efficient 75% Heat Recovery Ventilation Medium Use Group (Hotel, Restaurant, Retail) | HRV with Minimum 75% Sensible Heat Recovery Effectiveness at 32°F | HRV with Minimum 55% Sensible Heat Recovery Effectiveness as per Ontario Building Code 2017 |  |  | CFM | TRM Version 5.0 | 2020-11-12 | 0 | 0.78 | 0 | 0 | 0 | 0 | 0 | 2 | 14 | Midstream | 0.05 | 1 | 1
COM-HRV-SH-352-03 | Current |  | Commercial | Heat Recovery Ventialation | Multi-Family, Health Care and Nursing Homes | New Construction/Natural Replacement | space heating | High Efficient 75% Heat Recovery Ventilation High Use Group (Multi-Residential, Health Care, Nursing Homes) | HRV with Minimum 75% Sensible Heat Recovery Effectiveness at 32°F | HRV with Minimum 55% Sensible Heat Recovery Effectiveness as per Ontario Building Code 2017 |  |  | CFM | TRM Version 5.0 | 2020-11-12 | 0 | 1.39 | 0 | 0 | 0 | 0 | 0 | 2 | 14 | Midstream | 0.05 | 1 | 1
COM-HRV-SH-353-03 | Current |  | Commercial | Heat Recovery Ventialation | Hotels | New Construction/Natural Replacement | space heating | High Efficient 75% Heat Recovery Ventilation Medium Use Group (Hotel, Restaurant, Retail) | HRV with Minimum 75% Sensible Heat Recovery Effectiveness at 32°F | HRV with Minimum 55% Sensible Heat Recovery Effectiveness as per Ontario Building Code 2017 |  |  | CFM | TRM Version 5.0 | 2020-11-12 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 2 | 14 | Midstream | 0.05 | 1 | 1
COM-HRV-SH-354-03 | Current |  | Commercial | Heat Recovery Ventialation | Restaurant | New Construction/Natural Replacement | space heating | High Efficient 75% Heat Recovery Ventilation Medium Use Group (Hotel, Restaurant, Retail) | HRV with Minimum 75% Sensible Heat Recovery Effectiveness at 32°F | HRV with Minimum 55% Sensible Heat Recovery Effectiveness as per Ontario Building Code 2017 |  |  | CFM | TRM Version 5.0 | 2020-11-12 | 0 | 0.72 | 0 | 0 | 0 | 0 | 0 | 2 | 14 | Midstream | 0.05 | 1 | 1
COM-HRV-SH-355-03 | Current |  | Commercial | Heat Recovery Ventialation | Retail | New Construction/Natural Replacement | space heating | High Efficient 75% Heat Recovery Ventilation Medium Use Group (Hotel, Restaurant, Retail) | HRV with Minimum 75% Sensible Heat Recovery Effectiveness at 32°F | HRV with Minimum 55% Sensible Heat Recovery Effectiveness as per Ontario Building Code 2017 |  |  | CFM | TRM Version 5.0 | 2020-11-12 | 0 | 0.61 | 0 | 0 | 0 | 0 | 0 | 2 | 14 | Midstream | 0.05 | 1 | 1
COM-HRV-SH-356-03 | Current |  | Commercial | Heat Recovery Ventialation | Office | New Construction/Natural Replacement | space heating | High Efficient 75% Heat Recovery Ventilation Low Use Group (Office, Warehouse, School) | HRV with Minimum 75% Sensible Heat Recovery Effectiveness at 32°F | HRV with Minimum 55% Sensible Heat Recovery Effectiveness as per Ontario Building Code 2017 |  |  | CFM | TRM Version 5.0 | 2020-11-12 | 0 | 0.53 | 0 | 0 | 0 | 0 | 0 | 2 | 14 | Midstream | 0.05 | 1 | 1
COM-HRV-SH-357-03 | Current |  | Commercial | Heat Recovery Ventialation | Warehouse | New Construction/Natural Replacement | space heating | High Efficient 75% Heat Recovery Ventilation Low Use Group (Office, Warehouse, School) | HRV with Minimum 75% Sensible Heat Recovery Effectiveness at 32°F | HRV with Minimum 55% Sensible Heat Recovery Effectiveness as per Ontario Building Code 2017 |  |  | CFM | TRM Version 5.0 | 2020-11-12 | 0 | 0.51 | 0 | 0 | 0 | 0 | 0 | 2 | 14 | Midstream | 0.05 | 1 | 1
COM-HRV-SH-358-03 | Current |  | Commercial | Heat Recovery Ventialation | School | New Construction/Natural Replacement | space heating | High Efficient 75% Heat Recovery Ventilation Low Use Group (Office, Warehouse, School) | HRV with Minimum 75% Sensible Heat Recovery Effectiveness at 32°F | HRV with Minimum 55% Sensible Heat Recovery Effectiveness as per Ontario Building Code 2017 |  |  | CFM | TRM Version 5.0 | 2020-11-12 | 0 | 0.45 | 0 | 0 | 0 | 0 | 0 | 2 | 14 | Midstream | 0.05 | 1 | 1
COM-HRV-SH-342-03 | Current |  | Commercial | Heat Recovery Ventialation | High Use | New Construction/Natural Replacement | space heating | High Efficient 85% Heat Recovery Ventilation High Use Group (Multi-Residential, Health Care, Nursing Homes) | HRV with Minimum 85% Sensible Heat Recovery Effectiveness at 32°F | HRV with Minimum 55% Sensible Heat Recovery Effectiveness as per Ontario Building Code 2017 |  |  | CFM | TRM Version 5.0 | 2020-11-12 | 0 | 2.09 | 0 | 0 | 0 | 0 | 0 | 3 | 14 | Midstream | 0.05 | 1 | 1
COM-HRV-SH-343-03 | Current |  | Commercial | Heat Recovery Ventialation | Low Use | New Construction/Natural Replacement | space heating | High Efficient 85% Heat Recovery Ventilation Low Use Group (Office, Warehouse, School) | HRV with Minimum 85% Sensible Heat Recovery Effectiveness at 32°F | HRV with Minimum 55% Sensible Heat Recovery Effectiveness as per Ontario Building Code 2017 |  |  | CFM | TRM Version 5.0 | 2020-11-12 | 0 | 0.74 | 0 | 0 | 0 | 0 | 0 | 3 | 14 | Midstream | 0.05 | 1 | 1
COM-HRV-SH-344-03 | Current |  | Commercial | Heat Recovery Ventialation | Medium Use | New Construction/Natural Replacement | space heating | High Efficient 85% Heat Recovery Ventilation Medium Use Group (Hotel, Restaurant, Retail) | HRV with Minimum 85% Sensible Heat Recovery Effectiveness at 32°F | HRV with Minimum 55% Sensible Heat Recovery Effectiveness as per Ontario Building Code 2017 |  |  | CFM | TRM Version 5.0 | 2020-11-12 | 0 | 1.16 | 0 | 0 | 0 | 0 | 0 | 3 | 14 | Midstream | 0.05 | 1 | 1
COM-HRV-SH-359-03 | Current |  | Commercial | Heat Recovery Ventialation | Multi-Family, Health Care and Nursing Homes | New Construction/Natural Replacement | space heating | High Efficient 85% Heat Recovery Ventilation High Use Group (Multi-Residential, Health Care, Nursing Homes) | HRV with Minimum 85% Sensible Heat Recovery Effectiveness at 32°F | HRV with Minimum 55% Sensible Heat Recovery Effectiveness as per Ontario Building Code 2017 |  |  | CFM | TRM Version 5.0 | 2020-11-12 | 0 | 2.09 | 0 | 0 | 0 | 0 | 0 | 3 | 14 | Midstream | 0.05 | 1 | 1
COM-HRV-SH-360-03 | Current |  | Commercial | Heat Recovery Ventialation | Hotels | New Construction/Natural Replacement | space heating | High Efficient 85% Heat Recovery Ventilation Medium Use Group (Hotel, Restaurant, Retail) | HRV with Minimum 85% Sensible Heat Recovery Effectiveness at 32°F | HRV with Minimum 55% Sensible Heat Recovery Effectiveness as per Ontario Building Code 2017 |  |  | CFM | TRM Version 5.0 | 2020-11-12 | 0 | 1.49 | 0 | 0 | 0 | 0 | 0 | 3 | 14 | Midstream | 0.05 | 1 | 1
COM-HRV-SH-361-03 | Current |  | Commercial | Heat Recovery Ventialation | Restaurant | New Construction/Natural Replacement | space heating | High Efficient 85% Heat Recovery Ventilation Medium Use Group (Hotel, Restaurant, Retail) | HRV with Minimum 85% Sensible Heat Recovery Effectiveness at 32°F | HRV with Minimum 55% Sensible Heat Recovery Effectiveness as per Ontario Building Code 2017 |  |  | CFM | TRM Version 5.0 | 2020-11-12 | 0 | 1.08 | 0 | 0 | 0 | 0 | 0 | 3 | 14 | Midstream | 0.05 | 1 | 1
COM-HRV-SH-362-03 | Current |  | Commercial | Heat Recovery Ventialation | Retail | New Construction/Natural Replacement | space heating | High Efficient 85% Heat Recovery Ventilation Medium Use Group (Hotel, Restaurant, Retail) | HRV with Minimum 85% Sensible Heat Recovery Effectiveness at 32°F | HRV with Minimum 55% Sensible Heat Recovery Effectiveness as per Ontario Building Code 2017 |  |  | CFM | TRM Version 5.0 | 2020-11-12 | 0 | 0.91 | 0 | 0 | 0 | 0 | 0 | 3 | 14 | Midstream | 0.05 | 1 | 1
COM-HRV-SH-363-03 | Current |  | Commercial | Heat Recovery Ventialation | Office | New Construction/Natural Replacement | space heating | High Efficient 85% Heat Recovery Ventilation Low Use Group (Office, Warehouse, School) | HRV with Minimum 85% Sensible Heat Recovery Effectiveness at 32°F | HRV with Minimum 55% Sensible Heat Recovery Effectiveness as per Ontario Building Code 2017 |  |  | CFM | TRM Version 5.0 | 2020-11-12 | 0 | 0.8 | 0 | 0 | 0 | 0 | 0 | 3 | 14 | Midstream | 0.05 | 1 | 1
COM-HRV-SH-364-03 | Current |  | Commercial | Heat Recovery Ventialation | Warehouse | New Construction/Natural Replacement | space heating | High Efficient 85% Heat Recovery Ventilation Low Use Group (Office, Warehouse, School) | HRV with Minimum 85% Sensible Heat Recovery Effectiveness at 32°F | HRV with Minimum 55% Sensible Heat Recovery Effectiveness as per Ontario Building Code 2017 |  |  | CFM | TRM Version 5.0 | 2020-11-12 | 0 | 0.76 | 0 | 0 | 0 | 0 | 0 | 3 | 14 | Midstream | 0.05 | 1 | 1
COM-HRV-SH-365-03 | Current |  | Commercial | Heat Recovery Ventialation | School | New Construction/Natural Replacement | space heating | High Efficient 85% Heat Recovery Ventilation Low Use Group (Office, Warehouse, School) | HRV with Minimum 85% Sensible Heat Recovery Effectiveness at 32°F | HRV with Minimum 55% Sensible Heat Recovery Effectiveness as per Ontario Building Code 2017 |  |  | CFM | TRM Version 5.0 | 2020-11-12 | 0 | 0.67 | 0 | 0 | 0 | 0 | 0 | 3 | 14 | Midstream | 0.05 | 1 | 1
MRS-FA-WH-462-09 | Current |  | Commercial | Faucet Aerator | Multi-residential | Retrofit | water heating | Faucet Aerator | Kitchen, 1.0 GPM | Standard flow kitchen aerator (code compliant) | 2.2 GPM | unit |  | TRM Version 7.0 | 2022-11-30 | 20.57 | 0 | 0 | 0 | 7742 | 0 | 1.14 | 0 | 10 | Midstream | 0.1 | 1 | 1
MRS-FA-WH-463-09 | Current |  | Commercial | Faucet Aerator | Multi-residential | Retrofit | water heating | Faucet Aerator | Kitchen, 1.5 GPM | Standard flow kitchen aerator (code compliant) | 2.2 GPM | unit |  | TRM Version 7.0 | 2022-11-30 | 12 | 0 | 0 | 0 | 4516 | 0 | 1.14 | 0 | 10 | Midstream | 0.1 | 1 | 1
COM-ERV-SH-380-09 | Current |  | Commercial | Energy Recovery Ventilation | High Use Group | New Construction/Natural Replacement | space heating | High Efficient 65% Energy Recovery Ventilation High Use Group (Multi-Residential, Health Care, Nursing Homes) | Minimum 65% Sensible Heat Recovery Effectiveness and 63% Total Energy Recovery Effectiveness at 32°F | Minimum 55% Energy Recovery Effectiveness as per Ontario Building Code 2017 |  |  | CFM | TRM Version 5.0 | 2020-11-12 | 0 | 0.85 | 0 | 0 | 0 | 0 | 0 | 1 | 14 | Midstream | 0.05 | 1 | 1
COM-ERV-SH-381-09 | Current |  | Commercial | Energy Recovery Ventilation | Medium Use Group | New Construction/Natural Replacement | space heating | High Efficient 65% Energy Recovery Ventilation Medium Use Group (Hotel, Restaurant, Retail) | Minimum 65% Sensible Heat Recovery Effectiveness and 63% Total Energy Recovery Effectiveness at 32°F | Minimum 55% Energy Recovery Effectiveness as per Ontario Building Code 2017 |  |  | CFM | TRM Version 5.0 | 2020-11-12 | 0 | 0.47 | 0 | 0 | 0 | 0 | 0 | 1 | 14 | Midstream | 0.05 | 1 | 1
COM-ERV-SH-382-09 | Current |  | Commercial | Energy Recovery Ventilation | Low Use Group | New Construction/Natural Replacement | space heating | High Efficient 65% Energy Recovery Ventilation Low Use Group (Office, Warehouse, School) | Minimum 65% Sensible Heat Recovery Effectiveness and 63% Total Energy Recovery Effectiveness at 32°F | Minimum 55% Energy Recovery Effectiveness as per Ontario Building Code 2017 |  |  | CFM | TRM Version 5.0 | 2020-11-12 | 0 | 0.3 | 0 | 0 | 0 | 0 | 0 | 1 | 14 | Midstream | 0.05 | 1 | 1
COM-ERV-SH-383-09 | Current |  | Commercial | Energy Recovery Ventilation | Multi-Residential, Health Care, Nursing Homes | New Construction/Natural Replacement | space heating | High Efficient 65% Energy Recovery Ventilation High Use Group (Multi-Residential, Health Care, Nursing Homes) | Minimum 65% Sensible Heat Recovery Effectiveness and 63% Total Energy Recovery Effectiveness at 32°F | Minimum 55% Energy Recovery Effectiveness as per Ontario Building Code 2017 |  |  | CFM | TRM Version 5.0 | 2020-11-12 | 0 | 0.85 | 0 | 0 | 0 | 0 | 0 | 1 | 14 | Midstream | 0.05 | 1 | 1
COM-ERV-SH-384-09 | Current |  | Commercial | Energy Recovery Ventilation | Hotel | New Construction/Natural Replacement | space heating | High Efficient 65% Energy Recovery Ventilation Medium Use Group (Hotel, Restaurant, Retail) | Minimum 65% Sensible Heat Recovery Effectiveness and 63% Total Energy Recovery Effectiveness at 32°F | Minimum 55% Energy Recovery Effectiveness as per Ontario Building Code 2017 |  |  | CFM | TRM Version 5.0 | 2020-11-12 | 0 | 0.61 | 0 | 0 | 0 | 0 | 0 | 1 | 14 | Midstream | 0.05 | 1 | 1
COM-ERV-SH-385-09 | Current |  | Commercial | Energy Recovery Ventilation | Restaurant | New Construction/Natural Replacement | space heating | High Efficient 65% Energy Recovery Ventilation Medium Use Group (Hotel, Restaurant, Retail) | Minimum 65% Sensible Heat Recovery Effectiveness and 63% Total Energy Recovery Effectiveness at 32°F | Minimum 55% Energy Recovery Effectiveness as per Ontario Building Code 2017 |  |  | CFM | TRM Version 5.0 | 2020-11-12 | 0 | 0.44 | 0 | 0 | 0 | 0 | 0 | 1 | 14 | Midstream | 0.05 | 1 | 1
COM-ERV-SH-386-09 | Current |  | Commercial | Energy Recovery Ventilation | Retail | New Construction/Natural Replacement | space heating | High Efficient 65% Energy Recovery Ventilation Medium Use Group (Hotel, Restaurant, Retail) | Minimum 65% Sensible Heat Recovery Effectiveness and 63% Total Energy Recovery Effectiveness at 32°F | Minimum 55% Energy Recovery Effectiveness as per Ontario Building Code 2017 |  |  | CFM | TRM Version 5.0 | 2020-11-12 | 0 | 0.37 | 0 | 0 | 0 | 0 | 0 | 1 | 14 | Midstream | 0.05 | 1 | 1
COM-ERV-SH-387-09 | Current |  | Commercial | Energy Recovery Ventilation | Office | New Construction/Natural Replacement | space heating | High Efficient 65% Energy Recovery Ventilation Low Use Group (Office, Warehouse, School) | Minimum 65% Sensible Heat Recovery Effectiveness and 63% Total Energy Recovery Effectiveness at 32°F | Minimum 55% Energy Recovery Effectiveness as per Ontario Building Code 2017 |  |  | CFM | TRM Version 5.0 | 2020-11-12 | 0 | 0.32 | 0 | 0 | 0 | 0 | 0 | 1 | 14 | Midstream | 0.05 | 1 | 1
COM-ERV-SH-388-09 | Current |  | Commercial | Energy Recovery Ventilation | Warehouse | New Construction/Natural Replacement | space heating | High Efficient 65% Energy Recovery Ventilation Low Use Group (Office, Warehouse, School) | Minimum 65% Sensible Heat Recovery Effectiveness and 63% Total Energy Recovery Effectiveness at 32°F | Minimum 55% Energy Recovery Effectiveness as per Ontario Building Code 2017 |  |  | CFM | TRM Version 5.0 | 2020-11-12 | 0 | 0.31 | 0 | 0 | 0 | 0 | 0 | 1 | 14 | Midstream | 0.05 | 1 | 1
COM-ERV-SH-389-09 | Current |  | Commercial | Energy Recovery Ventilation | School | New Construction/Natural Replacement | space heating | High Efficient 65% Energy Recovery Ventilation Low Use Group (Office, Warehouse, School) | Minimum 65% Sensible Heat Recovery Effectiveness and 63% Total Energy Recovery Effectiveness at 32°F | Minimum 55% Energy Recovery Effectiveness as per Ontario Building Code 2017 |  |  | CFM | TRM Version 5.0 | 2020-11-12 | 0 | 0.27 | 0 | 0 | 0 | 0 | 0 | 1 | 14 | Midstream | 0.05 | 1 | 1
COM-ERV-SH-380-13 | Current |  | Commercial | Energy Recovery Ventilation | High Use Group | New Construction/Natural Replacement | space heating | High Efficient 75% Energy Recovery Ventilation High Use Group (Multi-Residential, Health Care, Nursing Homes) | Minimum 75% Sensible Heat Recovery Effectiveness and 73% Total Energy Recovery Effectiveness at 32°F | Minimum 55% Energy Recovery Effectiveness as per Ontario Building Code 2017 |  |  | CFM | TRM Version 5.0 | 2020-11-12 | 0 | 1.7 | 0 | 0 | 0 | 0 | 0 | 2 | 14 | Midstream | 0.05 | 1 | 1
COM-ERV-SH-381-13 | Current |  | Commercial | Energy Recovery Ventilation | Medium Use Group | New Construction/Natural Replacement | space heating | High Efficient 75% Energy Recovery Ventilation Medium Use Group (Hotel, Restaurant, and Retail) | Minimum 75% Sensible Heat Recovery Effectiveness and 73% Total Energy Recovery Effectiveness at 32°F | Minimum 55% Energy Recovery Effectiveness as per Ontario Building Code 2017 |  |  | CFM | TRM Version 5.0 | 2020-11-12 | 0 | 0.95 | 0 | 0 | 0 | 0 | 0 | 2 | 14 | Midstream | 0.05 | 1 | 1
COM-ERV-SH-382-13 | Current |  | Commercial | Energy Recovery Ventilation | Low Use Group | New Construction/Natural Replacement | space heating | High Efficient 75% Energy Recovery Ventilation Low Use Group (Office, Warehouse, School) | Minimum 75% Sensible Heat Recovery Effectiveness and 73% Total Energy Recovery Effectiveness at 32°F | Minimum 55% Energy Recovery Effectiveness as per Ontario Building Code 2017 |  |  | CFM | TRM Version 5.0 | 2020-11-12 | 0 | 0.61 | 0 | 0 | 0 | 0 | 0 | 2 | 14 | Midstream | 0.05 | 1 | 1
COM-ERV-SH-383-13 | Current |  | Commercial | Energy Recovery Ventilation | Multi-Residential, Health Care, Nursing Homes | New Construction/Natural Replacement | space heating | High Efficient 75% Energy Recovery Ventilation High Use Group (Multi-Residential, Health Care, Nursing Homes) | Minimum 75% Sensible Heat Recovery Effectiveness and 73% Total Energy Recovery Effectiveness at 32°F | Minimum 55% Energy Recovery Effectiveness as per Ontario Building Code 2017 |  |  | CFM | TRM Version 5.0 | 2020-11-12 | 0 | 1.7 | 0 | 0 | 0 | 0 | 0 | 2 | 14 | Midstream | 0.05 | 1 | 1
COM-ERV-SH-384-13 | Current |  | Commercial | Energy Recovery Ventilation | Hotel | New Construction/Natural Replacement | space heating | High Efficient 75% Energy Recovery Ventilation Medium Use Group (Hotel, Restaurant, and Retail) | Minimum 75% Sensible Heat Recovery Effectiveness and 73% Total Energy Recovery Effectiveness at 32°F | Minimum 55% Energy Recovery Effectiveness as per Ontario Building Code 2017 |  |  | CFM | TRM Version 5.0 | 2020-11-12 | 0 | 1.22 | 0 | 0 | 0 | 0 | 0 | 2 | 14 | Midstream | 0.05 | 1 | 1
COM-ERV-SH-385-13 | Current |  | Commercial | Energy Recovery Ventilation | Restaurant | New Construction/Natural Replacement | space heating | High Efficient 75% Energy Recovery Ventilation Medium Use Group (Hotel, Restaurant, and Retail) | Minimum 75% Sensible Heat Recovery Effectiveness and 73% Total Energy Recovery Effectiveness at 32°F | Minimum 55% Energy Recovery Effectiveness as per Ontario Building Code 2017 |  |  | CFM | TRM Version 5.0 | 2020-11-12 | 0 | 0.88 | 0 | 0 | 0 | 0 | 0 | 2 | 14 | Midstream | 0.05 | 1 | 1
COM-ERV-SH-386-13 | Current |  | Commercial | Energy Recovery Ventilation | Retail | New Construction/Natural Replacement | space heating | High Efficient 75% Energy Recovery Ventilation Medium Use Group (Hotel, Restaurant, and Retail) | Minimum 75% Sensible Heat Recovery Effectiveness and 73% Total Energy Recovery Effectiveness at 32°F | Minimum 55% Energy Recovery Effectiveness as per Ontario Building Code 2017 |  |  | CFM | TRM Version 5.0 | 2020-11-12 | 0 | 0.74 | 0 | 0 | 0 | 0 | 0 | 2 | 14 | Midstream | 0.05 | 1 | 1
COM-ERV-SH-387-13 | Current |  | Commercial | Energy Recovery Ventilation | Office | New Construction/Natural Replacement | space heating | High Efficient 75% Energy Recovery Ventilation Low Use Group (Office, Warehouse, School) | Minimum 75% Sensible Heat Recovery Effectiveness and 73% Total Energy Recovery Effectiveness at 32°F | Minimum 55% Energy Recovery Effectiveness as per Ontario Building Code 2017 |  |  | CFM | TRM Version 5.0 | 2020-11-12 | 0 | 0.65 | 0 | 0 | 0 | 0 | 0 | 2 | 14 | Midstream | 0.05 | 1 | 1
COM-ERV-SH-388-13 | Current |  | Commercial | Energy Recovery Ventilation | Warehouse | New Construction/Natural Replacement | space heating | High Efficient 75% Energy Recovery Ventilation Low Use Group (Office, Warehouse, School) | Minimum 75% Sensible Heat Recovery Effectiveness and 73% Total Energy Recovery Effectiveness at 32°F | Minimum 55% Energy Recovery Effectiveness as per Ontario Building Code 2017 |  |  | CFM | TRM Version 5.0 | 2020-11-12 | 0 | 0.62 | 0 | 0 | 0 | 0 | 0 | 2 | 14 | Midstream | 0.05 | 1 | 1
COM-ERV-SH-389-13 | Current |  | Commercial | Energy Recovery Ventilation | School | New Construction/Natural Replacement | space heating | High Efficient 75% Energy Recovery Ventilation Low Use Group (Office, Warehouse, School) | Minimum 75% Sensible Heat Recovery Effectiveness and 73% Total Energy Recovery Effectiveness at 32°F | Minimum 55% Energy Recovery Effectiveness as per Ontario Building Code 2017 |  |  | CFM | TRM Version 5.0 | 2020-11-12 | 0 | 0.55 | 0 | 0 | 0 | 0 | 0 | 2 | 14 | Midstream | 0.05 | 1 | 1
COM-ERV-SH-390-05 | Current |  | Commercial | Energy Recovery Ventilation | High Use Group | New Construction/Natural Replacement | space heating | High Efficient 85% Energy Recovery Ventilation High Use Group (Multi-Residential, Health Care, Nursing Homes) | Minimum 85% Sensible Heat Recovery Effectiveness and 83% Total Energy Recovery Effectiveness at 32°F | Minimum 55% Energy Recovery Effectiveness as per Ontario Building Code 2017 |  |  | CFM | TRM Version 5.0 | 2020-11-12 | 0 | 2.56 | 0 | 0 | 0 | 0 | 0 | 3 | 14 | Midstream | 0.05 | 1 | 1
COM-ERV-SH-391-05 | Current |  | Commercial | Energy Recovery Ventilation | Medium Use Group | New Construction/Natural Replacement | space heating | High Efficient 85% Energy Recovery Ventilation Medium Use Group (Hotel, Restaurant, Retail) | Minimum 85% Sensible Heat Recovery Effectiveness and 83% Total Energy Recovery Effectiveness at 32°F | Minimum 55% Energy Recovery Effectiveness as per Ontario Building Code 2017 |  |  | CFM | TRM Version 5.0 | 2020-11-12 | 0 | 1.42 | 0 | 0 | 0 | 0 | 0 | 3 | 14 | Midstream | 0.05 | 1 | 1
COM-ERV-SH-392-05 | Current |  | Commercial | Energy Recovery Ventilation | Low Use Group | New Construction/Natural Replacement | space heating | High Efficient 85% Energy Recovery Ventilation Low Use Group (Office, Warehouse, School) | Minimum 85% Sensible Heat Recovery Effectiveness and 83% Total Energy Recovery Effectiveness at 32°F | Minimum 55% Energy Recovery Effectiveness as per Ontario Building Code 2017 |  |  | CFM | TRM Version 5.0 | 2020-11-12 | 0 | 0.91 | 0 | 0 | 0 | 0 | 0 | 3 | 14 | Midstream | 0.05 | 1 | 1
COM-ERV-SH-393-05 | Current |  | Commercial | Energy Recovery Ventilation | Multi-Residential, Health Care, Nursing Homes | New Construction/Natural Replacement | space heating | High Efficient 85% Energy Recovery Ventilation High Use Group (Multi-Residential, Health Care, Nursing Homes) | Minimum 85% Sensible Heat Recovery Effectiveness and 83% Total Energy Recovery Effectiveness at 32°F | Minimum 55% Energy Recovery Effectiveness as per Ontario Building Code 2017 |  |  | CFM | TRM Version 5.0 | 2020-11-12 | 0 | 2.56 | 0 | 0 | 0 | 0 | 0 | 3 | 14 | Midstream | 0.05 | 1 | 1
COM-ERV-SH-394-05 | Current |  | Commercial | Energy Recovery Ventilation | Hotel | New Construction/Natural Replacement | space heating | High Efficient 85% Energy Recovery Ventilation Medium Use Group (Hotel, Restaurant, Retail) | Minimum 85% Sensible Heat Recovery Effectiveness and 83% Total Energy Recovery Effectiveness at 32°F | Minimum 55% Energy Recovery Effectiveness as per Ontario Building Code 2017 |  |  | CFM | TRM Version 5.0 | 2020-11-12 | 0 | 1.83 | 0 | 0 | 0 | 0 | 0 | 3 | 14 | Midstream | 0.05 | 1 | 1
COM-ERV-SH-395-05 | Current |  | Commercial | Energy Recovery Ventilation | Restaurant | New Construction/Natural Replacement | space heating | High Efficient 85% Energy Recovery Ventilation Medium Use Group (Hotel, Restaurant, Retail) | Minimum 85% Sensible Heat Recovery Effectiveness and 83% Total Energy Recovery Effectiveness at 32°F | Minimum 55% Energy Recovery Effectiveness as per Ontario Building Code 2017 |  |  | CFM | TRM Version 5.0 | 2020-11-12 | 0 | 1.32 | 0 | 0 | 0 | 0 | 0 | 3 | 14 | Midstream | 0.05 | 1 | 1
COM-ERV-SH-396-05 | Current |  | Commercial | Energy Recovery Ventilation | Retail | New Construction/Natural Replacement | space heating | High Efficient 85% Energy Recovery Ventilation Medium Use Group (Hotel, Restaurant, Retail) | Minimum 85% Sensible Heat Recovery Effectiveness and 83% Total Energy Recovery Effectiveness at 32°F | Minimum 55% Energy Recovery Effectiveness as per Ontario Building Code 2017 |  |  | CFM | TRM Version 5.0 | 2020-11-12 | 0 | 1.11 | 0 | 0 | 0 | 0 | 0 | 3 | 14 | Midstream | 0.05 | 1 | 1
COM-ERV-SH-397-05 | Current |  | Commercial | Energy Recovery Ventilation | Office | New Construction/Natural Replacement | space heating | High Efficient 85% Energy Recovery Ventilation Low Use Group (Office, Warehouse, School) | Minimum 85% Sensible Heat Recovery Effectiveness and 83% Total Energy Recovery Effectiveness at 32°F | Minimum 55% Energy Recovery Effectiveness as per Ontario Building Code 2017 |  |  | CFM | TRM Version 5.0 | 2020-11-12 | 0 | 0.97 | 0 | 0 | 0 | 0 | 0 | 3 | 14 | Midstream | 0.05 | 1 | 1
COM-ERV-SH-398-05 | Current |  | Commercial | Energy Recovery Ventilation | Warehouse | New Construction/Natural Replacement | space heating | High Efficient 85% Energy Recovery Ventilation Low Use Group (Office, Warehouse, School) | Minimum 85% Sensible Heat Recovery Effectiveness and 83% Total Energy Recovery Effectiveness at 32°F | Minimum 55% Energy Recovery Effectiveness as per Ontario Building Code 2017 |  |  | CFM | TRM Version 5.0 | 2020-11-12 | 0 | 0.93 | 0 | 0 | 0 | 0 | 0 | 3 | 14 | Midstream | 0.05 | 1 | 1
COM-ERV-SH-399-05 | Current |  | Commercial | Energy Recovery Ventilation | School | New Construction/Natural Replacement | space heating | High Efficient 85% Energy Recovery Ventilation Low Use Group (Office, Warehouse, School) | Minimum 85% Sensible Heat Recovery Effectiveness and 83% Total Energy Recovery Effectiveness at 32°F | Minimum 55% Energy Recovery Effectiveness as per Ontario Building Code 2017 |  |  | CFM | TRM Version 5.0 | 2020-11-12 | 0 | 0.82 | 0 | 0 | 0 | 0 | 0 | 3 | 14 | Midstream | 0.05 | 1 | 1
COM-AC-SH-481-03 | Current |  | Commercial | Air Curtain |  | New Construction/Retrofit | space heating | Air Curtains | Pedestrian Doors 2 x (3' x 7') | Exterior doorway without vestibule or air curtain |  | unit |  | TRM Version 5.0 | 2020-11-12 | 1690 | 0 | 212 | 0 | 0 | 0 | 3150 | 0 | 15 | Midstream | 0.05 | 1 | 1
COM-AC-SH-487-03 | Current |  | Commercial | Air Curtain |  | New Construction/Retrofit | space heating | Air Curtains | Pedestrian Doors 2 x (3' x 7') | Exterior doorway with vestibule and no air curtain |  | unit |  | TRM Version 5.0 | 2020-11-12 | 1082 | 0 | 124 | 0 | 0 | 0 | 3150 | 0 | 15 | Midstream | 0.05 | 1 | 1
COM-AC-SH-483-03 | Current |  | Commercial | Air Curtain |  | New Construction/Retrofit | space heating | Air Curtains | Pedestrian Doors 2 x (6' x 8') | Exterior doorway without vestibule or air curtain |  | unit |  | TRM Version 5.0 | 2020-11-12 | 3774 | 0 | 431 | 0 | 0 | 0 | 3350 | 0 | 15 | Midstream | 0.05 | 1 | 1
COM-AC-SH-489-03 | Current |  | Commercial | Air Curtain |  | New Construction/Retrofit | space heating | Air Curtains | Pedestrian Doors 2 x (6' x 8') | Exterior doorway with vestibule and no air curtain |  | unit |  | TRM Version 5.0 | 2020-11-12 | 2416 | 0 | 232 | 0 | 0 | 0 | 3350 | 0 | 15 | Midstream | 0.05 | 1 | 1
COM-AC-SH-482-03 | Current |  | Commercial | Air Curtain |  | New Construction/Retrofit | space heating | Air Curtains | Pedestrian Doors 2 x (6' x 7') | Exterior doorway without vestibule or air curtain |  | unit |  | TRM Version 5.0 | 2020-11-12 | 3380 | 0 | 367 | 0 | 0 | 0 | 3350 | 0 | 15 | Midstream | 0.05 | 1 | 1
COM-AC-SH-488-03 | Current |  | Commercial | Air Curtain |  | New Construction/Retrofit | space heating | Air Curtains | Pedestrian Doors 2 x (6' x 7') | Exterior doorway with vestibule and no air curtain |  | unit |  | TRM Version 5.0 | 2020-11-12 | 2164 | 0 | 192 | 0 | 0 | 0 | 3350 | 0 | 15 | Midstream | 0.05 | 1 | 1
COM-AC-SH-478-03 | Current |  | Commercial | Air Curtain |  | New Construction/Retrofit | space heating | Air Curtains | Pedestrian Doors 3' x 7' | Exterior doorway without vestibule or air curtain |  | unit |  | TRM Version 5.0 | 2020-11-12 | 845 | 0 | 106 | 0 | 0 | 0 | 1645 | 0 | 15 | Midstream | 0.05 | 1 | 1
COM-AC-SH-484-03 | Current |  | Commercial | Air Curtain |  | New Construction/Retrofit | space heating | Air Curtains | Pedestrian Doors 3' x 7' | Exterior doorway with vestibule and no air curtain |  | unit |  | TRM Version 5.0 | 2020-11-12 | 541 | 0 | 62 | 0 | 0 | 0 | 1645 | 0 | 15 | Midstream | 0.05 | 1 | 1
COM-AC-SH-479-03 | Current |  | Commercial | Air Curtain |  | New Construction/Retrofit | space heating | Air Curtains | Pedestrian Doors 6' x 7' | Exterior doorway without vestibule or air curtain |  | unit |  | TRM Version 5.0 | 2020-11-12 | 1690 | 0 | 184 | 0 | 0 | 0 | 1745 | 0 | 15 | Midstream | 0.05 | 1 | 1
COM-AC-SH-485-03 | Current |  | Commercial | Air Curtain |  | New Construction/Retrofit | space heating | Air Curtains | Pedestrian Doors 6' x 7' | Exterior doorway with vestibule and no air curtain |  | unit |  | TRM Version 5.0 | 2020-11-12 | 1082 | 0 | 96 | 0 | 0 | 0 | 1745 | 0 | 15 | Midstream | 0.05 | 1 | 1
COM-AC-SH-480-03 | Current |  | Commercial | Air Curtain |  | New Construction/Retrofit | space heating | Air Curtains | Pedestrian Doors 6' x 8' | Exterior doorway without vestibule or air curtain |  | unit |  | TRM Version 5.0 | 2020-11-12 | 1887 | 0 | 215 | 0 | 0 | 0 | 1745 | 0 | 15 | Midstream | 0.05 | 1 | 1
COM-AC-SH-486-03 | Current |  | Commercial | Air Curtain |  | New Construction/Retrofit | space heating | Air Curtains | Pedestrian Doors 6' x 8' | Exterior doorway with vestibule and no air curtain |  | unit |  | TRM Version 5.0 | 2020-11-12 | 1208 | 0 | 116 | 0 | 0 | 0 | 1745 | 0 | 15 | Midstream | 0.05 | 1 | 1
COM-DCV-SH-527-04 | Current |  | Commercial | Demand Control Ventilation | Office | New Construction/Natural Replacement | space heating | Demand Control Ventilation with CO2 Sensor (Office) | Scheduled Ventilation (Occupied Periods) | New single-zone, constant volume ventilation system | Provides min outdoor air requirements as specificed in Table 6.2.2.1 of ASHRAE Standard 62.1-2013 [1] |  | sq ft | TRM Version 5.0 | 2020-11-12 | 0 | 0.112 | 0 | 0 | 0 | 0 | 750 | 0 | 15 | Midstream | 0.2 | 1 | 1
COM-DCV-SH-528-04 | Current |  | Commercial | Demand Control Ventilation | Office | Retrofit | space heating | Demand Control Ventilation with CO2 Sensor (Office) | Scheduled Ventilation (Occupied Periods) | New single-zone, constant volume ventilation system | Provides min outdoor air requirements as specificed in Table 6.2.2.1 of ASHRAE Standard 62.1-2013 [1] |  | sq ft | TRM Version 5.0 | 2020-11-12 | 0 | 0.112 | 0 | 0 | 0 | 0 | 1050 | 0 | 15 | Midstream | 0.05 | 1 | 1
COM-DCV-SH-529-04 | Current |  | Commercial | Demand Control Ventilation | Retail | New Construction/Natural Replacement | space heating | Demand Control Ventilation with CO2 Sensor (Retail) | Scheduled Ventilation (Occupied Periods) | New single-zone, constant volume ventilation system | Provides min outdoor air requirements as specificed in Table 6.2.2.1 of ASHRAE Standard 62.1-2013 [1] |  | sq ft | TRM Version 5.0 | 2020-11-12 | 0 | 0.392 | 0 | 0 | 0 | 0 | 750 | 0 | 15 | Midstream | 0.2 | 1 | 1
COM-DCV-SH-530-04 | Current |  | Commercial | Demand Control Ventilation | Retail | Retrofit | space heating | Demand Control Ventilation with CO2 Sensor (Retail) | Scheduled Ventilation (Occupied Periods) | New single-zone, constant volume ventilation system | Provides min outdoor air requirements as specificed in Table 6.2.2.1 of ASHRAE Standard 62.1-2013 [1] |  | sq ft | TRM Version 5.0 | 2020-11-12 | 0 | 0.392 | 0 | 0 | 0 | 0 | 1050 | 0 | 15 | Midstream | 0.05 | 1 | 1
COM-DCV-SH-531-04 | Current |  | Commercial | Demand Control Ventilation | Cinemas and Performing Arts | Retrofit | space heating | Demand Control Ventilation with CO2 Sensor (Cinemas and Performing Arts) | Scheduled Ventilation (Occupied Periods) | Existing single-zone, constant volume ventilation system | Provides min outdoor air requirements as specificed in Table 6.2.2.1 of ASHRAE Standard 62.1-2013 [1] |  | sq ft | TRM Version 5.0 | 2020-11-12 | 0 | 1.69 | 0 | 0 | 0 | 0 | 1050 | 0 | 15 | Midstream | 0.05 | 1 | 1
COM-DCV-SH-532-04 | Current |  | Commercial | Demand Control Ventilation | Cinemas and Performing Arts | New Construction/Natural Replacement | space heating | Demand Control Ventilation with CO2 Sensor (Cinemas and Performing Arts) | Scheduled Ventilation (Occupied Periods) | Existing single-zone, constant volume ventilation system | Provides min outdoor air requirements as specificed in Table 6.2.2.1 of ASHRAE Standard 62.1-2013 [1] |  | sq ft | TRM Version 5.0 | 2020-11-12 | 0 | 1.69 | 0 | 0 | 0 | 0 | 750 | 0 | 15 | Midstream | 0.2 | 1 | 1
COM-DCV-SH-533-04 | Current |  | Commercial | Demand Control Ventilation | Community Center Meeting Space | Retrofit | space heating | Demand Control Ventilation with CO2 Sensor (Community Center Meeting Space) | Scheduled Ventilation (Occupied Periods) | Existing single-zone, constant volume ventilation system | Provides min outdoor air requirements as specificed in Table 6.2.2.1 of ASHRAE Standard 62.1-2013 [1] |  | sq ft | TRM Version 5.0 | 2020-11-12 | 0 | 0.441 | 0 | 0 | 0 | 0 | 1050 | 0 | 15 | Midstream | 0.05 | 1 | 1
COM-DCV-SH-534-04 | Current |  | Commercial | Demand Control Ventilation | Community Center Meeting Space | New Construction/Natural Replacement | space heating | Demand Control Ventilation with CO2 Sensor (Community Center Meeting Space) | Scheduled Ventilation (Occupied Periods) | Existing single-zone, constant volume ventilation system | Provides min outdoor air requirements as specificed in Table 6.2.2.1 of ASHRAE Standard 62.1-2013 [1] |  | sq ft | TRM Version 5.0 | 2020-11-12 | 0 | 0.441 | 0 | 0 | 0 | 0 | 750 | 0 | 15 | Midstream | 0.2 | 1 | 1
COM-DCV-SH-535-04 | Current |  | Commercial | Demand Control Ventilation | Exercise Center/Sports Arena | Retrofit | space heating | Demand Control Ventilation with CO2 Sensor (Exercise Center/Sports Arena) | Scheduled Ventilation (Occupied Periods) | Existing single-zone, constant volume ventilation system | Provides min outdoor air requirements as specificed in Table 6.2.2.1 of ASHRAE Standard 62.1-2013 [1] |  | sq ft | TRM Version 5.0 | 2020-11-12 | 0 | 0.435 | 0 | 0 | 0 | 0 | 1050 | 0 | 15 | Midstream | 0.05 | 1 | 1
COM-DCV-SH-536-04 | Current |  | Commercial | Demand Control Ventilation | Exercise Center/Sports Arena | New Construction/Natural Replacement | space heating | Demand Control Ventilation with CO2 Sensor (Exercise Center/Sports Arena) | Scheduled Ventilation (Occupied Periods) | Existing single-zone, constant volume ventilation system | Provides min outdoor air requirements as specificed in Table 6.2.2.1 of ASHRAE Standard 62.1-2013 [1] |  | sq ft | TRM Version 5.0 | 2020-11-12 | 0 | 0.435 | 0 | 0 | 0 | 0 | 750 | 0 | 15 | Midstream | 0.2 | 1 | 1
COM-DCV-SH-537-04 | Current |  | Commercial | Demand Control Ventilation | Hotel Conference Rooms | Retrofit | space heating | Demand Control Ventilation with CO2 Sensor (Hotel Conference Rooms) | Scheduled Ventilation (Occupied Periods) | Existing single-zone, constant volume ventilation system | Provides min outdoor air requirements as specificed in Table 6.2.2.1 of ASHRAE Standard 62.1-2013 [1] |  | sq ft | TRM Version 5.0 | 2020-11-12 | 0 | 1.043 | 0 | 0 | 0 | 0 | 1050 | 0 | 15 | Midstream | 0.05 | 1 | 1
COM-DCV-SH-538-04 | Current |  | Commercial | Demand Control Ventilation | Hotel Conference Rooms | New Construction/Natural Replacement | space heating | Demand Control Ventilation with CO2 Sensor (Hotel Conference Rooms) | Scheduled Ventilation (Occupied Periods) | Existing single-zone, constant volume ventilation system | Provides min outdoor air requirements as specificed in Table 6.2.2.1 of ASHRAE Standard 62.1-2013 [1] |  | sq ft | TRM Version 5.0 | 2020-11-12 | 0 | 1.043 | 0 | 0 | 0 | 0 | 750 | 0 | 15 | Midstream | 0.2 | 1 | 1
COM-DCV-SH-539-04 | Current |  | Commercial | Demand Control Ventilation | Post-Secondary School Classroom | Retrofit | space heating | Demand Control Ventilation with CO2 Sensor (Post-Secondary School Classroom) | Scheduled Ventilation (Occupied Periods) | Existing single-zone, constant volume ventilation system | Provides min outdoor air requirements as specificed in Table 6.2.2.1 of ASHRAE Standard 62.1-2013 [1] |  | sq ft | TRM Version 5.0 | 2020-11-12 | 0 | 0.601 | 0 | 0 | 0 | 0 | 1050 | 0 | 15 | Midstream | 0.05 | 1 | 1
COM-DCV-SH-540-04 | Current |  | Commercial | Demand Control Ventilation | Post-Secondary School Classroom | New Construction/Natural Replacement | space heating | Demand Control Ventilation with CO2 Sensor (Post-Secondary School Classroom) | Scheduled Ventilation (Occupied Periods) | Existing single-zone, constant volume ventilation system | Provides min outdoor air requirements as specificed in Table 6.2.2.1 of ASHRAE Standard 62.1-2013 [1] |  | sq ft | TRM Version 5.0 | 2020-11-12 | 0 | 0.601 | 0 | 0 | 0 | 0 | 750 | 0 | 15 | Midstream | 0.2 | 1 | 1
COM-DCV-SH-541-04 | Current |  | Commercial | Demand Control Ventilation | Primary/Secondary School Gymnasium | Retrofit | space heating | Demand Control Ventilation with CO2 Sensor (Primary/Secondary School Gymnasium) | Scheduled Ventilation (Occupied Periods) | Existing single-zone, constant volume ventilation system | Provides min outdoor air requirements as specificed in Table 6.2.2.1 of ASHRAE Standard 62.1-2013 [1] |  | sq ft | TRM Version 5.0 | 2020-11-12 | 0 | 1.484 | 0 | 0 | 0 | 0 | 1050 | 0 | 15 | Midstream | 0.05 | 1 | 1
COM-DCV-SH-542-04 | Current |  | Commercial | Demand Control Ventilation | Primary/Secondary School Gymnasium | New Construction/Natural Replacement | space heating | Demand Control Ventilation with CO2 Sensor (Primary/Secondary School Gymnasium) | Scheduled Ventilation (Occupied Periods) | Existing single-zone, constant volume ventilation system | Provides min outdoor air requirements as specificed in Table 6.2.2.1 of ASHRAE Standard 62.1-2013 [1] |  | sq ft | TRM Version 5.0 | 2020-11-12 | 0 | 1.484 | 0 | 0 | 0 | 0 | 750 | 0 | 15 | Midstream | 0.2 | 1 | 1
COM-DCV-SH-543-04 | Current |  | Commercial | Demand Control Ventilation | Senior/Nursing/Long-Term Care Facility (Common Areas) | Retrofit | space heating | Demand Control Ventilation with CO2 Sensor (Senior/Nursing/Long-Term Care Facility (Common Areas)) | Scheduled Ventilation (Occupied Periods) | Existing single-zone, constant volume ventilation system | Provides min outdoor air requirements as specificed in Table 6.2.2.1 of ASHRAE Standard 62.1-2013 [1] |  | sq ft | TRM Version 5.0 | 2020-11-12 | 0 | 0.636 | 0 | 0 | 0 | 0 | 1050 | 0 | 15 | Midstream | 0.05 | 1 | 1
COM-DCV-SH-544-04 | Current |  | Commercial | Demand Control Ventilation | Senior/Nursing/Long-Term Care Facility (Common Areas) | New Construction/Natural Replacement | space heating | Demand Control Ventilation with CO2 Sensor (Senior/Nursing/Long-Term Care Facility (Common Areas)) | Scheduled Ventilation (Occupied Periods) | Existing single-zone, constant volume ventilation system | Provides min outdoor air requirements as specificed in Table 6.2.2.1 of ASHRAE Standard 62.1-2013 [1] |  | sq ft | TRM Version 5.0 | 2020-11-12 | 0 | 0.636 | 0 | 0 | 0 | 0 | 750 | 0 | 15 | Midstream | 0.2 | 1 | 1
COM-AC-SH-471-03 | Current |  | Commercial | Air Curtain |  | New Construction/Retrofit | space heating | Air Curtains | Shipping and Receiving Doors "Dock-In" 10' x 10' | Exterior doorway without air curtain |  | unit |  | TRM Version 5.0 | 2020-11-12 | 5517 | 0 | -2838 | 0 | 0 | 0 | 6345 | 0 | 15 | Midstream | 0.05 | 1 | 1
COM-AC-SH-470-03 | Current |  | Commercial | Air Curtain |  | New Construction/Retrofit | space heating | Air Curtains | Shipping and Receiving Doors "Dock-In" 8' x 10' | Exterior doorway without air curtain |  | unit |  | TRM Version 5.0 | 2020-11-12 | 4941 | 0 | -1576 | 0 | 0 | 0 | 5663 | 0 | 15 | Midstream | 0.05 | 1 | 1
COM-AC-SH-468-03 | Current |  | Commercial | Air Curtain |  | New Construction/Retrofit | space heating | Air Curtains | Shipping and Receiving Doors "Dock-In" 8' x 8' | Exterior doorway without air curtain |  | unit |  | TRM Version 5.0 | 2020-11-12 | 4713 | 0 | -1688 | 0 | 0 | 0 | 5663 | 0 | 15 | Midstream | 0.05 | 1 | 1
COM-AC-SH-469-03 | Current |  | Commercial | Air Curtain |  | New Construction/Retrofit | space heating | Air Curtains | Shipping and Receiving Doors "Dock-In" 8' x 9' | Exterior doorway without air curtain |  | unit |  | TRM Version 5.0 | 2020-11-12 | 4845 | 0 | -1630 | 0 | 0 | 0 | 5663 | 0 | 15 | Midstream | 0.05 | 1 | 1
COM-AC-SH-472-03 | Current |  | Commercial | Air Curtain |  | New Construction/Retrofit | space heating | Air Curtains | Shipping and Receiving Doors "Drive-In" 10' x 10' | Exterior doorway without air curtain |  | unit |  | TRM Version 5.0 | 2020-11-12 | 4844 | 0 | 540 | 0 | 0 | 0 | 6345 | 0 | 15 | Midstream | 0.05 | 1 | 1
COM-AC-SH-473-03 | Current |  | Commercial | Air Curtain |  | New Construction/Retrofit | space heating | Air Curtains | Shipping and Receiving Doors "Drive-In" 12' x 12' | Exterior doorway without air curtain |  | unit |  | TRM Version 5.0 | 2020-11-12 | 5753 | 0 | 843 | 0 | 0 | 0 | 11158 | 0 | 15 | Midstream | 0.05 | 1 | 1
COM-AC-SH-474-03 | Current |  | Commercial | Air Curtain |  | New Construction/Retrofit | space heating | Air Curtains | Shipping and Receiving Doors "Drive-In" 14' x 14' | Exterior doorway without air curtain |  | unit |  | TRM Version 5.0 | 2020-11-12 | 6504 | 0 | 772 | 0 | 0 | 0 | 14159 | 0 | 15 | Midstream | 0.05 | 1 | 1
COM-AC-SH-475-03 | Current |  | Commercial | Air Curtain |  | New Construction/Retrofit | space heating | Air Curtains | Shipping and Receiving Doors "Drive-In" 16' x 16' | Exterior doorway without air curtain |  | unit |  | TRM Version 5.0 | 2020-11-12 | 7081 | 0 | 987 | 0 | 0 | 0 | 22226 | 0 | 15 | Midstream | 0.05 | 1 | 1
COM-AC-SH-476-03 | Current |  | Commercial | Air Curtain |  | New Construction/Retrofit | space heating | Air Curtains | Shipping and Receiving Doors "Drive-In" 18' x 18' | Exterior doorway without air curtain |  | unit |  | TRM Version 5.0 | 2020-11-12 | 7459 | 0 | 488 | 0 | 0 | 0 | 24699 | 0 | 15 | Midstream | 0.05 | 1 | 1
COM-AC-SH-477-03 | Current |  | Commercial | Air Curtain |  | New Construction/Retrofit | space heating | Air Curtains | Shipping and Receiving Doors "Drive-In" 20' x 20' | Exterior doorway without air curtain |  | unit |  | TRM Version 5.0 | 2020-11-12 | 7605 | 0 | 596 | 0 | 0 | 0 | 45256 | 0 | 15 | Midstream | 0.05 | 1 | 1
COM-HRV-SH-366-03 | Current |  | Commercial | Heat Recovery Ventialation | High Use | New Construction/Retrofit | space heating | High Efficient 55% Heat Recovery Ventilation High Use Group (Multi-Residential, Health Care, Nursing Homes) | Ventilation with HRV Integrated | Ventilation without HRV |  |  | CFM | TRM Version 5.0 | 2020-11-12 | 0 | 3.84 | 0 | 0 | 0 | 0 | 0 | 5.35 | 14 | Midstream | 0.05 | 1 | 1
COM-HRV-SH-368-03 | Current |  | Commercial | Heat Recovery Ventialation | Low Use | New Construction/Retrofit | space heating | High Efficient 55% Heat Recovery Ventilation Low Use Group (Office, Warehouse, School) | Ventilation with HRV Integrated | Ventilation without HRV |  |  | CFM | TRM Version 5.0 | 2020-11-12 | 0 | 1.36 | 0 | 0 | 0 | 0 | 0 | 5.35 | 14 | Midstream | 0.05 | 1 | 1
COM-HRV-SH-370-03 | Current |  | Commercial | Heat Recovery Ventialation | Medium Use | New Construction/Retrofit | space heating | High Efficient 55% Heat Recovery Ventilation Medium Use Group (Hotel, Restaurant, Retail) | Ventilation with HRV Integrated | Ventilation without HRV |  |  | CFM | TRM Version 5.0 | 2020-11-12 | 0 | 2.13 | 0 | 0 | 0 | 0 | 0 | 5.35 | 14 | Midstream | 0.05 | 1 | 1
COM-HRV-SH-372-03 | Current |  | Commercial | Heat Recovery Ventialation | High Use | New Construction/Retrofit | space heating | High Efficient 65% Heat Recovery Ventilation High Use Group (Multi-Residential, Health Care, Nursing Homes) | Ventilation with HRV Integrated | Ventilation without HRV |  |  | CFM | TRM Version 5.0 | 2020-11-12 | 0 | 4.54 | 0 | 0 | 0 | 0 | 0 | 6.35 | 14 | Midstream | 0.05 | 1 | 1
COM-HRV-SH-374-03 | Current |  | Commercial | Heat Recovery Ventialation | Low Use | New Construction/Retrofit | space heating | High Efficient 65% Heat Recovery Ventilation Low Use Group (Office, Warehouse, School) | Ventilation with HRV Integrated | Ventilation without HRV |  |  | CFM | TRM Version 5.0 | 2020-11-12 | 0 | 1.61 | 0 | 0 | 0 | 0 | 0 | 6.35 | 14 | Midstream | 0.05 | 1 | 1
COM-HRV-SH-376-03 | Current |  | Commercial | Heat Recovery Ventialation | Medium Use | New Construction/Retrofit | space heating | High Efficient 65% Heat Recovery Ventilation Medium Use Group (Hotel, Restaurant, Retail) | Ventilation with HRV Integrated | Ventilation without HRV |  |  | CFM | TRM Version 5.0 | 2020-11-12 | 0 | 2.52 | 0 | 0 | 0 | 0 | 0 | 6.35 | 14 | Midstream | 0.05 | 1 | 1
COM-HRV-SH-378-03 | Current |  | Commercial | Heat Recovery Ventialation | High Use | New Construction/Retrofit | space heating | High Efficient 75% Heat Recovery Ventilation High Use Group (Multi-Residential, Health Care, Nursing Homes) | Ventilation with HRV Integrated | Ventilation without HRV |  |  | CFM | TRM Version 5.0 | 2020-11-12 | 0 | 5.24 | 0 | 0 | 0 | 0 | 0 | 7.35 | 14 | Midstream | 0.05 | 1 | 1
COM-HRV-SH-380-03 | Current |  | Commercial | Heat Recovery Ventialation | Low Use | New Construction/Retrofit | space heating | High Efficient 75% Heat Recovery Ventilation Low Use Group (Office, Warehouse, School) | Ventilation with HRV Integrated | Ventilation without HRV |  |  | CFM | TRM Version 5.0 | 2020-11-12 | 0 | 1.86 | 0 | 0 | 0 | 0 | 0 | 7.35 | 14 | Midstream | 0.05 | 1 | 1
COM-HRV-SH-382-03 | Current |  | Commercial | Heat Recovery Ventialation | Medium Use | New Construction/Retrofit | space heating | High Efficient 75% Heat Recovery Ventilation Medium Use Group (Hotel, Restaurant, Retail) | Ventilation with HRV Integrated | Ventilation without HRV |  |  | CFM | TRM Version 5.0 | 2020-11-12 | 0 | 2.91 | 0 | 0 | 0 | 0 | 0 | 7.35 | 14 | Midstream | 0.05 | 1 | 1
COM-HRV-SH-384-03 | Current |  | Commercial | Heat Recovery Ventialation | High Use | New Construction/Retrofit | space heating | High Efficient 85% Heat Recovery Ventilation High Use Group (Multi-Residential, Health Care, Nursing Homes) | Ventilation with HRV Integrated | Ventilation without HRV |  |  | CFM | TRM Version 5.0 | 2020-11-12 | 0 | 5.93 | 0 | 0 | 0 | 0 | 0 | 8.35 | 14 | Midstream | 0.05 | 1 | 1
COM-HRV-SH-386-03 | Current |  | Commercial | Heat Recovery Ventialation | Low Use | New Construction/Retrofit | space heating | High Efficient 85% Heat Recovery Ventilation Low Use Group (Office, Warehouse, School) | Ventilation with HRV Integrated | Ventilation without HRV |  |  | CFM | TRM Version 5.0 | 2020-11-12 | 0 | 2.11 | 0 | 0 | 0 | 0 | 0 | 8.35 | 14 | Midstream | 0.05 | 1 | 1
COM-HRV-SH-388-03 | Current |  | Commercial | Heat Recovery Ventialation | Medium Use | New Construction/Retrofit | space heating | High Efficient 85% Heat Recovery Ventilation Medium Use Group (Hotel, Restaurant, Retail) | Ventilation with HRV Integrated | Ventilation without HRV |  |  | CFM | TRM Version 5.0 | 2020-11-12 | 0 | 3.3 | 0 | 0 | 0 | 0 | 0 | 8.35 | 14 | Midstream | 0.05 | 1 | 1
COM-HRV-SH-390-03 | Current |  | Commercial | Heat Recovery Ventialation | Multi-Family, Health Care and Nursing Homes | New Construction/Retrofit | space heating | High Efficient 55% Heat Recovery Ventilation High Use Group (Multi-Residential, Health Care, Nursing Homes) | Ventilation with HRV Integrated | Ventilation without HRV |  |  | CFM | TRM Version 5.0 | 2020-11-12 | 0 | 3.84 | 0 | 0 | 0 | 0 | 0 | 5.35 | 14 | Midstream | 0.05 | 1 | 1
COM-HRV-SH-392-03 | Current |  | Commercial | Heat Recovery Ventialation | Hotels | New Construction/Retrofit | space heating | High Efficient 55% Heat Recovery Ventilation Medium Use Group (Hotel, Restaurant, Retail) | Ventilation with HRV Integrated | Ventilation without HRV |  |  | CFM | TRM Version 5.0 | 2020-11-12 | 0 | 2.74 | 0 | 0 | 0 | 0 | 0 | 5.35 | 14 | Midstream | 0.05 | 1 | 1
COM-HRV-SH-394-03 | Current |  | Commercial | Heat Recovery Ventialation | Restaurant | New Construction/Retrofit | space heating | High Efficient 55% Heat Recovery Ventilation Medium Use Group (Hotel, Restaurant, Retail) | Ventilation with HRV Integrated | Ventilation without HRV |  |  | CFM | TRM Version 5.0 | 2020-11-12 | 0 | 1.99 | 0 | 0 | 0 | 0 | 0 | 5.35 | 14 | Midstream | 0.05 | 1 | 1
COM-HRV-SH-396-03 | Current |  | Commercial | Heat Recovery Ventialation | Retail | New Construction/Retrofit | space heating | High Efficient 55% Heat Recovery Ventilation Medium Use Group (Hotel, Restaurant, Retail) | Ventilation with HRV Integrated | Ventilation without HRV |  |  | CFM | TRM Version 5.0 | 2020-11-12 | 0 | 1.67 | 0 | 0 | 0 | 0 | 0 | 5.35 | 14 | Midstream | 0.05 | 1 | 1
COM-HRV-SH-398-03 | Current |  | Commercial | Heat Recovery Ventialation | Office | New Construction/Retrofit | space heating | High Efficient 55% Heat Recovery Ventilation Low Use Group (Office, Warehouse, School) | Ventilation with HRV Integrated | Ventilation without HRV |  |  | CFM | TRM Version 5.0 | 2020-11-12 | 0 | 1.46 | 0 | 0 | 0 | 0 | 0 | 5.35 | 14 | Midstream | 0.05 | 1 | 1
COM-HRV-SH-400-03 | Current |  | Commercial | Heat Recovery Ventialation | Warehouse | New Construction/Retrofit | space heating | High Efficient 55% Heat Recovery Ventilation Low Use Group (Office, Warehouse, School) | Ventilation with HRV Integrated | Ventilation without HRV |  |  | CFM | TRM Version 5.0 | 2020-11-12 | 0 | 1.39 | 0 | 0 | 0 | 0 | 0 | 5.35 | 14 | Midstream | 0.05 | 1 | 1
COM-HRV-SH-402-03 | Current |  | Commercial | Heat Recovery Ventialation | School | New Construction/Retrofit | space heating | High Efficient 55% Heat Recovery Ventilation Low Use Group (Office, Warehouse, School) | Ventilation with HRV Integrated | Ventilation without HRV |  |  | CFM | TRM Version 5.0 | 2020-11-12 | 0 | 1.23 | 0 | 0 | 0 | 0 | 0 | 5.35 | 14 | Midstream | 0.05 | 1 | 1
COM-HRV-SH-404-03 | Current |  | Commercial | Heat Recovery Ventialation | Multi-Family, Health Care and Nursing Homes | New Construction/Retrofit | space heating | High Efficient 65% Heat Recovery Ventilation High Use Group (Multi-Residential, Health Care, Nursing Homes) | Ventilation with HRV Integrated | Ventilation without HRV |  |  | CFM | TRM Version 5.0 | 2020-11-12 | 0 | 4.54 | 0 | 0 | 0 | 0 | 0 | 6.35 | 14 | Midstream | 0.05 | 1 | 1
COM-HRV-SH-406-03 | Current |  | Commercial | Heat Recovery Ventialation | Hotels | New Construction/Retrofit | space heating | High Efficient 65% Heat Recovery Ventilation Medium Use Group (Hotel, Restaurant, Retail) | Ventilation with HRV Integrated | Ventilation without HRV |  |  | CFM | TRM Version 5.0 | 2020-11-12 | 0 | 3.24 | 0 | 0 | 0 | 0 | 0 | 6.35 | 14 | Midstream | 0.05 | 1 | 1
COM-HRV-SH-408-03 | Current |  | Commercial | Heat Recovery Ventialation | Restaurant | New Construction/Retrofit | space heating | High Efficient 65% Heat Recovery Ventilation Medium Use Group (Hotel, Restaurant, Retail) | Ventilation with HRV Integrated | Ventilation without HRV |  |  | CFM | TRM Version 5.0 | 2020-11-12 | 0 | 2.35 | 0 | 0 | 0 | 0 | 0 | 6.35 | 14 | Midstream | 0.05 | 1 | 1
COM-HRV-SH-410-03 | Current |  | Commercial | Heat Recovery Ventialation | Retail | New Construction/Retrofit | space heating | High Efficient 65% Heat Recovery Ventilation Medium Use Group (Hotel, Restaurant, Retail) | Ventilation with HRV Integrated | Ventilation without HRV |  |  | CFM | TRM Version 5.0 | 2020-11-12 | 0 | 1.97 | 0 | 0 | 0 | 0 | 0 | 6.35 | 14 | Midstream | 0.05 | 1 | 1
COM-HRV-SH-412-03 | Current |  | Commercial | Heat Recovery Ventialation | Office | New Construction/Retrofit | space heating | High Efficient 65% Heat Recovery Ventilation Low Use Group (Office, Warehouse, School) | Ventilation with HRV Integrated | Ventilation without HRV |  |  | CFM | TRM Version 5.0 | 2020-11-12 | 0 | 1.73 | 0 | 0 | 0 | 0 | 0 | 6.35 | 14 | Midstream | 0.05 | 1 | 1
COM-HRV-SH-414-03 | Current |  | Commercial | Heat Recovery Ventialation | Warehouse | New Construction/Retrofit | space heating | High Efficient 65% Heat Recovery Ventilation Low Use Group (Office, Warehouse, School) | Ventilation with HRV Integrated | Ventilation without HRV |  |  | CFM | TRM Version 5.0 | 2020-11-12 | 0 | 1.65 | 0 | 0 | 0 | 0 | 0 | 6.35 | 14 | Midstream | 0.05 | 1 | 1
COM-HRV-SH-416-03 | Current |  | Commercial | Heat Recovery Ventialation | School | New Construction/Retrofit | space heating | High Efficient 65% Heat Recovery Ventilation Low Use Group (Office, Warehouse, School) | Ventilation with HRV Integrated | Ventilation without HRV |  |  | CFM | TRM Version 5.0 | 2020-11-12 | 0 | 1.46 | 0 | 0 | 0 | 0 | 0 | 6.35 | 14 | Midstream | 0.05 | 1 | 1
COM-HRV-SH-418-03 | Current |  | Commercial | Heat Recovery Ventialation | Multi-Family, Health Care and Nursing Homes | New Construction/Retrofit | space heating | High Efficient 75% Heat Recovery Ventilation High Use Group (Multi-Residential, Health Care, Nursing Homes) | Ventilation with HRV Integrated | Ventilation without HRV |  |  | CFM | TRM Version 5.0 | 2020-11-12 | 0 | 5.24 | 0 | 0 | 0 | 0 | 0 | 7.35 | 14 | Midstream | 0.05 | 1 | 1
COM-HRV-SH-420-03 | Current |  | Commercial | Heat Recovery Ventialation | Hotels | New Construction/Retrofit | space heating | High Efficient 75% Heat Recovery Ventilation Medium Use Group (Hotel, Restaurant, Retail) | Ventilation with HRV Integrated | Ventilation without HRV |  |  | CFM | TRM Version 5.0 | 2020-11-12 | 0 | 3.74 | 0 | 0 | 0 | 0 | 0 | 7.35 | 14 | Midstream | 0.05 | 1 | 1
COM-HRV-SH-422-03 | Current |  | Commercial | Heat Recovery Ventialation | Restaurant | New Construction/Retrofit | space heating | High Efficient 75% Heat Recovery Ventilation Medium Use Group (Hotel, Restaurant, Retail) | Ventilation with HRV Integrated | Ventilation without HRV |  |  | CFM | TRM Version 5.0 | 2020-11-12 | 0 | 2.71 | 0 | 0 | 0 | 0 | 0 | 7.35 | 14 | Midstream | 0.05 | 1 | 1
COM-HRV-SH-424-03 | Current |  | Commercial | Heat Recovery Ventialation | Retail | New Construction/Retrofit | space heating | High Efficient 75% Heat Recovery Ventilation Medium Use Group (Hotel, Restaurant, Retail) | Ventilation with HRV Integrated | Ventilation without HRV |  |  | CFM | TRM Version 5.0 | 2020-11-12 | 0 | 2.28 | 0 | 0 | 0 | 0 | 0 | 7.35 | 14 | Midstream | 0.05 | 1 | 1
COM-HRV-SH-426-03 | Current |  | Commercial | Heat Recovery Ventialation | Office | New Construction/Retrofit | space heating | High Efficient 75% Heat Recovery Ventilation Low Use Group (Office, Warehouse, School) | Ventilation with HRV Integrated | Ventilation without HRV |  |  | CFM | TRM Version 5.0 | 2020-11-12 | 0 | 1.99 | 0 | 0 | 0 | 0 | 0 | 7.35 | 14 | Midstream | 0.05 | 1 | 1
COM-HRV-SH-428-03 | Current |  | Commercial | Heat Recovery Ventialation | Warehouse | New Construction/Retrofit | space heating | High Efficient 75% Heat Recovery Ventilation Low Use Group (Office, Warehouse, School) | Ventilation with HRV Integrated | Ventilation without HRV |  |  | CFM | TRM Version 5.0 | 2020-11-12 | 0 | 1.9 | 0 | 0 | 0 | 0 | 0 | 7.35 | 14 | Midstream | 0.05 | 1 | 1
COM-HRV-SH-430-03 | Current |  | Commercial | Heat Recovery Ventialation | School | New Construction/Retrofit | space heating | High Efficient 75% Heat Recovery Ventilation Low Use Group (Office, Warehouse, School) | Ventilation with HRV Integrated | Ventilation without HRV |  |  | CFM | TRM Version 5.0 | 2020-11-12 | 0 | 1.68 | 0 | 0 | 0 | 0 | 0 | 7.35 | 14 | Midstream | 0.05 | 1 | 1
COM-HRV-SH-432-03 | Current |  | Commercial | Heat Recovery Ventialation | Multi-Family, Health Care and Nursing Homes | New Construction/Retrofit | space heating | High Efficient 85% Heat Recovery Ventilation High Use Group (Multi-Residential, Health Care, Nursing Homes) | Ventilation with HRV Integrated | Ventilation without HRV |  |  | CFM | TRM Version 5.0 | 2020-11-12 | 0 | 5.93 | 0 | 0 | 0 | 0 | 0 | 8.35 | 14 | Midstream | 0.05 | 1 | 1
COM-HRV-SH-434-03 | Current |  | Commercial | Heat Recovery Ventialation | Hotels | New Construction/Retrofit | space heating | High Efficient 85% Heat Recovery Ventilation Medium Use Group (Hotel, Restaurant, Retail) | Ventilation with HRV Integrated | Ventilation without HRV |  |  | CFM | TRM Version 5.0 | 2020-11-12 | 0 | 4.24 | 0 | 0 | 0 | 0 | 0 | 8.35 | 14 | Midstream | 0.05 | 1 | 1
COM-HRV-SH-436-03 | Current |  | Commercial | Heat Recovery Ventialation | Restaurant | New Construction/Retrofit | space heating | High Efficient 85% Heat Recovery Ventilation Medium Use Group (Hotel, Restaurant, Retail) | Ventilation with HRV Integrated | Ventilation without HRV |  |  | CFM | TRM Version 5.0 | 2020-11-12 | 0 | 3.07 | 0 | 0 | 0 | 0 | 0 | 8.35 | 14 | Midstream | 0.05 | 1 | 1
COM-HRV-SH-438-03 | Current |  | Commercial | Heat Recovery Ventialation | Retail | New Construction/Retrofit | space heating | High Efficient 85% Heat Recovery Ventilation Medium Use Group (Hotel, Restaurant, Retail) | Ventilation with HRV Integrated | Ventilation without HRV |  |  | CFM | TRM Version 5.0 | 2020-11-12 | 0 | 2.58 | 0 | 0 | 0 | 0 | 0 | 8.35 | 14 | Midstream | 0.05 | 1 | 1
COM-HRV-SH-440-03 | Current |  | Commercial | Heat Recovery Ventialation | Office | New Construction/Retrofit | space heating | High Efficient 85% Heat Recovery Ventilation Low Use Group (Office, Warehouse, School) | Ventilation with HRV Integrated | Ventilation without HRV |  |  | CFM | TRM Version 5.0 | 2020-11-12 | 0 | 2.26 | 0 | 0 | 0 | 0 | 0 | 8.35 | 14 | Midstream | 0.05 | 1 | 1
COM-HRV-SH-442-03 | Current |  | Commercial | Heat Recovery Ventialation | Warehouse | New Construction/Retrofit | space heating | High Efficient 85% Heat Recovery Ventilation Low Use Group (Office, Warehouse, School) | Ventilation with HRV Integrated | Ventilation without HRV |  |  | CFM | TRM Version 5.0 | 2020-11-12 | 0 | 2.15 | 0 | 0 | 0 | 0 | 0 | 8.35 | 14 | Midstream | 0.05 | 1 | 1
COM-HRV-SH-444-03 | Current |  | Commercial | Heat Recovery Ventialation | School | New Construction/Retrofit | space heating | High Efficient 85% Heat Recovery Ventilation Low Use Group (Office, Warehouse, School) | Ventilation with HRV Integrated | Ventilation without HRV |  |  | CFM | TRM Version 5.0 | 2020-11-12 | 0 | 1.91 | 0 | 0 | 0 | 0 | 0 | 8.35 | 14 | Midstream | 0.05 | 1 | 1
COM-HRV-SH-367-03 | Current |  | Commercial | Heat Recovery Ventialation | High Use | New Construction/Retrofit | space heating | High Efficient 55% Heat Recovery Ventilation High Use Group (Multi-Residential, Health Care, Nursing Homes) | Ventilation with HRV Standalone | Ventilation without HRV |  |  | CFM | TRM Version 5.0 | 2020-11-12 | 0 | 3.84 | 0 | -4.39 | 0 | 0 | 0 | 8.28 | 14 | Midstream | 0.05 | 1 | 1
COM-HRV-SH-369-03 | Current |  | Commercial | Heat Recovery Ventialation | Low Use | New Construction/Retrofit | space heating | High Efficient 55% Heat Recovery Ventilation Low Use Group (Office, Warehouse, School) | Ventilation with HRV Standalone | Ventilation without HRV |  |  | CFM | TRM Version 5.0 | 2020-11-12 | 0 | 1.36 | 0 | -1.56 | 0 | 0 | 0 | 8.28 | 14 | Midstream | 0.05 | 1 | 1
COM-HRV-SH-371-03 | Current |  | Commercial | Heat Recovery Ventialation | Medium Use | New Construction/Retrofit | space heating | High Efficient 55% Heat Recovery Ventilation Medium Use Group (Hotel, Restaurant, Retail) | Ventilation with HRV Standalone | Ventilation without HRV |  |  | CFM | TRM Version 5.0 | 2020-11-12 | 0 | 2.13 | 0 | -2.44 | 0 | 0 | 0 | 8.28 | 14 | Midstream | 0.05 | 1 | 1
COM-HRV-SH-373-03 | Current |  | Commercial | Heat Recovery Ventialation | High Use | New Construction/Retrofit | space heating | High Efficient 65% Heat Recovery Ventilation High Use Group (Multi-Residential, Health Care, Nursing Homes) | Ventilation with HRV Standalone | Ventilation without HRV |  |  | CFM | TRM Version 5.0 | 2020-11-12 | 0 | 4.54 | 0 | -4.39 | 0 | 0 | 0 | 9.28 | 14 | Midstream | 0.05 | 1 | 1
COM-HRV-SH-375-03 | Current |  | Commercial | Heat Recovery Ventialation | Low Use | New Construction/Retrofit | space heating | High Efficient 65% Heat Recovery Ventilation Low Use Group (Office, Warehouse, School) | Ventilation with HRV Standalone | Ventilation without HRV |  |  | CFM | TRM Version 5.0 | 2020-11-12 | 0 | 1.61 | 0 | -1.56 | 0 | 0 | 0 | 9.28 | 14 | Midstream | 0.05 | 1 | 1
COM-HRV-SH-377-03 | Current |  | Commercial | Heat Recovery Ventialation | Medium Use | New Construction/Retrofit | space heating | High Efficient 65% Heat Recovery Ventilation Medium Use Group (Hotel, Restaurant, Retail) | Ventilation with HRV Standalone | Ventilation without HRV |  |  | CFM | TRM Version 5.0 | 2020-11-12 | 0 | 2.52 | 0 | -2.44 | 0 | 0 | 0 | 9.28 | 14 | Midstream | 0.05 | 1 | 1
COM-HRV-SH-379-03 | Current |  | Commercial | Heat Recovery Ventialation | High Use | New Construction/Retrofit | space heating | High Efficient 75% Heat Recovery Ventilation High Use Group (Multi-Residential, Health Care, Nursing Homes) | Ventilation with HRV Standalone | Ventilation without HRV |  |  | CFM | TRM Version 5.0 | 2020-11-12 | 0 | 5.24 | 0 | -4.39 | 0 | 0 | 0 | 10.28 | 14 | Midstream | 0.05 | 1 | 1
COM-HRV-SH-381-03 | Current |  | Commercial | Heat Recovery Ventialation | Low Use | New Construction/Retrofit | space heating | High Efficient 75% Heat Recovery Ventilation Low Use Group (Office, Warehouse, School) | Ventilation with HRV Standalone | Ventilation without HRV |  |  | CFM | TRM Version 5.0 | 2020-11-12 | 0 | 1.86 | 0 | -1.56 | 0 | 0 | 0 | 10.28 | 14 | Midstream | 0.05 | 1 | 1
COM-HRV-SH-383-03 | Current |  | Commercial | Heat Recovery Ventialation | Medium Use | New Construction/Retrofit | space heating | High Efficient 75% Heat Recovery Ventilation Medium Use Group (Hotel, Restaurant, Retail) | Ventilation with HRV Standalone | Ventilation without HRV |  |  | CFM | TRM Version 5.0 | 2020-11-12 | 0 | 2.91 | 0 | -2.44 | 0 | 0 | 0 | 10.28 | 14 | Midstream | 0.05 | 1 | 1
COM-HRV-SH-385-03 | Current |  | Commercial | Heat Recovery Ventialation | High Use | New Construction/Retrofit | space heating | High Efficient 85% Heat Recovery Ventilation High Use Group (Multi-Residential, Health Care, Nursing Homes) | Ventilation with HRV Standalone | Ventilation without HRV |  |  | CFM | TRM Version 5.0 | 2020-11-12 | 0 | 5.93 | 0 | -4.39 | 0 | 0 | 0 | 11.28 | 14 | Midstream | 0.05 | 1 | 1
COM-HRV-SH-387-03 | Current |  | Commercial | Heat Recovery Ventialation | Low Use | New Construction/Retrofit | space heating | High Efficient 85% Heat Recovery Ventilation Low Use Group (Office, Warehouse, School) | Ventilation with HRV Standalone | Ventilation without HRV |  |  | CFM | TRM Version 5.0 | 2020-11-12 | 0 | 2.11 | 0 | -1.56 | 0 | 0 | 0 | 11.28 | 14 | Midstream | 0.05 | 1 | 1
COM-HRV-SH-389-03 | Current |  | Commercial | Heat Recovery Ventialation | Medium Use | New Construction/Retrofit | space heating | High Efficient 85% Heat Recovery Ventilation Medium Use Group (Hotel, Restaurant, Retail) | Ventilation with HRV Standalone | Ventilation without HRV |  |  | CFM | TRM Version 5.0 | 2020-11-12 | 0 | 3.3 | 0 | -2.44 | 0 | 0 | 0 | 11.28 | 14 | Midstream | 0.05 | 1 | 1
COM-HRV-SH-391-03 | Current |  | Commercial | Heat Recovery Ventialation | Multi-Family, Health Care and Nursing Homes | New Construction/Retrofit | space heating | High Efficient 55% Heat Recovery Ventilation High Use Group (Multi-Residential, Health Care, Nursing Homes) | Ventilation with HRV Standalone | Ventilation without HRV |  |  | CFM | TRM Version 5.0 | 2020-11-12 | 0 | 3.84 | 0 | -4.39 | 0 | 0 | 0 | 8.28 | 14 | Midstream | 0.05 | 1 | 1
COM-HRV-SH-393-03 | Current |  | Commercial | Heat Recovery Ventialation | Hotels | New Construction/Retrofit | space heating | High Efficient 55% Heat Recovery Ventilation Medium Use Group (Hotel, Restaurant, Retail) | Ventilation with HRV Standalone | Ventilation without HRV |  |  | CFM | TRM Version 5.0 | 2020-11-12 | 0 | 2.74 | 0 | -3.14 | 0 | 0 | 0 | 8.28 | 14 | Midstream | 0.05 | 1 | 1
COM-HRV-SH-395-03 | Current |  | Commercial | Heat Recovery Ventialation | Restaurant | New Construction/Retrofit | space heating | High Efficient 55% Heat Recovery Ventilation Medium Use Group (Hotel, Restaurant, Retail) | Ventilation with HRV Standalone | Ventilation without HRV |  |  | CFM | TRM Version 5.0 | 2020-11-12 | 0 | 1.99 | 0 | -2.28 | 0 | 0 | 0 | 8.28 | 14 | Midstream | 0.05 | 1 | 1
COM-HRV-SH-397-03 | Current |  | Commercial | Heat Recovery Ventialation | Retail | New Construction/Retrofit | space heating | High Efficient 55% Heat Recovery Ventilation Medium Use Group (Hotel, Restaurant, Retail) | Ventilation with HRV Standalone | Ventilation without HRV |  |  | CFM | TRM Version 5.0 | 2020-11-12 | 0 | 1.67 | 0 | -1.91 | 0 | 0 | 0 | 8.28 | 14 | Midstream | 0.05 | 1 | 1
COM-HRV-SH-399-03 | Current |  | Commercial | Heat Recovery Ventialation | Office | New Construction/Retrofit | space heating | High Efficient 55% Heat Recovery Ventilation Low Use Group (Office, Warehouse, School) | Ventilation with HRV Standalone | Ventilation without HRV |  |  | CFM | TRM Version 5.0 | 2020-11-12 | 0 | 1.46 | 0 | -1.67 | 0 | 0 | 0 | 8.28 | 14 | Midstream | 0.05 | 1 | 1
COM-HRV-SH-401-03 | Current |  | Commercial | Heat Recovery Ventialation | Warehouse | New Construction/Retrofit | space heating | High Efficient 55% Heat Recovery Ventilation Low Use Group (Office, Warehouse, School) | Ventilation with HRV Standalone | Ventilation without HRV |  |  | CFM | TRM Version 5.0 | 2020-11-12 | 0 | 1.39 | 0 | -1.6 | 0 | 0 | 0 | 8.28 | 14 | Midstream | 0.05 | 1 | 1
COM-HRV-SH-403-03 | Current |  | Commercial | Heat Recovery Ventialation | School | New Construction/Retrofit | space heating | High Efficient 55% Heat Recovery Ventilation Low Use Group (Office, Warehouse, School) | Ventilation with HRV Standalone | Ventilation without HRV |  |  | CFM | TRM Version 5.0 | 2020-11-12 | 0 | 1.23 | 0 | -1.41 | 0 | 0 | 0 | 8.28 | 14 | Midstream | 0.05 | 1 | 1
COM-HRV-SH-405-03 | Current |  | Commercial | Heat Recovery Ventialation | Multi-Family, Health Care and Nursing Homes | New Construction/Retrofit | space heating | High Efficient 65% Heat Recovery Ventilation High Use Group (Multi-Residential, Health Care, Nursing Homes) | Ventilation with HRV Standalone | Ventilation without HRV |  |  | CFM | TRM Version 5.0 | 2020-11-12 | 0 | 4.54 | 0 | -4.39 | 0 | 0 | 0 | 9.28 | 14 | Midstream | 0.05 | 1 | 1
COM-HRV-SH-407-03 | Current |  | Commercial | Heat Recovery Ventialation | Hotels | New Construction/Retrofit | space heating | High Efficient 65% Heat Recovery Ventilation Medium Use Group (Hotel, Restaurant, Retail) | Ventilation with HRV Standalone | Ventilation without HRV |  |  | CFM | TRM Version 5.0 | 2020-11-12 | 0 | 3.24 | 0 | -3.14 | 0 | 0 | 0 | 9.28 | 14 | Midstream | 0.05 | 1 | 1
COM-HRV-SH-409-03 | Current |  | Commercial | Heat Recovery Ventialation | Restaurant | New Construction/Retrofit | space heating | High Efficient 65% Heat Recovery Ventilation Medium Use Group (Hotel, Restaurant, Retail) | Ventilation with HRV Standalone | Ventilation without HRV |  |  | CFM | TRM Version 5.0 | 2020-11-12 | 0 | 2.35 | 0 | -2.28 | 0 | 0 | 0 | 9.28 | 14 | Midstream | 0.05 | 1 | 1
COM-HRV-SH-411-03 | Current |  | Commercial | Heat Recovery Ventialation | Retail | New Construction/Retrofit | space heating | High Efficient 65% Heat Recovery Ventilation Medium Use Group (Hotel, Restaurant, Retail) | Ventilation with HRV Standalone | Ventilation without HRV |  |  | CFM | TRM Version 5.0 | 2020-11-12 | 0 | 1.97 | 0 | -1.91 | 0 | 0 | 0 | 9.28 | 14 | Midstream | 0.05 | 1 | 1
COM-HRV-SH-413-03 | Current |  | Commercial | Heat Recovery Ventialation | Office | New Construction/Retrofit | space heating | High Efficient 65% Heat Recovery Ventilation Low Use Group (Office, Warehouse, School) | Ventilation with HRV Standalone | Ventilation without HRV |  |  | CFM | TRM Version 5.0 | 2020-11-12 | 0 | 1.73 | 0 | -1.67 | 0 | 0 | 0 | 9.28 | 14 | Midstream | 0.05 | 1 | 1
COM-HRV-SH-415-03 | Current |  | Commercial | Heat Recovery Ventialation | Warehouse | New Construction/Retrofit | space heating | High Efficient 65% Heat Recovery Ventilation Low Use Group (Office, Warehouse, School) | Ventilation with HRV Standalone | Ventilation without HRV |  |  | CFM | TRM Version 5.0 | 2020-11-12 | 0 | 1.65 | 0 | -1.6 | 0 | 0 | 0 | 9.28 | 14 | Midstream | 0.05 | 1 | 1
COM-HRV-SH-417-03 | Current |  | Commercial | Heat Recovery Ventialation | School | New Construction/Retrofit | space heating | High Efficient 65% Heat Recovery Ventilation Low Use Group (Office, Warehouse, School) | Ventilation with HRV Standalone | Ventilation without HRV |  |  | CFM | TRM Version 5.0 | 2020-11-12 | 0 | 1.46 | 0 | -1.41 | 0 | 0 | 0 | 9.28 | 14 | Midstream | 0.05 | 1 | 1
COM-HRV-SH-419-03 | Current |  | Commercial | Heat Recovery Ventialation | Multi-Family, Health Care and Nursing Homes | New Construction/Retrofit | space heating | High Efficient 75% Heat Recovery Ventilation High Use Group (Multi-Residential, Health Care, Nursing Homes) | Ventilation with HRV Standalone | Ventilation without HRV |  |  | CFM | TRM Version 5.0 | 2020-11-12 | 0 | 5.24 | 0 | -4.39 | 0 | 0 | 0 | 10.28 | 14 | Midstream | 0.05 | 1 | 1
COM-HRV-SH-421-03 | Current |  | Commercial | Heat Recovery Ventialation | Hotels | New Construction/Retrofit | space heating | High Efficient 75% Heat Recovery Ventilation Medium Use Group (Hotel, Restaurant, Retail) | Ventilation with HRV Standalone | Ventilation without HRV |  |  | CFM | TRM Version 5.0 | 2020-11-12 | 0 | 3.74 | 0 | -3.14 | 0 | 0 | 0 | 10.28 | 14 | Midstream | 0.05 | 1 | 1
COM-HRV-SH-423-03 | Current |  | Commercial | Heat Recovery Ventialation | Restaurant | New Construction/Retrofit | space heating | High Efficient 75% Heat Recovery Ventilation Medium Use Group (Hotel, Restaurant, Retail) | Ventilation with HRV Standalone | Ventilation without HRV |  |  | CFM | TRM Version 5.0 | 2020-11-12 | 0 | 2.71 | 0 | -2.28 | 0 | 0 | 0 | 10.28 | 14 | Midstream | 0.05 | 1 | 1
COM-HRV-SH-425-03 | Current |  | Commercial | Heat Recovery Ventialation | Retail | New Construction/Retrofit | space heating | High Efficient 75% Heat Recovery Ventilation Medium Use Group (Hotel, Restaurant, Retail) | Ventilation with HRV Standalone | Ventilation without HRV |  |  | CFM | TRM Version 5.0 | 2020-11-12 | 0 | 2.28 | 0 | -1.91 | 0 | 0 | 0 | 10.28 | 14 | Midstream | 0.05 | 1 | 1
COM-HRV-SH-427-03 | Current |  | Commercial | Heat Recovery Ventialation | Office | New Construction/Retrofit | space heating | High Efficient 75% Heat Recovery Ventilation Low Use Group (Office, Warehouse, School) | Ventilation with HRV Standalone | Ventilation without HRV |  |  | CFM | TRM Version 5.0 | 2020-11-12 | 0 | 1.99 | 0 | -1.67 | 0 | 0 | 0 | 10.28 | 14 | Midstream | 0.05 | 1 | 1
COM-HRV-SH-429-03 | Current |  | Commercial | Heat Recovery Ventialation | Warehouse | New Construction/Retrofit | space heating | High Efficient 75% Heat Recovery Ventilation Low Use Group (Office, Warehouse, School) | Ventilation with HRV Standalone | Ventilation without HRV |  |  | CFM | TRM Version 5.0 | 2020-11-12 | 0 | 1.9 | 0 | -1.6 | 0 | 0 | 0 | 10.28 | 14 | Midstream | 0.05 | 1 | 1
COM-HRV-SH-431-03 | Current |  | Commercial | Heat Recovery Ventialation | School | New Construction/Retrofit | space heating | High Efficient 75% Heat Recovery Ventilation Low Use Group (Office, Warehouse, School) | Ventilation with HRV Standalone | Ventilation without HRV |  |  | CFM | TRM Version 5.0 | 2020-11-12 | 0 | 1.68 | 0 | -1.41 | 0 | 0 | 0 | 10.28 | 14 | Midstream | 0.05 | 1 | 1
COM-HRV-SH-433-03 | Current |  | Commercial | Heat Recovery Ventialation | Multi-Family, Health Care and Nursing Homes | New Construction/Retrofit | space heating | High Efficient 85% Heat Recovery Ventilation High Use Group (Multi-Residential, Health Care, Nursing Homes) | Ventilation with HRV Standalone | Ventilation without HRV |  |  | CFM | TRM Version 5.0 | 2020-11-12 | 0 | 5.93 | 0 | -4.39 | 0 | 0 | 0 | 11.28 | 14 | Midstream | 0.05 | 1 | 1
COM-HRV-SH-435-03 | Current |  | Commercial | Heat Recovery Ventialation | Hotels | New Construction/Retrofit | space heating | High Efficient 85% Heat Recovery Ventilation Medium Use Group (Hotel, Restaurant, Retail) | Ventilation with HRV Standalone | Ventilation without HRV |  |  | CFM | TRM Version 5.0 | 2020-11-12 | 0 | 4.24 | 0 | -3.14 | 0 | 0 | 0 | 11.28 | 14 | Midstream | 0.05 | 1 | 1
COM-HRV-SH-437-03 | Current |  | Commercial | Heat Recovery Ventialation | Restaurant | New Construction/Retrofit | space heating | High Efficient 85% Heat Recovery Ventilation Medium Use Group (Hotel, Restaurant, Retail) | Ventilation with HRV Standalone | Ventilation without HRV |  |  | CFM | TRM Version 5.0 | 2020-11-12 | 0 | 3.07 | 0 | -2.28 | 0 | 0 | 0 | 11.28 | 14 | Midstream | 0.05 | 1 | 1
COM-HRV-SH-439-03 | Current |  | Commercial | Heat Recovery Ventialation | Retail | New Construction/Retrofit | space heating | High Efficient 85% Heat Recovery Ventilation Medium Use Group (Hotel, Restaurant, Retail) | Ventilation with HRV Standalone | Ventilation without HRV |  |  | CFM | TRM Version 5.0 | 2020-11-12 | 0 | 2.58 | 0 | -1.91 | 0 | 0 | 0 | 11.28 | 14 | Midstream | 0.05 | 1 | 1
COM-HRV-SH-441-03 | Current |  | Commercial | Heat Recovery Ventialation | Office | New Construction/Retrofit | space heating | High Efficient 85% Heat Recovery Ventilation Low Use Group (Office, Warehouse, School) | Ventilation with HRV Standalone | Ventilation without HRV |  |  | CFM | TRM Version 5.0 | 2020-11-12 | 0 | 2.26 | 0 | -1.67 | 0 | 0 | 0 | 11.28 | 14 | Midstream | 0.05 | 1 | 1
COM-HRV-SH-443-03 | Current |  | Commercial | Heat Recovery Ventialation | Warehouse | New Construction/Retrofit | space heating | High Efficient 85% Heat Recovery Ventilation Low Use Group (Office, Warehouse, School) | Ventilation with HRV Standalone | Ventilation without HRV |  |  | CFM | TRM Version 5.0 | 2020-11-12 | 0 | 2.15 | 0 | -1.6 | 0 | 0 | 0 | 11.28 | 14 | Midstream | 0.05 | 1 | 1
COM-HRV-SH-445-03 | Current |  | Commercial | Heat Recovery Ventialation | School | New Construction/Retrofit | space heating | High Efficient 85% Heat Recovery Ventilation Low Use Group (Office, Warehouse, School) | Ventilation with HRV Standalone | Ventilation without HRV |  |  | CFM | TRM Version 5.0 | 2020-11-12 | 0 | 1.91 | 0 | -1.41 | 0 | 0 | 0 | 11.28 | 14 | Midstream | 0.05 | 1 | 1
COM-CM-SH-498-03 | Current |  | Commercial | Condensing Make Up Air Unit | Commercial | New Construction/Natural Replacement | space heating | Condensing Make Up Air Unit (MUA) - Commercial | VFD | Conventional MUA | 80% Thermal Efficiency |  | CFM | TRM Version 5.0 | 2020-11-12 | 0 | 2.03 | 0 | 2.04 | 0 | 0 | 870 | 1.02 | 20 | Midstream | 0.05 | 1 | 1
COM-CM-SH-501-03 | Current |  | Commercial | Condensing Make Up Air Unit | Multi-Residential and Long Term Care | New Construction/Natural Replacement | space heating | Condensing Make Up Air Unit (MUA) - Commercial | VFD | Conventional MUA | 80% Thermal Efficiency |  | CFM | TRM Version 5.0 | 2020-11-12 | 0 | 3 | 0 | 2.3 | 0 | 0 | 870 | 1.02 | 20 | Midstream | 0.05 | 1 | 1
COM-CMB-FS-621-02 | Current |  | Commercial | Combination Oven |  | New Construction/Natural Replacement | food service | Energy Star Combination Oven | Energy Star Rated Combiniation Oven, 15-28 pan | Conventional combination oven |  | unit |  | TRM Version 6.0 | 2021-12-16 | 1295 | 0 | 4747 | 0 | 51684 | 0 | 5007 | 0 | 12 | Midstream | 0.2 | 1 | 1
COM-CMB-FS-622-02 | Current |  | Commercial | Combination Oven |  | New Construction/Natural Replacement | food service | Energy Star Combination Oven | Energy Star Rated Combiniation Oven, 29+ pan | Conventional combination oven |  | unit |  | TRM Version 6.0 | 2021-12-16 | 1048 | 0 | 485 | 0 | 599459 | 0 | 8507 | 0 | 12 | Midstream | 0.2 | 1 | 1
COM-CMB-FS-623-02 | Current |  | Commercial | Combination Oven |  | New Construction/Natural Replacement | food service | Energy Star Combination Oven | Energy Star Rated Combiniation Oven, average | Conventional combination oven |  | unit |  | TRM Version 6.0 | 2021-12-16 | 1186 | 0 | 2088 | 0 | 145120 | 0 | 4440 | 0 | 12 | Midstream | 0.2 | 1 | 1
COM-CO-FS-520-03 | Current |  | Commercial | Convection Ovens |  | New Construction/Natural Replacement | food service | Energy Star Convection Ovens | Energy Star Rated Convection Oven (Full Size) | Conventional Convection Oven (Full Size) |  | unit |  | TRM Version 6.0 | 2021-12-16 | 954 | 0 | 44.2 | 0 | 0 | 0 | 1200 | 0 | 12 | Midstream | 0.2 | 1 | 1
COM-RO-FS-651-02 | Current |  | Commercial | Rack Oven |  | New Construction/Natural Replacement | food service | ENERGY STAR Rack Oven | Energy Star Rated Rack Oven, Double | Conventiona rack oven |  | unit |  | TRM Version 6.0 | 2021-12-16 | 1187 | 0 | 1858 | 0 | 0 | 0 | 2591 | 0 | 12 | Midstream | 0.2 | 1 | 1
COM-RO-FS-650-02 | Current |  | Commercial | Rack Oven |  | New Construction/Natural Replacement | food service | ENERGY STAR Rack Oven | Energy Star Rated Rack Oven, Single | Conventiona rack oven |  | unit |  | TRM Version 6.0 | 2021-12-16 | 915 | 0 | 826 | 0 | 0 | 0 | 1544 | 0 | 12 | Midstream | 0.2 | 1 | 1
COM-OL-WH-329-03 | Current |  | Commercial | Ozone Laundry |  | New Construction/Retrofit | water heating | Commercial Ozone Laundry Treatment | Ozone Treatment Tunnel Washer <= 120 lbs | Commercial laundry with no ozone treatment system |  |  | lbs/yr | TRM Version 7.0 | 2022-11-30 | 0 | 0.0295 | 0 | 0.0015 | 0 | 1.29 | 71429 | 0 | 15 | Midstream | 0.08 | 1 | 1
COM-OL-WH-331-03 | Current |  | Commercial | Ozone Laundry |  | New Construction/Retrofit | water heating | Commercial Ozone Laundry Treatment | Ozone Treatment Tunnel Washer=> 500 lbs | Commercial laundry with no ozone treatment system |  |  | lbs/yr | TRM Version 7.0 | 2022-11-30 | 0 | 0.0295 | 0 | 0.0015 | 0 | 1.29 | 228571 | 0 | 15 | Midstream | 0.08 | 1 | 1
COM-OL-WH-330-03 | Current |  | Commercial | Ozone Laundry |  | New Construction/Retrofit | water heating | Commercial Ozone Laundry Treatment | Ozone Treatment Tunnel Washer 121 lbs to 499 lbs | Commercial laundry with no ozone treatment system |  |  | lbs/yr | TRM Version 7.0 | 2022-11-30 | 0 | 0.0295 | 0 | 0.0015 | 0 | 1.29 | 150000 | 0 | 15 | Midstream | 0.08 | 1 | 1
COM-OL-WH-326-03 | Current |  | Commercial | Ozone Laundry |  | New Construction/Retrofit | water heating | Commercial Ozone Laundry Treatment | Ozone Treatment Washer extractor =< 60 lbs | Commercial laundry with no ozone treatment system |  |  | lbs/yr | TRM Version 7.0 | 2022-11-30 | 0 | 0.0376 | 0 | 0.00211 | 0 | 2.1 | 15714 | 0 | 15 | Midstream | 0.08 | 1 | 1
COM-OL-WH-327-03 | Current |  | Commercial | Ozone Laundry |  | New Construction/Retrofit | water heating | Commercial Ozone Laundry Treatment | Ozone Treatment Washer extractor 61 lbs to 499 lbs | Commercial laundry with no ozone treatment system |  |  | lbs/yr | TRM Version 7.0 | 2022-11-30 | 0 | 0.0376 | 0 | 0.00211 | 0 | 2.1 | 35714 | 0 | 15 | Midstream | 0.08 | 1 | 1
COM-OL-WH-328-03 | Current |  | Commercial | Ozone Laundry |  | New Construction/Retrofit | water heating | Commercial Ozone Laundry Treatment | Ozone Treatment Washer extractor=> 500 lbs | Commercial laundry with no ozone treatment system |  |  | lbs/yr | TRM Version 7.0 | 2022-11-30 | 0 | 0.0376 | 0 | 0.00211 | 0 | 2.1 | 44286 | 0 | 15 | Midstream | 0.08 | 1 | 1
COM-CMB-FS-620-02 | Current |  | Commercial | Combination Oven |  | New Construction/Natural Replacement | food service | Energy Star Combination Oven | Energy Star Rated Combination Oven, 6-14 pan | Conventional combination oven |  | unit |  | TRM Version 6.0 | 2021-12-16 | 1104 | 0 | 72 | 0 | 209664 | 0 | 3941 | 0 | 12 | Midstream | 0.2 | 1 | 1
COM-GR-FS-800-04 | Current |  | Commercial | Griddles |  | New Construction/Natural Replacement | food service | Energy Star Griddle | ENERGY STAR Certified Griddle | Non-ENERGY STAR Griddle |  |  | ft | TRM Version 7.0 | 2022-11-30 | 0 | 439 | 0 | 0 | 0 | 0 | 0 | 1096 | 12 | Midstream | 0.2 | 1 | 1
COM-GR-FS-801-04 | Current |  | Commercial | Griddles |  | New Construction/Natural Replacement | food service | Energy Star Griddle | ENERGY STAR Certified Griddle | Non-ENERGY STAR Griddle |  | unit |  | TRM Version 7.0 | 2022-11-30 | 1974 | 0 | 0 | 0 | 0 | 0 | 4581 | 0 | 12 | Midstream | 0.2 | 1 | 1
COM-FR-FS-325-03 | Current | Split measure into two Vat sizes | Commercial | Fryer |  | New Construction/Natural Replacement | food service | Energy Star Fryer, Standard Vat | Energy Star Rated Fryer | Non-Energy Star rated Fryer |  | unit |  | TRM Version 7.0 | 2022-11-30 | 1466 | 0 | 0 | 0 | 0 | 0 | 2657 | 0 | 12 | Midstream | 0.2 | 1 | 1
COM-FR-FS-326-03 | Current | Split measure into two Vat sizes | Commercial | Fryer |  | New Construction/Natural Replacement | food service | Energy Star Fryer, Large Vat | Energy Star Rated Fryer | Non-Energy Star rated Fryer |  | unit |  | TRM Version 7.0 | 2022-11-30 | 1709 | 0 | 0 | 0 | 0 | 0 | 3113 | 0 | 12 | Midstream | 0.2 | 1 | 1
COM-SC-FS-325-03 | Current |  | Commercial | Steam Cookers |  | New Construction/Natural Replacement | food service | Energy Star Steam Cookers | Energy Star Rated Steam Cooker | Boiler-based steam cooker |  | unit |  | TRM Version 7.0 | 2022-11-30 | 8461 | 0 | 0 | 0 | 1109458 | 0 | 3045 | 0 | 12 | Midstream | 0.2 | 1 | 1
COM-CNB-FS-810-04 | Current | New measure in TRM V7.0 | Commercial | Conveyor Broiler |  | New Construction/Natural Replacement | food service | Energy-Efficient Conveyor Broiler, <22" width | high-efficiency conveyor broiler with a catalyst and an idle input rate less than the rates listed below or a dual stage or modulating gas valve with a capability of throttling the input rate below the idle rates <40,000 Btu/h | Conventional Conveyor Broiler |  | unit |  | TRM Version 7.0 | 2022-11-30 | 1954 | 0 | 2443 | 0 | 0 | 0 | 3154 | 0 | 12 | Midstream | 0.2 | 1 | 1
COM-CNB-FS-811-04 | Current | New measure in TRM V7.0 | Commercial | Conveyor Broiler |  | New Construction/Natural Replacement | food service | Energy-Efficient Conveyor Broiler, 22" - 26" width | high-efficiency conveyor broiler with a catalyst and an idle input rate less than the rates listed below or a dual stage or modulating gas valve with a capability of throttling the input rate below the idle rates <60,000 Btu/h | Conventional Conveyor Broiler |  | unit |  | TRM Version 7.0 | 2022-11-30 | 3070 | 0 | 3839 | 0 | 0 | 0 | 3933 | 0 | 12 | Midstream | 0.2 | 1 | 1
COM-CNB-FS-812-04 | Current | New measure in TRM V7.0 | Commercial | Conveyor Broiler |  | New Construction/Natural Replacement | food service | Energy-Efficient Conveyor Broiler, > 26" width | high-efficiency conveyor broiler with a catalyst and an idle input rate less than the rates listed below or a dual stage or modulating gas valve with a capability of throttling the input rate below the idle rates <70,000 Btu/h | Conventional Conveyor Broiler |  | unit |  | TRM Version 7.0 | 2022-11-30 | 3768 | 0 | 4712 | 0 | 0 | 0 | 4586 | 0 | 12 | Midstream | 0.2 | 1 | 1
COM-CNO-FS-806-04 | Current | New measure in TRM V7.0 | Commercial | Conveyor Oven |  | New Construction/Natural Replacement | food service | Energy-Efficient Conveyor Oven, large ≥ 1520 sq in | Large Conveyor Oven Chamber Area ≥ 1520 sq in, 45% cooking efficiency | Conventional Conveyor Oven |  | unit |  | TRM Version 7.0 | 2022-11-30 | 1519 | 0 | 2601 | 0 | 0 | 0 | 1994 | 0 | 12 | Midstream | 0.2 | 1 | 1
COM-UB-FS-332-03 | Current |  | Commercial | Under-Fired Broilers |  | New Construction/Natural Replacement | food service | High Efficiency Under-Fired Broilers - 3 foot | low idle energy rate (≤22,000 Btu/hr per linear foot) | Conventional Efficiency Under-Fired Broiler | conventional underfired broiler | unit |  | TRM Version 7.0 | 2022-11-30 | 2636 | 0 | 0 | 0 | 0 | 0 | 1868 | 0 | 12 | Midstream | 0.2 | 1 | 1
COM-UB-FS-333-03 | Current |  | Commercial | Under-Fired Broilers |  | New Construction/Natural Replacement | food service | High Efficiency Under-Fired Broilers - 4 foot | low idle energy rate (≤22,000 Btu/hr per linear foot) | Conventional Efficiency Under-Fired Broiler | conventional underfired broiler | unit |  | TRM Version 7.0 | 2022-11-30 | 3515 | 0 | 0 | 0 | 0 | 0 | 2948 | 0 | 12 | Midstream | 0.2 | 1 | 1
COM-UB-FS-334-03 | Current |  | Commercial | Under-Fired Broilers |  | New Construction/Natural Replacement | food service | High Efficiency Under-Fired Broilers - 5 foot | low idle energy rate (≤22,000 Btu/hr per linear foot) | Conventional Efficiency Under-Fired Broiler | conventional underfired broiler | unit |  | TRM Version 7.0 | 2022-11-30 | 4393 | 0 | 0 | 0 | 0 | 0 | 3820 | 0 | 12 | Midstream | 0.2 | 1 | 1
COM-UB-FS-335-03 | Current |  | Commercial | Under-Fired Broilers |  | New Construction/Natural Replacement | food service | High Efficiency Under-Fired Broilers - 6 foot | low idle energy rate (≤22,000 Btu/hr per linear foot) | Conventional Efficiency Under-Fired Broiler | conventional underfired broiler | unit |  | TRM Version 7.0 | 2022-11-30 | 5272 | 0 | 0 | 0 | 0 | 0 | 4134 | 0 | 12 | Midstream | 0.2 | 1 | 1
COM-UB-FS-336-03 | Current |  | Commercial | Under-Fired Broilers |  | New Construction/Natural Replacement | food service | High Efficiency Under-Fired Broilers - 2 foot | low idle energy rate (≤22,000 Btu/hr per linear foot) | Conventional Efficiency Under-Fired Broiler | conventional underfired broiler | unit |  | TRM Version 7.0 | 2022-11-30 | 1757 | 0 | 0 | 0 | 0 | 0 | 1264 | 0 | 12 | Midstream | 0.2 | 1 | 1
COM-DW-WH-555-04 | Current | revised from TRM Version 5.0: natural gas, electric savings, and water savings | Commercial | Dishwasher |  | New Construction/Natural Replacement | water heating | Energy Star Dishwasher | Multi Tank Conveyor - High Temperature | Non-Energy Star Dishwasher |  | unit |  | TRM Version 7.0 | 2022-11-30 | 2970 | 0 | 14386 | 0 | 437533 | 0 | 1216 | 0 | 20 | Midstream | 0.27 | 1 | 1
COM-DW-WH-556-04 | Current | revised from TRM Version 5.0: natural gas, electric savings, and water savings | Commercial | Dishwasher |  | New Construction/Natural Replacement | water heating | Energy Star Dishwasher | Multi Tank Conveyor - Low Temperature | Non-Energy Star Dishwasher |  | unit |  | TRM Version 7.0 | 2022-11-30 | 3447 | 0 | 3375 | 0 | 507851 | 0 | 1216 | 0 | 20 | Midstream | 0.27 | 1 | 1
COM-DW-WH-553-04 | Current | revised from TRM Version 5.0: natural gas, electric savings, and water savings | Commercial | Dishwasher |  | New Construction/Natural Replacement | water heating | Energy Star Dishwasher | Single Tank Conveyor – High Temperature | Non-Energy Star Dishwasher |  | unit |  | TRM Version 7.0 | 2022-11-30 | 1167 | 0 | 7599 | 0 | 171888 | 0 | 2570 | 0 | 20 | Midstream | 0.27 | 1 | 1
COM-DW-WH-554-04 | Current | revised from TRM Version 5.0: natural gas, electric savings, and water savings | Commercial | Dishwasher |  | New Construction/Natural Replacement | water heating | Energy Star Dishwasher | Single Tank Conveyor - Low Temperature | Non-Energy Star Dishwasher |  | unit |  | TRM Version 7.0 | 2022-11-30 | 2546 | 0 | 3474 | 0 | 375028 | 0 | 0 | 0 | 20 | Midstream | 0.27 | 1 | 1
COM-CNO-FS-805-04 | Current | New measure in TRM V7.0 | Commercial | Conveyor Oven |  | New Construction/Natural Replacement | food service | Energy-Efficient Conveyor Oven, small < 1520 sq in | Small Conveyor Oven Chamber Area <1520 sq in, 37% cooking efficiency | Conventional Conveyor Oven |  | unit |  | TRM Version 7.0 | 2022-11-30 | 562 | 0 | 619 | 0 | 0 | 0 | 859 | 0 | 12 | Midstream | 0.2 | 1 | 1
COM-DW-WH-551-04 | Current | revised from TRM Version 5.0: natural gas, electric savings, and water savings | Commercial | Dishwasher |  | New Construction/Natural Replacement | water heating | Energy Star Dishwasher | Stationary Single Tank Door – High Temperature | Non-Energy Star Dishwasher |  | unit |  | TRM Version 7.0 | 2022-11-30 | 1262 | 0 | 6032 | 0 | 185951 | 0 | 1247 | 0 | 15 | Midstream | 0.2 | 1 | 1
COM-DW-WH-552-04 | Current | revised from TRM Version 5.0: natural gas, electric savings, and water savings | Commercial | Dishwasher |  | New Construction/Natural Replacement | water heating | Energy Star Dishwasher | Stationary Single Tank Door – Low Temperature | Non-Energy Star Dishwasher |  | unit |  | TRM Version 7.0 | 2022-11-30 | 2846 | 0 | 946 | 0 | 419302 | 0 | 830 | 0 | 15 | Midstream | 0.2 | 1 | 1
COM-DW-WH-549-04 | Current | revised from TRM Version 5.0: natural gas, electric savings, and water savings | Commercial | Dishwasher |  | New Construction/Natural Replacement | water heating | Energy Star Dishwasher | Undercounter – High Temperature | Non-Energy Star Dishwasher |  | unit |  | TRM Version 7.0 | 2022-11-30 | 285 | 0 | 2767 | 0 | 41995 | 0 | 2538 | 0 | 10 | Midstream | 0.4 | 1 | 1
COM-DW-WH-550-04 | Current | revised from TRM Version 5.0: natural gas, electric savings, and water savings | Commercial | Dishwasher |  | New Construction/Natural Replacement | water heating | Energy Star Dishwasher | Undercounter – Low Temperature | Non-Energy Star Dishwasher |  | unit |  | TRM Version 7.0 | 2022-11-30 | 438 | 0 | 1405 | 0 | 64458 | 0 | 293 | 0 | 10 | Midstream | 0.4 | 1 | 1
COM-DK-SH-524-04 | Current | Updated savings values | Commercial | Demand Control Kitchen Ventilation |  | New Construction/Natural Replacement | space heating | Demand Control Kitchen Ventilation | 0 - 5,000 CFM | Constant Volume Kitchen Ventilation |  | unit |  | TRM Version 8.0 | 2024-04-30 | 4307 | 0 | 15865 | 0 | 0 | 0 | 5490 | 0 | 15 | Midstream | 0.05 | 1 | 1
COM-DK-SH-526-04 | Current | Updated savings values | Commercial | Demand Control Kitchen Ventilation |  | New Construction/Natural Replacement | space heating | Demand Control Kitchen Ventilation | 10,001 - 15,000 CFM | Constant Volume Kitchen Ventilation |  | unit |  | TRM Version 8.0 | 2024-04-30 | 17947 | 0 | 29586 | 0 | 0 | 0 | 22875 | 0 | 15 | Midstream | 0.05 | 1 | 1
COM-DK-SH-525-04 | Current | Updated savings values | Commercial | Demand Control Kitchen Ventilation |  | New Construction/Natural Replacement | space heating | Demand Control Kitchen Ventilation | 5,001 - 10,000 CFM | Constant Volume Kitchen Ventilation |  | unit |  | TRM Version 8.0 | 2024-04-30 | 10768 | 0 | 22364 | 0 | 0 | 0 | 13725 | 0 | 15 | Midstream | 0.05 | 1 | 1
COM-CU-SH-515-03 | Current | Updated size descriptions in eTRM to match TRM, entered energy savings that appear to be new from last TRM | Commercial | Condensing Unit Heater |  | Natural Replacement | space heating | Condensing Unit Heater | 125-225 kBtu/hr 90% Thermal Efficiency, 89% Annual Efficiency | Non-Condensing Unit Heater | 80% Thermal Efficiency, 78% Annual Efficiency |  | kBtu/hr input capacity | TRM Version 8.0 | 2024-04-30 | 0 | 6.52 | -438 | 0 | 0 | 0 | 0 | 16.07 | 18 | Midstream | 0 | 1 | 1
COM-CU-SH-516-03 | Current | Entered energy savings that appear to be new from last TRM | Commercial | Condensing Unit Heater |  | Natural Replacement | space heating | Condensing Unit Heater | 225-300 kBtu/hr 90% Thermal Efficiency, 89% Annual Efficiency | Non-Condensing Unit Heater | 80% Thermal Efficiency, 78% Annual Efficiency |  | kBtu/hr input capacity | TRM Version 8.0 | 2024-04-30 | 0 | 6.52 | -451 | 0 | 0 | 0 | 0 | 16.07 | 18 | Midstream | 0 | 1 | 1
COM-CU-SH-514-03 | Current | Updated size descriptions in eTRM to match TRM, entered energy savings that appear to be new from last TRM | Commercial | Condensing Unit Heater |  | Natural Replacement | space heating | Condensing Unit Heater | 30-125 kBtu/hr - 90% Thermal Efficiency, 89% Annual Efficiency | Non-Condensing Unit Heater | 80% Thermal Efficiency, 78% Annual Efficiency |  | kBtu/hr input capacity | TRM Version 8.0 | 2024-04-30 | 0 | 6.52 | -244 | 0 | 0 | 0 | 0 | 16.07 | 18 | Midstream | 0 | 1 | 1
COM-CU-SH-518-03 | Current | Updated size descriptions in eTRM to match TRM, entered energy savings that appear to be new from last TRM | Commercial | Condensing Unit Heater |  | New Construction | space heating | Condensing Unit Heater | 125-225 kBtu/hr 90% Thermal Efficiency, 89% Annual Efficiency | Non-Condensing Unit Heater | 80% Thermal Efficiency, 78% Annual Efficiency |  | kBtu/hr input capacity | TRM Version 8.0 | 2024-04-30 | 0 | 4.62 | -310 | 0 | 0 | 0 | 0 | 16.07 | 18 | Midstream | 0 | 1 | 1
COM-CU-SH-519-03 | Current | Entered energy savings that appear to be new from last TRM | Commercial | Condensing Unit Heater |  | New Construction | space heating | Condensing Unit Heater | 225-300 kBtu/hr 90% Thermal Efficiency, 89% Annual Efficiency | Non-Condensing Unit Heater | 80% Thermal Efficiency, 78% Annual Efficiency |  | kBtu/hr input capacity | TRM Version 8.0 | 2024-04-30 | 0 | 4.62 | -320 | 0 | 0 | 0 | 0 | 16.07 | 18 | Midstream | 0 | 1 | 1
COM-CU-SH-517-03 | Current | Updated size descriptions in eTRM to match TRM, entered energy savings that appear to be new from last TRM | Commercial | Condensing Unit Heater |  | New Construction | space heating | Condensing Unit Heater | 30-125 kBtu/hr - 90% Thermal Efficiency, 89% Annual Efficiency | Non-Condensing Unit Heater | 80% Thermal Efficiency, 78% Annual Efficiency |  | kBtu/hr input capacity | TRM Version 8.0 | 2024-04-30 | 0 | 4.62 | -173 | 0 | 0 | 0 | 0 | 16.07 | 18 | Midstream | 0 | 1 | 1
COM-CT-WH-533-10 | Current | Updated size descriptions in eTRM to match TRM. Split New Construction and Natural Replacement to effectively represent baseline. Updated technology descriptions. Updated energy savings. | Commercial | Condensing Tankless Water Heater | High Utilization | Natural Replacement | water heating | Condensing Tankless Water Heater - High Utilization | <200 kBtu/hr UEF >= 0.90 Stand-by Loss = negligible | Non-Condensing Storage Water Heater | Storage Water Heater 75 kBtu/hr. and greater Uniform Energy Factor (UEF)=0.6597-0.00024Vs | unit | kBtu/hr input capacity | TRM Version 8.0 | 2024-04-30 | 212 | 4.349 | 0 | 0 | 0 | 0 | 3030 | 0 | 20 | Midstream | 0.02 | 1 | 1
COM-CT-WH-533-11 | Current | Split New Construction and Natural Replacement to effectively represent baseline. Updated technology descriptions. Updated energy savings. | Commercial | Condensing Tankless Water Heater | High Utilization | Natural Replacement | water heating | Condensing Tankless Water Heater - High Utilization | >=200 kBtu/hr Thermal efficiency >= 94% Stand-by Loss = negligible | Non-Condensing Storage Water Heater | Storage Water Heater 75 kBtu/hr. and greater Thermal efficiency = 80% Stand-by Loss Q/800 +110√V0 Btu/hr | unit | kBtu/hr input capacity | TRM Version 8.0 | 2024-04-30 | 351 | 1.954 | 0 | 0 | 0 | 0 | 3030 | 0 | 20 | Midstream | 0.02 | 1 | 1
COM-CT-WH-533-12 | Current | Updated size descriptions in eTRM to match TRM. Split New Construction and Natural Replacement to effectively represent baseline. Updated technology descriptions. Updated energy savings. | Commercial | Condensing Tankless Water Heater | High Utilization | Natural Replacement | water heating | Condensing Tankless Water Heater - High Utilization | <200 kBtu/hr UEF >= 0.95 Stand-by Loss = negligible | Non-Condensing Storage Water Heater | Storage Water Heater 75 kBtu/hr. and greater Uniform Energy Factor (UEF)=0.6597-0.00024Vs | unit | kBtu/hr input capacity | TRM Version 8.0 | 2024-04-30 | 212 | 5.211 | 0 | 0 | 0 | 0 | 3030 | 0 | 20 | Midstream | 0.02 | 1 | 1
COM-CT-WH-533-13 | Current | Split New Construction and Natural Replacement to effectively represent baseline. Updated technology descriptions. Updated energy savings. | Commercial | Condensing Tankless Water Heater | High Utilization | Natural Replacement | water heating | Condensing Tankless Water Heater - High Utilization | >=200 kBtu/hr Thermal efficiency >= 96% Stand-by Loss = negligible | Non-Condensing Storage Water Heater | Storage Water Heater 75 kBtu/hr. and greater Thermal efficiency = 80% Stand-by Loss Q/800 +110√V0 Btu/hr | unit | kBtu/hr input capacity | TRM Version 8.0 | 2024-04-30 | 521 | 2.233 | 0 | 0 | 0 | 0 | 3030 | 0 | 20 | Midstream | 0.02 | 1 | 1
COM-CT-WH-533-14 | Current | Split New Construction and Natural Replacement to effectively represent baseline. Updated technology descriptions. Updated energy savings. | Commercial | Condensing Tankless Water Heater | High Utilization | Natural Replacement | water heating | Condensing Tankless Water Heater - High Utilization | >=200 kBtu/hr Thermal efficiency >= 98% Stand-by Loss = negligible | Non-Condensing Storage Water Heater | Storage Water Heater 75 kBtu/hr. and greater Thermal efficiency = 80% Stand-by Loss Q/800 +110√V0 Btu/hr | unit | kBtu/hr input capacity | TRM Version 8.0 | 2024-04-30 | 867 | 2.512 | 0 | 0 | 0 | 0 | 3030 | 0 | 20 | Midstream | 0.02 | 1 | 1
COM-CT-WH-534-08 | Current | Updated size descriptions in eTRM to match TRM. Split New Construction and Natural Replacement to effectively represent baseline. Updated technology descriptions. Updated energy savings. | Commercial | Condensing Tankless Water Heater | High Utilization | New Construction | water heating | Condensing Tankless Water Heater - High Utilization | <200 kBtu/hr UEF >= 0.95 Stand-by Loss = negligible | Non-Condensing Storage Water Heater | Storage Water Heater 75 kBtu/hr. and greater Uniform Energy Factor (UEF)=0.8107-0.00021Vs | unit | kBtu/hr input capacity | TRM Version 8.0 | 2024-04-30 | 178 | 2.09 | 0 | 0 | 0 | 0 | 1030 | 0 | 20 | Midstream | 0.02 | 1 | 1
COM-CT-WH-534-09 | Current | Split New Construction and Natural Replacement to effectively represent baseline. Updated technology descriptions. Updated energy savings. | Commercial | Condensing Tankless Water Heater | High Utilization | New Construction | water heating | Condensing Tankless Water Heater - High Utilization | >=200 kBtu/hr Thermal efficiency >= 96% Stand-by Loss = negligible | Non-Condensing Storage Water Heater | Storage Water Heater 75 kBtu/hr. and greater Thermal efficiency = 90% Stand-by Loss 0.84(Q/800 +110√V0)Btu/hr | unit | kBtu/hr input capacity | TRM Version 8.0 | 2024-04-30 | 295 | 0.744 | 0 | 0 | 0 | 0 | 1030 | 0 | 20 | Midstream | 0.02 | 1 | 1
COM-CT-WH-534-10 | Current | Split New Construction and Natural Replacement to effectively represent baseline. Updated technology descriptions. Updated energy savings. | Commercial | Condensing Tankless Water Heater | High Utilization | New Construction | water heating | Condensing Tankless Water Heater - High Utilization | >=1000 < 2500 kBtu/hr Thermal efficiency >= 98% Stand-by Loss = negligible | Non-Condensing Storage Water Heater | Storage Water Heater 75 kBtu/hr. and greater Thermal efficiency = 80% Stand-by Loss Q/800 +110√V0 Btu/hr | unit | kBtu/hr input capacity | TRM Version 8.0 | 2024-04-30 | 438 | 0.992 | 0 | 0 | 0 | 0 | 1030 | 0 | 20 | Midstream | 0.02 | 1 | 1
COM-CT-WH-534-11 | Current | Split New Construction and Natural Replacement to effectively represent baseline. Updated technology descriptions. Updated energy savings. | Commercial | Condensing Tankless Water Heater | High Utilization | New Construction | water heating | Condensing Tankless Water Heater - High Utilization | >=2500 kBtu/hr Thermal efficiency >= 98% Stand-by Loss = negligible | Non-Condensing Storage Water Heater | Storage Water Heater 75 kBtu/hr. and greater Thermal efficiency = 80% Stand-by Loss Q/800 +110√V0 Btu/hr | unit | kBtu/hr input capacity | TRM Version 8.0 | 2024-04-30 | 728 | 0.992 | 0 | 0 | 0 | 0 | 1030 | 0 | 20 | Midstream | 0.02 | 1 | 1
COM-CT-WH-535-10 | Current | Updated size descriptions in eTRM to match TRM. Split New Construction and Natural Replacement to effectively represent baseline. Updated technology descriptions. Updated energy savings. | Commercial | Condensing Tankless Water Heater | Low Utilization | Natural Replacement | water heating | Condensing Tankless Water Heater - Low Utilization | <200 kBtu/hr UEF >= 0.90 Stand-by Loss = negligible | Non-Condensing Storage Water Heater | Storage Water Heater 75 kBtu/hr. and greater Uniform Energy Factor (UEF)=0.6597-0.00024Vs | unit | kBtu/hr input capacity | TRM Version 8.0 | 2024-04-30 | 212 | 1.918 | 0 | 0 | 0 | 0 | 3030 | 0 | 20 | Midstream | 0.02 | 1 | 1
COM-CT-WH-535-11 | Current | Split New Construction and Natural Replacement to effectively represent baseline. Updated technology descriptions. Updated energy savings. | Commercial | Condensing Tankless Water Heater | Low Utilization | Natural Replacement | water heating | Condensing Tankless Water Heater - Low Utilization | >=200 kBtu/hr Thermal efficiency >= 94% Stand-by Loss = negligible | Non-Condensing Storage Water Heater | Storage Water Heater 75 kBtu/hr. and greater Thermal efficiency = 80% Stand-by Loss Q/800 +110√V0 Btu/hr | unit | kBtu/hr input capacity | TRM Version 8.0 | 2024-04-30 | 351 | 0.862 | 0 | 0 | 0 | 0 | 3030 | 0 | 20 | Midstream | 0.02 | 1 | 1
COM-CT-WH-535-12 | Current | Updated size descriptions in eTRM to match TRM. Split New Construction and Natural Replacement to effectively represent baseline. Updated technology descriptions. Updated energy savings. | Commercial | Condensing Tankless Water Heater | Low Utilization | Natural Replacement | water heating | Condensing Tankless Water Heater - Low Utilization | <200 kBtu/hr UEF >= 0.95 Stand-by Loss = negligible | Non-Condensing Storage Water Heater | Storage Water Heater 75 kBtu/hr. and greater Uniform Energy Factor (UEF)=0.6597-0.00024Vs | unit | kBtu/hr input capacity | TRM Version 8.0 | 2024-04-30 | 212 | 2.299 | 0 | 0 | 0 | 0 | 3030 | 0 | 20 | Midstream | 0.02 | 1 | 1
COM-CT-WH-535-13 | Current | Split New Construction and Natural Replacement to effectively represent baseline. Updated technology descriptions. Updated energy savings. | Commercial | Condensing Tankless Water Heater | Low Utilization | Natural Replacement | water heating | Condensing Tankless Water Heater - Low Utilization | >=200 kBtu/hr Thermal efficiency >= 96% Stand-by Loss = negligible | Non-Condensing Storage Water Heater | Storage Water Heater 75 kBtu/hr. and greater Thermal efficiency = 80% Stand-by Loss Q/800 +110√V0 Btu/hr | unit | kBtu/hr input capacity | TRM Version 8.0 | 2024-04-30 | 521 | 0.985 | 0 | 0 | 0 | 0 | 3030 | 0 | 20 | Midstream | 0.02 | 1 | 1
COM-CT-WH-535-14 | Current | Split New Construction and Natural Replacement to effectively represent baseline. Updated technology descriptions. Updated energy savings. | Commercial | Condensing Tankless Water Heater | Low Utilization | Natural Replacement | water heating | Condensing Tankless Water Heater - Low Utilization | >=200 kBtu/hr Thermal efficiency >= 98% Stand-by Loss = negligible | Non-Condensing Storage Water Heater | Storage Water Heater 75 kBtu/hr. and greater Thermal efficiency = 80% Stand-by Loss Q/800 +110√V0 Btu/hr | unit | kBtu/hr input capacity | TRM Version 8.0 | 2024-04-30 | 867 | 1.108 | 0 | 0 | 0 | 0 | 3030 | 0 | 20 | Midstream | 0.02 | 1 | 1
COM-CT-WH-536-08 | Current | Updated size descriptions in eTRM to match TRM. Split New Construction and Natural Replacement to effectively represent baseline. Updated technology descriptions. Updated energy savings. | Commercial | Condensing Tankless Water Heater | Low Utilization | New Construction | water heating | Condensing Tankless Water Heater - Low Utilization | <200 kBtu/hr UEF >= 0.95 Stand-by Loss = negligible | Non-Condensing Storage Water Heater | Storage Water Heater 75 kBtu/hr. and greater Uniform Energy Factor (UEF)=0.8107-0.00021Vs | unit | kBtu/hr input capacity | TRM Version 8.0 | 2024-04-30 | 178 | 0.922 | 0 | 0 | 0 | 0 | 1030 | 0 | 20 | Midstream | 0.02 | 1 | 1
COM-CT-WH-536-09 | Current | Split New Construction and Natural Replacement to effectively represent baseline. Updated technology descriptions. Updated energy savings. | Commercial | Condensing Tankless Water Heater | Low Utilization | New Construction | water heating | Condensing Tankless Water Heater - Low Utilization | >=200 kBtu/hr Thermal efficiency >= 96% Stand-by Loss = negligible | Non-Condensing Storage Water Heater | Storage Water Heater 75 kBtu/hr. and greater Thermal efficiency = 90% Stand-by Loss 0.84(Q/800 +110√V0)Btu/hr | unit | kBtu/hr input capacity | TRM Version 8.0 | 2024-04-30 | 295 | 0.328 | 0 | 0 | 0 | 0 | 1030 | 0 | 20 | Midstream | 0.02 | 1 | 1
COM-CT-WH-536-10 | Current | Split New Construction and Natural Replacement to effectively represent baseline. Updated technology descriptions. Updated energy savings. | Commercial | Condensing Tankless Water Heater | Low Utilization | New Construction | water heating | Condensing Tankless Water Heater - Low Utilization | >=1000 < 2500 kBtu/hr Thermal efficiency >= 98% Stand-by Loss = negligible | Non-Condensing Storage Water Heater | Storage Water Heater 75 kBtu/hr. and greater Thermal efficiency = 80% Stand-by Loss Q/800 +110√V0 Btu/hr | unit | kBtu/hr input capacity | TRM Version 8.0 | 2024-04-30 | 438 | 0.438 | 0 | 0 | 0 | 0 | 1030 | 0 | 20 | Midstream | 0.02 | 1 | 1
COM-CT-WH-536-11 | Current | Split New Construction and Natural Replacement to effectively represent baseline. Updated technology descriptions. Updated energy savings. | Commercial | Condensing Tankless Water Heater | Low Utilization | New Construction | water heating | Condensing Tankless Water Heater - Low Utilization | >=2500 kBtu/hr Thermal efficiency >= 98% Stand-by Loss = negligible | Non-Condensing Storage Water Heater | Storage Water Heater 75 kBtu/hr. and greater Thermal efficiency = 80% Stand-by Loss Q/800 +110√V0 Btu/hr | unit | kBtu/hr input capacity | TRM Version 8.0 | 2024-04-30 | 728 | 0.438 | 0 | 0 | 0 | 0 | 1030 | 0 | 20 | Midstream | 0.02 | 1 | 1
COM-CT-WH-537-10 | Current | Updated size descriptions in eTRM to match TRM. Split New Construction and Natural Replacement to effectively represent baseline. Updated technology descriptions. Updated energy savings. | Commercial | Condensing Tankless Water Heater | Medium Utilization | Natural Replacement | water heating | Condensing Tankless Water Heater - Medium Utilization | <200 kBtu/hr UEF >= 0.90 Stand-by Loss = negligible | Non-Condensing Storage Water Heater | Storage Water Heater 75 kBtu/hr. and greater Uniform Energy Factor (UEF)=0.6597-0.00024Vs | unit | kBtu/hr input capacity | TRM Version 8.0 | 2024-04-30 | 212 | 3.128 | 0 | 0 | 0 | 0 | 3030 | 0 | 20 | Midstream | 0.02 | 1 | 1
COM-CT-WH-537-11 | Current | Split New Construction and Natural Replacement to effectively represent baseline. Updated technology descriptions. Updated energy savings. | Commercial | Condensing Tankless Water Heater | Medium Utilization | Natural Replacement | water heating | Condensing Tankless Water Heater - Medium Utilization | >=200 kBtu/hr Thermal efficiency >= 94% Stand-by Loss = negligible | Non-Condensing Storage Water Heater | Storage Water Heater 75 kBtu/hr. and greater Thermal efficiency = 80% Stand-by Loss Q/800 +110√V0 Btu/hr | unit | kBtu/hr input capacity | TRM Version 8.0 | 2024-04-30 | 351 | 1.405 | 0 | 0 | 0 | 0 | 3030 | 0 | 20 | Midstream | 0.02 | 1 | 1
COM-CT-WH-537-12 | Current | Updated size descriptions in eTRM to match TRM. Split New Construction and Natural Replacement to effectively represent baseline. Updated technology descriptions. Updated energy savings. | Commercial | Condensing Tankless Water Heater | Medium Utilization | Natural Replacement | water heating | Condensing Tankless Water Heater - Medium Utilization | <200 kBtu/hr UEF >= 0.95 Stand-by Loss = negligible | Non-Condensing Storage Water Heater | Storage Water Heater 75 kBtu/hr. and greater Uniform Energy Factor (UEF)=0.6597-0.00024Vs | unit | kBtu/hr input capacity | TRM Version 8.0 | 2024-04-30 | 212 | 3.748 | 0 | 0 | 0 | 0 | 3030 | 0 | 20 | Midstream | 0.02 | 1 | 1
COM-CT-WH-537-13 | Current | Split New Construction and Natural Replacement to effectively represent baseline. Updated technology descriptions. Updated energy savings. | Commercial | Condensing Tankless Water Heater | Medium Utilization | Natural Replacement | water heating | Condensing Tankless Water Heater - Medium Utilization | >=200 kBtu/hr Thermal efficiency >= 96% Stand-by Loss = negligible | Non-Condensing Storage Water Heater | Storage Water Heater 75 kBtu/hr. and greater Thermal efficiency = 80% Stand-by Loss Q/800 +110√V0 Btu/hr | unit | kBtu/hr input capacity | TRM Version 8.0 | 2024-04-30 | 521 | 1.606 | 0 | 0 | 0 | 0 | 3030 | 0 | 20 | Midstream | 0.02 | 1 | 1
COM-CT-WH-537-14 | Current | Split New Construction and Natural Replacement to effectively represent baseline. Updated technology descriptions. Updated energy savings. | Commercial | Condensing Tankless Water Heater | Medium Utilization | Natural Replacement | water heating | Condensing Tankless Water Heater - Medium Utilization | >=200 kBtu/hr Thermal efficiency >= 98% Stand-by Loss = negligible | Non-Condensing Storage Water Heater | Storage Water Heater 75 kBtu/hr. and greater Thermal efficiency = 80% Stand-by Loss Q/800 +110√V0 Btu/hr | unit | kBtu/hr input capacity | TRM Version 8.0 | 2024-04-30 | 867 | 1.807 | 0 | 0 | 0 | 0 | 3030 | 0 | 20 | Midstream | 0.02 | 1 | 1
COM-CT-WH-538-08 | Current | Updated size descriptions in eTRM to match TRM. Split New Construction and Natural Replacement to effectively represent baseline. Updated technology descriptions. Updated energy savings. | Commercial | Condensing Tankless Water Heater | Medium Utilization | New Construction | water heating | Condensing Tankless Water Heater - Medium Utilization | <200 kBtu/hr UEF >= 0.95 Stand-by Loss = negligible | Non-Condensing Storage Water Heater | Storage Water Heater 75 kBtu/hr. and greater Uniform Energy Factor (UEF)=0.8107-0.00021Vs | unit | kBtu/hr input capacity | TRM Version 8.0 | 2024-04-30 | 178 | 1.503 | 0 | 0 | 0 | 0 | 1030 | 0 | 20 | Midstream | 0.02 | 1 | 1
COM-CT-WH-538-09 | Current | Split New Construction and Natural Replacement to effectively represent baseline. Updated technology descriptions. Updated energy savings. | Commercial | Condensing Tankless Water Heater | Medium Utilization | New Construction | water heating | Condensing Tankless Water Heater - Medium Utilization | >=200 kBtu/hr Thermal efficiency >= 96% Stand-by Loss = negligible | Non-Condensing Storage Water Heater | Storage Water Heater 75 kBtu/hr. and greater Thermal efficiency = 90% Stand-by Loss 0.84(Q/800 +110√V0)Btu/hr | unit | kBtu/hr input capacity | TRM Version 8.0 | 2024-04-30 | 295 | 0.535 | 0 | 0 | 0 | 0 | 1030 | 0 | 20 | Midstream | 0.02 | 1 | 1
COM-CT-WH-538-10 | Current | Split New Construction and Natural Replacement to effectively represent baseline. Updated technology descriptions. Updated energy savings. | Commercial | Condensing Tankless Water Heater | Medium Utilization | New Construction | water heating | Condensing Tankless Water Heater - Medium Utilization | >=1000 < 2500 kBtu/hr Thermal efficiency >= 98% Stand-by Loss = negligible | Non-Condensing Storage Water Heater | Storage Water Heater 75 kBtu/hr. and greater Thermal efficiency = 80% Stand-by Loss Q/800 +110√V0 Btu/hr | unit | kBtu/hr input capacity | TRM Version 8.0 | 2024-04-30 | 438 | 0.714 | 0 | 0 | 0 | 0 | 1030 | 0 | 20 | Midstream | 0.02 | 1 | 1
COM-CT-WH-538-11 | Current | Split New Construction and Natural Replacement to effectively represent baseline. Updated technology descriptions. Updated energy savings. | Commercial | Condensing Tankless Water Heater | Medium Utilization | New Construction | water heating | Condensing Tankless Water Heater - Medium Utilization | >=2500 kBtu/hr Thermal efficiency >= 98% Stand-by Loss = negligible | Non-Condensing Storage Water Heater | Storage Water Heater 75 kBtu/hr. and greater Thermal efficiency = 80% Stand-by Loss Q/800 +110√V0 Btu/hr | unit | kBtu/hr input capacity | TRM Version 8.0 | 2024-04-30 | 728 | 0.714 | 0 | 0 | 0 | 0 | 1030 | 0 | 20 | Midstream | 0.02 | 1 | 1
COM-CS-WH-527-16 | Current | Split New Construction and Natural Replacement to effectively represent baseline and efficient efficiencies. Updated savings. | Commercial | Condensing Storage Water Heater | High Utilization | Natural Replacement | water heating | Condensing storage water heater | > 75 kBTU/hr and <= 105 kBTU/hr, rated nominal volume <= 120 US gallon, single-phase power, water temp <180 deg f, UEF >= 0.86 < 0.89 | Non-condensing storage water heater | > 75 kBTU/hr and <= 105 kBTU/hr, rated nominal volume <= 120 US gallon, single-phase power, water temp <180 deg f, UEF = 0.6597 - 0.00024Vs |  | kBtu/hr input capacity | TRM Version 8.0 | 2024-04-30 | 0 | 5.699 | 0 | 0 | 0 | 0 | 2591 | 0 | 15 | Midstream | 0.05 | 1 | 1
COM-CS-WH-527-17 | Current | Split New Construction and Natural Replacement to effectively represent baseline and efficient efficiencies. Updated savings. | Commercial | Condensing Storage Water Heater | High Utilization | Natural Replacement | water heating | Condensing storage water heater | > 75 kBTU/hr and <= 105 kBTU/hr, rated nominal volume <= 120 US gallon, single-phase power, water temp <180 deg f, UEF >= 0.89 | Non-condensing storage water heater | > 75 kBTU/hr and <= 105 kBTU/hr, rated nominal volume <= 120 US gallon, single-phase power, water temp <180 deg f, UEF = 0.6597 - 0.00024Vs |  | kBtu/hr input capacity | TRM Version 8.0 | 2024-04-30 | 0 | 6.497 | 0 | 0 | 0 | 0 | 2591 | 0 | 15 | Midstream | 0.05 | 1 | 1
COM-CS-WH-527-18 | Current | Split New Construction and Natural Replacement to effectively represent baseline and efficient efficiencies. Updated savings. | Commercial | Condensing Storage Water Heater | High Utilization | Natural Replacement | water heating | Condensing storage water heater | All water heaters not described by UEF baseline definition with thermal efficiency >= 92% < 95%, <= 250 kBTU/hr | Non-condensing storage water heater | All water heaters not described by UEF baseline definition with thermal efficiency >= 80% |  | kBtu/hr input capacity | TRM Version 8.0 | 2024-04-30 | 0 | 2.577 | 0 | 0 | 0 | 0 | 2591 | 0 | 15 | Midstream | 0.05 | 1 | 1
COM-CS-WH-527-19 | Current | Split New Construction and Natural Replacement to effectively represent baseline and efficient efficiencies. Updated savings. | Commercial | Condensing Storage Water Heater | High Utilization | Natural Replacement | water heating | Condensing storage water heater | All water heaters not described by UEF baseline definition with thermal efficiency >= 95% < 97%, <= 250 kBTU/hr | Non-condensing storage water heater | All water heaters not described by UEF baseline definition with thermal efficiency >= 80% |  | kBtu/hr input capacity | TRM Version 8.0 | 2024-04-30 | 0 | 3.221 | 0 | 0 | 0 | 0 | 2591 | 0 | 15 | Midstream | 0.05 | 1 | 1
COM-CS-WH-527-20 | Current | Split New Construction and Natural Replacement to effectively represent baseline and efficient efficiencies. Updated savings. | Commercial | Condensing Storage Water Heater | High Utilization | Natural Replacement | water heating | Condensing storage water heater | All water heaters not described by UEF baseline definition with thermal efficiency >= 97%, <= 250 kBTU/hr | Non-condensing storage water heater | All water heaters not described by UEF baseline definition with thermal efficiency >= 80% |  | kBtu/hr input capacity | TRM Version 8.0 | 2024-04-30 | 0 | 3.651 | 0 | 0 | 0 | 0 | 2591 | 0 | 15 | Midstream | 0.05 | 1 | 1
COM-CS-WH-527-21 | Current | Split New Construction and Natural Replacement to effectively represent baseline and efficient efficiencies. Updated savings. | Commercial | Condensing Storage Water Heater | High Utilization | Natural Replacement | water heating | Condensing storage water heater | All water heaters not described by UEF baseline definition with thermal efficiency >= 92% < 95%, > 250 kBTU/hr | Non-condensing storage water heater | All water heaters not described by UEF baseline definition with thermal efficiency >= 80% |  | kBtu/hr input capacity | TRM Version 8.0 | 2024-04-30 | 0 | 2.577 | 0 | 0 | 0 | 0 | 4464 | 0 | 15 | Midstream | 0.05 | 1 | 1
COM-CS-WH-527-22 | Current | Split New Construction and Natural Replacement to effectively represent baseline and efficient efficiencies. Updated savings. | Commercial | Condensing Storage Water Heater | High Utilization | Natural Replacement | water heating | Condensing storage water heater | All water heaters not described by UEF baseline definition with thermal efficiency >= 95% < 97%, > 250 kBTU/hr | Non-condensing storage water heater | All water heaters not described by UEF baseline definition with thermal efficiency >= 80% |  | kBtu/hr input capacity | TRM Version 8.0 | 2024-04-30 | 0 | 3.221 | 0 | 0 | 0 | 0 | 4464 | 0 | 15 | Midstream | 0.05 | 1 | 1
COM-CS-WH-527-23 | Current | Split New Construction and Natural Replacement to effectively represent baseline and efficient efficiencies. Updated savings. | Commercial | Condensing Storage Water Heater | High Utilization | Natural Replacement | water heating | Condensing storage water heater | All water heaters not described by UEF baseline definition with thermal efficiency >= 97%, > 250 kBTU/hr | Non-condensing storage water heater | All water heaters not described by UEF baseline definition with thermal efficiency >= 80% |  | kBtu/hr input capacity | TRM Version 8.0 | 2024-04-30 | 0 | 3.651 | 0 | 0 | 0 | 0 | 4464 | 0 | 15 | Midstream | 0.05 | 1 | 1
COM-CS-WH-528-12 | Current | Split New Construction and Natural Replacement to effectively represent baseline and efficient efficiencies. Updated savings. | Commercial | Condensing Storage Water Heater | High Utilization | New Construction | water heating | Condensing storage water heater | > 75 kBTU/hr and <= 105 kBTU/hr, rated nominal volume <= 120 US gallon, single-phase power, water temp <180 deg f, UEF >= 0.86 < 0.89 | Non-condensing storage water heater | > 75 kBTU/hr and <= 105 kBTU/hr, rated nominal volume <= 120 US gallon, single-phase power, water temp <180 deg f, UEF = 0.8107 - 0.00021Vs |  | kBtu/hr input capacity | TRM Version 8.0 | 2024-04-30 | 0 | 1.323 | 0 | 0 | 0 | 0 | 2591 | 0 | 15 | Midstream | 0.05 | 1 | 1
COM-CS-WH-528-13 | Current | Split New Construction and Natural Replacement to effectively represent baseline and efficient efficiencies. Updated savings. | Commercial | Condensing Storage Water Heater | High Utilization | New Construction | water heating | Condensing storage water heater | > 75 kBTU/hr and <= 105 kBTU/hr, rated nominal volume <= 120 US gallon, single-phase power, water temp <180 deg f, UEF >= 0.89 | Non-condensing storage water heater | > 75 kBTU/hr and <= 105 kBTU/hr, rated nominal volume <= 120 US gallon, single-phase power, water temp <180 deg f, UEF = 0.8107 - 0.00021Vs |  | kBtu/hr input capacity | TRM Version 8.0 | 2024-04-30 | 0 | 1.968 | 0 | 0 | 0 | 0 | 2591 | 0 | 15 | Midstream | 0.05 | 1 | 1
COM-CS-WH-528-14 | Current | Split New Construction and Natural Replacement to effectively represent baseline and efficient efficiencies. Updated savings. | Commercial | Condensing Storage Water Heater | High Utilization | New Construction | water heating | Condensing storage water heater | All water heaters not described by UEF baseline definition with thermal efficiency >= 95 < 97%, <= 250 kBTU/hr | Non-condensing storage water heater | All water heaters not described by UEF baseline definition with thermal efficiency = 90% |  | kBtu/hr input capacity | TRM Version 8.0 | 2024-04-30 | 0 | 0.954 | 0 | 0 | 0 | 0 | 2591 | 0 | 15 | Midstream | 0.05 | 1 | 1
COM-CS-WH-528-15 | Current | Split New Construction and Natural Replacement to effectively represent baseline and efficient efficiencies. Updated savings. | Commercial | Condensing Storage Water Heater | High Utilization | New Construction | water heating | Condensing storage water heater | All water heaters not described by UEF baseline definition with thermal efficiency >= 97%, <= 250 kBTU/hr | Non-condensing storage water heater | All water heaters not described by UEF baseline definition with thermal efficiency = 90% |  | kBtu/hr input capacity | TRM Version 8.0 | 2024-04-30 | 0 | 1.336 | 0 | 0 | 0 | 0 | 2591 | 0 | 15 | Midstream | 0.05 | 1 | 1
COM-CS-WH-528-16 | Current | Split New Construction and Natural Replacement to effectively represent baseline and efficient efficiencies. Updated savings. | Commercial | Condensing Storage Water Heater | High Utilization | New Construction | water heating | Condensing storage water heater | All water heaters not described by UEF baseline definition with thermal efficiency >= 95 < 97%, > 250 kBTU/hr | Non-condensing storage water heater | All water heaters not described by UEF baseline definition with thermal efficiency = 90% |  | kBtu/hr input capacity | TRM Version 8.0 | 2024-04-30 | 0 | 0.954 | 0 | 0 | 0 | 0 | 4464 | 0 | 15 | Midstream | 0.05 | 1 | 1
COM-CS-WH-528-17 | Current | Split New Construction and Natural Replacement to effectively represent baseline and efficient efficiencies. Updated savings. | Commercial | Condensing Storage Water Heater | High Utilization | New Construction | water heating | Condensing storage water heater | All water heaters not described by UEF baseline definition with thermal efficiency >= 97%, > 250 kBTU/hr | Non-condensing storage water heater | All water heaters not described by UEF baseline definition with thermal efficiency = 90% |  | kBtu/hr input capacity | TRM Version 8.0 | 2024-04-30 | 0 | 1.336 | 0 | 0 | 0 | 0 | 4464 | 0 | 15 | Midstream | 0.05 | 1 | 1
COM-CS-WH-529-16 | Current | Split New Construction and Natural Replacement to effectively represent baseline and efficient efficiencies. Updated savings. | Commercial | Condensing Storage Water Heater | Low Utilization | Natural Replacement | water heating | Condensing storage water heater | > 75 kBTU/hr and <= 105 kBTU/hr, rated nominal volume <= 120 US gallon, single-phase power, water temp <180 deg f, UEF >= 0.86 < 0.89 | Non-condensing storage water heater | > 75 kBTU/hr and <= 105 kBTU/hr, rated nominal volume <= 120 US gallon, single-phase power, water temp <180 deg f, UEF = 0.6597 - 0.00024Vs |  | kBtu/hr input capacity | TRM Version 8.0 | 2024-04-30 | 0 | 2.515 | 0 | 0 | 0 | 0 | 2591 | 0 | 15 | Midstream | 0.05 | 1 | 1
COM-CS-WH-529-17 | Current | Split New Construction and Natural Replacement to effectively represent baseline and efficient efficiencies. Updated savings. | Commercial | Condensing Storage Water Heater | Low Utilization | Natural Replacement | water heating | Condensing storage water heater | > 75 kBTU/hr and <= 105 kBTU/hr, rated nominal volume <= 120 US gallon, single-phase power, water temp <180 deg f, UEF >= 0.89 | Non-condensing storage water heater | > 75 kBTU/hr and <= 105 kBTU/hr, rated nominal volume <= 120 US gallon, single-phase power, water temp <180 deg f, UEF = 0.6597 - 0.00024Vs |  | kBtu/hr input capacity | TRM Version 8.0 | 2024-04-30 | 0 | 2.868 | 0 | 0 | 0 | 0 | 2591 | 0 | 15 | Midstream | 0.05 | 1 | 1
COM-CS-WH-529-18 | Current | Split New Construction and Natural Replacement to effectively represent baseline and efficient efficiencies. Updated savings. | Commercial | Condensing Storage Water Heater | Low Utilization | Natural Replacement | water heating | Condensing storage water heater | All water heaters not described by UEF baseline definition with thermal efficiency >= 92% < 95%, <= 250 kBTU/hr | Non-condensing storage water heater | All water heaters not described by UEF baseline definition with thermal efficiency >= 80% |  | kBtu/hr input capacity | TRM Version 8.0 | 2024-04-30 | 0 | 1.137 | 0 | 0 | 0 | 0 | 2591 | 0 | 15 | Midstream | 0.05 | 1 | 1
COM-CS-WH-529-19 | Current | Split New Construction and Natural Replacement to effectively represent baseline and efficient efficiencies. Updated savings. | Commercial | Condensing Storage Water Heater | Low Utilization | Natural Replacement | water heating | Condensing storage water heater | All water heaters not described by UEF baseline definition with thermal efficiency >= 95% < 97%, <= 250 kBTU/hr | Non-condensing storage water heater | All water heaters not described by UEF baseline definition with thermal efficiency >= 80% |  | kBtu/hr input capacity | TRM Version 8.0 | 2024-04-30 | 0 | 1.422 | 0 | 0 | 0 | 0 | 2591 | 0 | 15 | Midstream | 0.05 | 1 | 1
COM-CS-WH-529-20 | Current | Split New Construction and Natural Replacement to effectively represent baseline and efficient efficiencies. Updated savings. | Commercial | Condensing Storage Water Heater | Low Utilization | Natural Replacement | water heating | Condensing storage water heater | All water heaters not described by UEF baseline definition with thermal efficiency >= 97%, <= 250 kBTU/hr | Non-condensing storage water heater | All water heaters not described by UEF baseline definition with thermal efficiency >= 80% |  | kBtu/hr input capacity | TRM Version 8.0 | 2024-04-30 | 0 | 1.611 | 0 | 0 | 0 | 0 | 2591 | 0 | 15 | Midstream | 0.05 | 1 | 1
COM-CS-WH-529-21 | Current | Split New Construction and Natural Replacement to effectively represent baseline and efficient efficiencies. Updated savings. | Commercial | Condensing Storage Water Heater | Low Utilization | Natural Replacement | water heating | Condensing storage water heater | All water heaters not described by UEF baseline definition with thermal efficiency >= 92% < 95%, > 250 kBTU/hr | Non-condensing storage water heater | All water heaters not described by UEF baseline definition with thermal efficiency >= 80% |  | kBtu/hr input capacity | TRM Version 8.0 | 2024-04-30 | 0 | 1.137 | 0 | 0 | 0 | 0 | 4464 | 0 | 15 | Midstream | 0.05 | 1 | 1
COM-CS-WH-529-22 | Current | Split New Construction and Natural Replacement to effectively represent baseline and efficient efficiencies. Updated savings. | Commercial | Condensing Storage Water Heater | Low Utilization | Natural Replacement | water heating | Condensing storage water heater | All water heaters not described by UEF baseline definition with thermal efficiency >= 95% < 97%, > 250 kBTU/hr | Non-condensing storage water heater | All water heaters not described by UEF baseline definition with thermal efficiency >= 80% |  | kBtu/hr input capacity | TRM Version 8.0 | 2024-04-30 | 0 | 1.422 | 0 | 0 | 0 | 0 | 4464 | 0 | 15 | Midstream | 0.05 | 1 | 1
COM-CS-WH-529-23 | Current | Split New Construction and Natural Replacement to effectively represent baseline and efficient efficiencies. Updated savings. | Commercial | Condensing Storage Water Heater | Low Utilization | Natural Replacement | water heating | Condensing storage water heater | All water heaters not described by UEF baseline definition with thermal efficiency >= 97%, > 250 kBTU/hr | Non-condensing storage water heater | All water heaters not described by UEF baseline definition with thermal efficiency >= 80% |  | kBtu/hr input capacity | TRM Version 8.0 | 2024-04-30 | 0 | 1.611 | 0 | 0 | 0 | 0 | 4464 | 0 | 15 | Midstream | 0.05 | 1 | 1
COM-CS-WH-530-12 | Current | Split New Construction and Natural Replacement to effectively represent baseline and efficient efficiencies. Updated savings. | Commercial | Condensing Storage Water Heater | Low Utilization | New Construction | water heating | Condensing storage water heater | > 75 kBTU/hr and <= 105 kBTU/hr, rated nominal volume <= 120 US gallon, single-phase power, water temp <180 deg f, UEF >= 0.86 < 0.89 | Non-condensing storage water heater | > 75 kBTU/hr and <= 105 kBTU/hr, rated nominal volume <= 120 US gallon, single-phase power, water temp <180 deg f, UEF = 0.8107 - 0.00021Vs |  | kBtu/hr input capacity | TRM Version 8.0 | 2024-04-30 | 0 | 0.584 | 0 | 0 | 0 | 0 | 2591 | 0 | 15 | Midstream | 0.05 | 1 | 1
COM-CS-WH-530-13 | Current | Split New Construction and Natural Replacement to effectively represent baseline and efficient efficiencies. Updated savings. | Commercial | Condensing Storage Water Heater | Low Utilization | New Construction | water heating | Condensing storage water heater | > 75 kBTU/hr and <= 105 kBTU/hr, rated nominal volume <= 120 US gallon, single-phase power, water temp <180 deg f, UEF >= 0.89 | Non-condensing storage water heater | > 75 kBTU/hr and <= 105 kBTU/hr, rated nominal volume <= 120 US gallon, single-phase power, water temp <180 deg f, UEF = 0.8107 - 0.00021Vs |  | kBtu/hr input capacity | TRM Version 8.0 | 2024-04-30 | 0 | 0.869 | 0 | 0 | 0 | 0 | 2591 | 0 | 15 | Midstream | 0.05 | 1 | 1
COM-CS-WH-530-14 | Current | Split New Construction and Natural Replacement to effectively represent baseline and efficient efficiencies. Updated savings. | Commercial | Condensing Storage Water Heater | Low Utilization | New Construction | water heating | Condensing storage water heater | All water heaters not described by UEF baseline definition with thermal efficiency >= 95 < 97%, <= 250 kBTU/hr | Non-condensing storage water heater | All water heaters not described by UEF baseline definition with thermal efficiency = 90% |  | kBtu/hr input capacity | TRM Version 8.0 | 2024-04-30 | 0 | 0.421 | 0 | 0 | 0 | 0 | 2591 | 0 | 15 | Midstream | 0.05 | 1 | 1
COM-CS-WH-530-15 | Current | Split New Construction and Natural Replacement to effectively represent baseline and efficient efficiencies. Updated savings. | Commercial | Condensing Storage Water Heater | Low Utilization | New Construction | water heating | Condensing storage water heater | All water heaters not described by UEF baseline definition with thermal efficiency >= 97%, <= 250 kBTU/hr | Non-condensing storage water heater | All water heaters not described by UEF baseline definition with thermal efficiency = 90% |  | kBtu/hr input capacity | TRM Version 8.0 | 2024-04-30 | 0 | 0.59 | 0 | 0 | 0 | 0 | 2591 | 0 | 15 | Midstream | 0.05 | 1 | 1
COM-CS-WH-530-16 | Current | Split New Construction and Natural Replacement to effectively represent baseline and efficient efficiencies. Updated savings. | Commercial | Condensing Storage Water Heater | Low Utilization | New Construction | water heating | Condensing storage water heater | All water heaters not described by UEF baseline definition with thermal efficiency >= 95 < 97%, > 250 kBTU/hr | Non-condensing storage water heater | All water heaters not described by UEF baseline definition with thermal efficiency = 90% |  | kBtu/hr input capacity | TRM Version 8.0 | 2024-04-30 | 0 | 0.421 | 0 | 0 | 0 | 0 | 4464 | 0 | 15 | Midstream | 0.05 | 1 | 1
COM-CS-WH-530-17 | Current | Split New Construction and Natural Replacement to effectively represent baseline and efficient efficiencies. Updated savings. | Commercial | Condensing Storage Water Heater | Low Utilization | New Construction | water heating | Condensing storage water heater | All water heaters not described by UEF baseline definition with thermal efficiency >= 97%, > 250 kBTU/hr | Non-condensing storage water heater | All water heaters not described by UEF baseline definition with thermal efficiency = 90% |  | kBtu/hr input capacity | TRM Version 8.0 | 2024-04-30 | 0 | 0.59 | 0 | 0 | 0 | 0 | 4464 | 0 | 15 | Midstream | 0.05 | 1 | 1
COM-CS-WH-531-16 | Current | Split New Construction and Natural Replacement to effectively represent baseline and efficient efficiencies. Updated savings. | Commercial | Condensing Storage Water Heater | Medium Utilization | Natural Replacement | water heating | Condensing storage water heater | > 75 kBTU/hr and <= 105 kBTU/hr, rated nominal volume <= 120 US gallon, single-phase power, water temp <180 deg f, UEF >= 0.86 < 0.89 | Non-condensing storage water heater | > 75 kBTU/hr and <= 105 kBTU/hr, rated nominal volume <= 120 US gallon, single-phase power, water temp <180 deg f, UEF = 0.6597 - 0.00024Vs |  | kBtu/hr input capacity | TRM Version 8.0 | 2024-04-30 | 0 | 4.103 | 0 | 0 | 0 | 0 | 2591 | 0 | 15 | Midstream | 0.05 | 1 | 1
COM-CS-WH-531-17 | Current | Split New Construction and Natural Replacement to effectively represent baseline and efficient efficiencies. Updated savings. | Commercial | Condensing Storage Water Heater | Medium Utilization | Natural Replacement | water heating | Condensing storage water heater | > 75 kBTU/hr and <= 105 kBTU/hr, rated nominal volume <= 120 US gallon, single-phase power, water temp <180 deg f, UEF >= 0.89 | Non-condensing storage water heater | > 75 kBTU/hr and <= 105 kBTU/hr, rated nominal volume <= 120 US gallon, single-phase power, water temp <180 deg f, UEF = 0.6597 - 0.00024Vs |  | kBtu/hr input capacity | TRM Version 8.0 | 2024-04-30 | 0 | 4.677 | 0 | 0 | 0 | 0 | 2591 | 0 | 15 | Midstream | 0.05 | 1 | 1
COM-CS-WH-531-18 | Current | Split New Construction and Natural Replacement to effectively represent baseline and efficient efficiencies. Updated savings. | Commercial | Condensing Storage Water Heater | Medium Utilization | Natural Replacement | water heating | Condensing storage water heater | All water heaters not described by UEF baseline definition with thermal efficiency >= 92% < 95%, <= 250 kBTU/hr | Non-condensing storage water heater | All water heaters not described by UEF baseline definition with thermal efficiency >= 80% |  | kBtu/hr input capacity | TRM Version 8.0 | 2024-04-30 | 0 | 1.855 | 0 | 0 | 0 | 0 | 2591 | 0 | 15 | Midstream | 0.05 | 1 | 1
COM-CS-WH-531-19 | Current | Split New Construction and Natural Replacement to effectively represent baseline and efficient efficiencies. Updated savings. | Commercial | Condensing Storage Water Heater | Medium Utilization | Natural Replacement | water heating | Condensing storage water heater | All water heaters not described by UEF baseline definition with thermal efficiency >= 95% < 97%, <= 250 kBTU/hr | Non-condensing storage water heater | All water heaters not described by UEF baseline definition with thermal efficiency >= 80% |  | kBtu/hr input capacity | TRM Version 8.0 | 2024-04-30 | 0 | 2.319 | 0 | 0 | 0 | 0 | 2591 | 0 | 15 | Midstream | 0.05 | 1 | 1
COM-CS-WH-531-20 | Current | Split New Construction and Natural Replacement to effectively represent baseline and efficient efficiencies. Updated savings. | Commercial | Condensing Storage Water Heater | Medium Utilization | Natural Replacement | water heating | Condensing storage water heater | All water heaters not described by UEF baseline definition with thermal efficiency >= 97%, <= 250 kBTU/hr | Non-condensing storage water heater | All water heaters not described by UEF baseline definition with thermal efficiency >= 80% |  | kBtu/hr input capacity | TRM Version 8.0 | 2024-04-30 | 0 | 2.628 | 0 | 0 | 0 | 0 | 2591 | 0 | 15 | Midstream | 0.05 | 1 | 1
COM-CS-WH-531-21 | Current | Split New Construction and Natural Replacement to effectively represent baseline and efficient efficiencies. Updated savings. | Commercial | Condensing Storage Water Heater | Medium Utilization | Natural Replacement | water heating | Condensing storage water heater | All water heaters not described by UEF baseline definition with thermal efficiency >= 92% < 95%, > 250 kBTU/hr | Non-condensing storage water heater | All water heaters not described by UEF baseline definition with thermal efficiency >= 80% |  | kBtu/hr input capacity | TRM Version 8.0 | 2024-04-30 | 0 | 1.855 | 0 | 0 | 0 | 0 | 4464 | 0 | 15 | Midstream | 0.05 | 1 | 1
COM-CS-WH-531-22 | Current | Split New Construction and Natural Replacement to effectively represent baseline and efficient efficiencies. Updated savings. | Commercial | Condensing Storage Water Heater | Medium Utilization | Natural Replacement | water heating | Condensing storage water heater | All water heaters not described by UEF baseline definition with thermal efficiency >= 95% < 97%, > 250 kBTU/hr | Non-condensing storage water heater | All water heaters not described by UEF baseline definition with thermal efficiency >= 80% |  | kBtu/hr input capacity | TRM Version 8.0 | 2024-04-30 | 0 | 2.319 | 0 | 0 | 0 | 0 | 4464 | 0 | 15 | Midstream | 0.05 | 1 | 1
COM-CS-WH-531-23 | Current | Split New Construction and Natural Replacement to effectively represent baseline and efficient efficiencies. Updated savings. | Commercial | Condensing Storage Water Heater | Medium Utilization | Natural Replacement | water heating | Condensing storage water heater | All water heaters not described by UEF baseline definition with thermal efficiency >= 97%, > 250 kBTU/hr | Non-condensing storage water heater | All water heaters not described by UEF baseline definition with thermal efficiency >= 80% |  | kBtu/hr input capacity | TRM Version 8.0 | 2024-04-30 | 0 | 2.628 | 0 | 0 | 0 | 0 | 4464 | 0 | 15 | Midstream | 0.05 | 1 | 1
COM-CS-WH-532-12 | Current | Split New Construction and Natural Replacement to effectively represent baseline and efficient efficiencies. Updated savings. | Commercial | Condensing Storage Water Heater | Medium Utilization | New Construction | water heating | Condensing storage water heater | > 75 kBTU/hr and <= 105 kBTU/hr, rated nominal volume <= 120 US gallon, single-phase power, water temp <180 deg f, UEF >= 0.86 < 0.89 | Non-condensing storage water heater | > 75 kBTU/hr and <= 105 kBTU/hr, rated nominal volume <= 120 US gallon, single-phase power, water temp <180 deg f, UEF = 0.8107 - 0.00021Vs |  | kBtu/hr input capacity | TRM Version 8.0 | 2024-04-30 | 0 | 0.952 | 0 | 0 | 0 | 0 | 2591 | 0 | 15 | Midstream | 0.05 | 1 | 1
COM-CS-WH-532-13 | Current | Split New Construction and Natural Replacement to effectively represent baseline and efficient efficiencies. Updated savings. | Commercial | Condensing Storage Water Heater | Medium Utilization | New Construction | water heating | Condensing storage water heater | > 75 kBTU/hr and <= 105 kBTU/hr, rated nominal volume <= 120 US gallon, single-phase power, water temp <180 deg f, UEF >= 0.89 | Non-condensing storage water heater | > 75 kBTU/hr and <= 105 kBTU/hr, rated nominal volume <= 120 US gallon, single-phase power, water temp <180 deg f, UEF = 0.8107 - 0.00021Vs |  | kBtu/hr input capacity | TRM Version 8.0 | 2024-04-30 | 0 | 1.417 | 0 | 0 | 0 | 0 | 2591 | 0 | 15 | Midstream | 0.05 | 1 | 1
COM-CS-WH-532-14 | Current | Split New Construction and Natural Replacement to effectively represent baseline and efficient efficiencies. Updated savings. | Commercial | Condensing Storage Water Heater | Medium Utilization | New Construction | water heating | Condensing storage water heater | All water heaters not described by UEF baseline definition with thermal efficiency >= 95 < 97%, <= 250 kBTU/hr | Non-condensing storage water heater | All water heaters not described by UEF baseline definition with thermal efficiency = 90% |  | kBtu/hr input capacity | TRM Version 8.0 | 2024-04-30 | 0 | 0.687 | 0 | 0 | 0 | 0 | 2591 | 0 | 15 | Midstream | 0.05 | 1 | 1
COM-CS-WH-532-15 | Current | Split New Construction and Natural Replacement to effectively represent baseline and efficient efficiencies. Updated savings. | Commercial | Condensing Storage Water Heater | Medium Utilization | New Construction | water heating | Condensing storage water heater | All water heaters not described by UEF baseline definition with thermal efficiency >= 97%, <= 250 kBTU/hr | Non-condensing storage water heater | All water heaters not described by UEF baseline definition with thermal efficiency = 90% |  | kBtu/hr input capacity | TRM Version 8.0 | 2024-04-30 | 0 | 0.962 | 0 | 0 | 0 | 0 | 2591 | 0 | 15 | Midstream | 0.05 | 1 | 1
COM-CS-WH-532-16 | Current | Split New Construction and Natural Replacement to effectively represent baseline and efficient efficiencies. Updated savings. | Commercial | Condensing Storage Water Heater | Medium Utilization | New Construction | water heating | Condensing storage water heater | All water heaters not described by UEF baseline definition with thermal efficiency >= 95 < 97%, > 250 kBTU/hr | Non-condensing storage water heater | All water heaters not described by UEF baseline definition with thermal efficiency = 90% |  | kBtu/hr input capacity | TRM Version 8.0 | 2024-04-30 | 0 | 0.687 | 0 | 0 | 0 | 0 | 4464 | 0 | 15 | Midstream | 0.05 | 1 | 1
COM-CS-WH-532-17 | Current | Split New Construction and Natural Replacement to effectively represent baseline and efficient efficiencies. Updated savings. | Commercial | Condensing Storage Water Heater | Medium Utilization | New Construction | water heating | Condensing storage water heater | All water heaters not described by UEF baseline definition with thermal efficiency >= 97%, > 250 kBTU/hr | Non-condensing storage water heater | All water heaters not described by UEF baseline definition with thermal efficiency = 90% |  | kBtu/hr input capacity | TRM Version 8.0 | 2024-04-30 | 0 | 0.962 | 0 | 0 | 0 | 0 | 4464 | 0 | 15 | Midstream | 0.05 | 1 | 1
RES-FA-WH-461-05 | Replaced | Updated in TRM Version 7.0 | Residential | Faucet Aerator |  | Retrofit | water heating | Faucet Aerator | Bathroom, 1.0 GPM | Standard flow bathroom aerator (code compliant) | 2.2 GPM | unit |  | TRM Version 5.0 | 2020-11-12 | 6.4 | 0 | 0 | 0 | 2501 | 0 | 0.6 | 0 | 10 | Direct Install | 0 | 1 | 1
RES-FA-WH-460-05 | Replaced | Updated in TRM Version 7.0 | Residential | Faucet Aerator |  | Retrofit | water heating | Faucet Aerator | Bathroom, 1.5 GPM | Standard flow bathroom aerator (code compliant) | 2.2 GPM | unit |  | TRM Version 5.0 | 2020-11-12 | 3.73 | 0 | 0 | 0 | 1459 | 0 | 0.6 | 0 | 10 | Direct Install | 0 | 1 | 1
RES-FA-WH-462-05 | Replaced | Updated in TRM Version 7.0 | Residential | Faucet Aerator |  | Retrofit | water heating | Faucet Aerator | Kitchen, 1.0 GPM | Standard flow kitchen aerator (code compliant) | 2.2 GPM | unit |  | TRM Version 5.0 | 2020-11-12 | 19.82 | 0 | 0 | 0 | 7742 | 0 | 1.14 | 0 | 10 | Direct Install | 0 | 1 | 1
RES-FA-WH-463-05 | Replaced | Updated in TRM Version 7.0 | Residential | Faucet Aerator |  | Retrofit | water heating | Faucet Aerator | Kitchen, 1.5 GPM | Standard flow kitchen aerator (code compliant) | 2.2 GPM | unit |  | TRM Version 5.0 | 2020-11-12 | 11.56 | 0 | 0 | 0 | 4516 | 0 | 1.14 | 0 | 10 | Direct Install | 0 | 1 | 1
RES-FA-WH-461-01 | Replaced | Updated in TRM Version 7.0 | Residential | Faucet Aerator |  | Retrofit | water heating | Faucet Aerator | Bathroom, 1.0 GPM | Standard flow bathroom aerator (code compliant) | 2.2 GPM | unit |  | TRM Version 5.0 | 2020-11-12 | 6.4 | 0 | 0 | 0 | 2501 | 0 | 0.6 | 0 | 10 | Downstream | 0.33 | 0.6458 | 1
RES-FA-WH-460-01 | Replaced | Updated in TRM Version 7.0 | Residential | Faucet Aerator |  | Retrofit | water heating | Faucet Aerator | Bathroom, 1.5 GPM | Standard flow bathroom aerator (code compliant) | 2.2 GPM | unit |  | TRM Version 5.0 | 2020-11-12 | 3.73 | 0 | 0 | 0 | 1459 | 0 | 0.6 | 0 | 10 | Downstream | 0.33 | 0.6458 | 1
RES-TW-WH-576-01 | Replaced | Updated in TRM Version 7.0 | Residential | Tankless Water Heater |  | New Construction/Natural Replacement | water heating | Tankless Water Heater | Condensing Tankless Water Heater, EF = 0.91 | Storage Tank Water Heater, EF=0.67 | EF=0.67 | unit |  | TRM Version 5.0 | 2020-11-12 | 128 | 0 | 0 | 0 | 0 | 0 | 2066 | 0 | 20 | Downstream | 0.02 | 1 | 1
RES-TW-WH-575-01 | Replaced | Updated in TRM Version 7.0 | Residential | Tankless Water Heater |  | New Construction/Natural Replacement | water heating | Tankless Water Heater | High Efficiency Non-Condensing Tankless Water Heater, EF = 0.82 | Storage Tank Water Heater, EF=0.67 | EF=0.67 | unit |  | TRM Version 5.0 | 2020-11-12 | 88.8 | 0 | 0 | 0 | 0 | 0 | 1667 | 0 | 20 | Downstream | 0.02 | 1 | 1
RES-SW-WH-574-01 | Replaced | Updated in TRM Version 7.0 | Residential | Storage Water Heater |  | New Construction | water heating | High Efficiency Gas Storage Water Heaters | High efficiency storage tank water heater (Energy Factor of 0.80) | ENERGY STAR power vented storage tank water heater | Energy factor of 0.67 | unit |  | TRM Version 5.0 | 2020-11-12 | 68.3 | 0 | 0 | 0 | 0 | 0 | 545 | 0 | 16 | Downstream | 0.1 | 1 | 1
RES-FA-WH-462-01 | Replaced | Updated in TRM Version 7.0 | Residential | Faucet Aerator |  | Retrofit | water heating | Faucet Aerator | Kitchen, 1.0 GPM | Standard flow kitchen aerator (code compliant) | 2.2 GPM | unit |  | TRM Version 5.0 | 2020-11-12 | 19.82 | 0 | 0 | 0 | 7742 | 0 | 1.14 | 0 | 10 | Downstream | 0.33 | 0.6768 | 1
RES-FA-WH-463-01 | Replaced | Updated in TRM Version 7.0 | Residential | Faucet Aerator |  | Retrofit | water heating | Faucet Aerator | Kitchen, 1.5 GPM | Standard flow kitchen aerator (code compliant) | 2.2 GPM | unit |  | TRM Version 5.0 | 2020-11-12 | 11.56 | 0 | 0 | 0 | 4516 | 0 | 1.14 | 0 | 10 | Downstream | 0.33 | 0.6768 | 1
RES-PW-WH-566-01 | Replaced | Updated in TRM Version 7.0 | Residential | Pipe Wrap |  | Retrofit | water heating | Pipe Wrap | R 4.35 | No pipe wrap | R-0.435 | ft |  | TRM Version 5.0 | 2020-11-12 | 3.64 | 0 | 0 | 0 | 0 | 0 | 0.39 | 0 | 15 | Downstream | 0.02 | 0.939 | 1
RES-FA-WH-461-03 | Replaced | Updated in TRM Version 7.0 | Residential | Faucet Aerator |  | Retrofit | water heating | Faucet Aerator | Bathroom, 1.0 GPM | Standard flow bathroom aerator (code compliant) | 2.2 GPM | unit |  | TRM Version 5.0 | 2020-11-12 | 6.4 | 0 | 0 | 0 | 2501 | 0 | 0.6 | 0 | 10 | Low-Income | 0 | 0.6458 | 1
RES-FA-WH-460-03 | Replaced | Updated in TRM Version 7.0 | Residential | Faucet Aerator |  | Retrofit | water heating | Faucet Aerator | Bathroom, 1.5 GPM | Standard flow bathroom aerator (code compliant) | 2.2 GPM | unit |  | TRM Version 5.0 | 2020-11-12 | 3.73 | 0 | 0 | 0 | 1459 | 0 | 0.6 | 0 | 10 | Low-Income | 0 | 0.6458 | 1
RES-TW-WH-576-02 | Replaced | Updated in TRM Version 7.0 | Residential | Tankless Water Heater |  | New Construction/Natural Replacement | water heating | Tankless Water Heater | Condensing Tankless Water Heater, EF = 0.91 | Storage Tank Water Heater, EF=0.67 | EF=0.67 | unit |  | TRM Version 5.0 | 2020-11-12 | 128 | 0 | 0 | 0 | 0 | 0 | 2066 | 0 | 20 | Low-Income | 0 | 1 | 1
RES-TW-WH-575-02 | Replaced | Updated in TRM Version 7.0 | Residential | Tankless Water Heater |  | New Construction/Natural Replacement | water heating | Tankless Water Heater | High Efficiency Non-Condensing Tankless Water Heater, EF = 0.82 | Storage Tank Water Heater, EF=0.67 | EF=0.67 | unit |  | TRM Version 5.0 | 2020-11-12 | 88.8 | 0 | 0 | 0 | 0 | 0 | 1667 | 0 | 20 | Low-Income | 0 | 1 | 1
RES-SW-WH-574-02 | Replaced | Updated in TRM Version 7.0 | Residential | Storage Water Heater |  | New Construction | water heating | High Efficiency Gas Storage Water Heaters | High efficiency storage tank water heater (Energy Factor of 0.80) | ENERGY STAR power vented storage tank water heater | Energy factor of 0.67 | unit |  | TRM Version 5.0 | 2020-11-12 | 44.1 | 0 | 0 | 0 | 0 | 0 | 545 | 0 | 16 | Low-Income | 0 | 1 | 1
RES-FA-WH-462-03 | Replaced | Updated in TRM Version 7.0 | Residential | Faucet Aerator |  | Retrofit | water heating | Faucet Aerator | Kitchen, 1.0 GPM | Standard flow kitchen aerator (code compliant) | 2.2 GPM | unit |  | TRM Version 5.0 | 2020-11-12 | 19.82 | 0 | 0 | 0 | 7742 | 0 | 1.14 | 0 | 10 | Low-Income | 0 | 0.6768 | 1
RES-FA-WH-463-03 | Replaced | Updated in TRM Version 7.0 | Residential | Faucet Aerator |  | Retrofit | water heating | Faucet Aerator | Kitchen, 1.5 GPM | Standard flow kitchen aerator (code compliant) | 2.2 GPM | unit |  | TRM Version 5.0 | 2020-11-12 | 11.56 | 0 | 0 | 0 | 4516 | 0 | 1.14 | 0 | 10 | Low-Income | 0 | 0.6768 | 1
RES-PW-WH-566-02 | Replaced | Updated in TRM Version 7.0 | Residential | Pipe Wrap |  | Retrofit | water heating | Pipe Wrap | R 4.35 | No pipe wrap | R-0.435 | ft |  | TRM Version 5.0 | 2020-11-12 | 3.64 | 0 | 0 | 0 | 0 | 0 | 0.39 | 0 | 15 | Low-Income | 0 | 0.939 | 1

## Measure Code
Sector | Code | Measure Group | Measure Group Code | End Use | Code | Measure Number | Status
Commercial | COM | Adaptive Thermostat | AT | food service | FS | No logic assigned to measure number. | Current
Multi-residential | MRS | Air Curtain | AC | space heating | SH | Just fit it in where you can. | Replaced
Residential | RES | Condensing Furnace | CF | water heating | WH |  | Retired
|  | Condensing Make Up Air Unit | CM
|  | Condensing Storage Water Heater | CS
|  | Condensing Tankless Water Heater | CT
|  | Condensing Unit Heater | CU
|  | Convection Ovens | CO
|  | Demand Control Kitchen Ventilation | DK
|  | Demand Control Ventilation | DCV
|  | Destratification Fans | DF
|  | Dishwasher | DW
|  | Dock Door Seals | DS
|  | Energy Recovery Ventilation | ERV
|  | Faucet Aerator | FA
|  | Fryer | FR
|  | Heat Recovery Ventialation | HRV
|  | Heat Reflector Panels | HP
|  | Infrared Heaters | IH
|  | Ozone Laundry | OL
|  | pipe wrap | PW
|  | Programmable Thermostat | PT
|  | Showerhead | SH
|  | Steam Cookers | SC
|  | Storage Water Heater | SW
|  | Tankless Water Heater | TW
|  | Under-Fired Broilers | UB
|  | Combination Oven | CMB
|  | Rack Oven | RO

## Sources
Source | Description
Joint Application for Approval of New and Updated Conservation Measures (EB-2014-0354) | prescriptive, direct install, and midstream net-to-gross values
2017 C&I Prescriptive Verification, Final Report - Measurement of NTG Factors and Gross Savings Verification, Itron, June 7, 2019 | net-to-gross and gross realization rate values for Commercial and Industrial Prescriptive program measures studies; measures studied include LEGD boilers, demand control kitchen ventilation, infrared heating, and demand control ventilation and LUG boilers, energy recovery ventilation, infrared heating, and air curtains
Showered Verification Among Rental Buildings, Ipsos Research, March 2012 | LEGD commercial multi-family showerhead installation rates
Verification Results: 2013 Hot Water Conservation Program (HWC) Multifamily, SeeLine Group Ltd., March 2014 | LUG commercial multi-family showerhead installation rates
TAPS Verification Program 2012 Year End Research Report, Study CR-604, Quadra Research, April 3, 2013 | LEGD single family low-income faucet aerator and showerhead installation rates
Final Report Following an Audit of the Union Gas ESK - Helping Homes Conserve - HHC - Program, Beslin Communication Group, March 15, 2013 | LUG single family low-income faucet aerator, showerhead, and pipe wrap installation rates
Adaptive Thermostat Ping Report, February 26, 2021 | LEGD and LUG retail purchase adaptive thermostat installation rates